## Slide 1: Corrosive Sulphur & Oil Passivation
Transformer Oil Passivation and Impact of Corrosive Sulphur
P. S. Amaro1, J. A. Pilgrim1, P. L. Lewin1, R. C. D. Brown2 , G. Wilson3, P. Jarman3 1 The Tony Davis High Voltage Laboratory, University of Southampton
2Chemistry, University of Southampton
3 National Grid, Warwick
18 January 2012
Notes: Please use the dd month yyyy format for the date for example 11 January 2008. The main title can be one or two lines long.

## Slide 2: Presentation Overview
Effects of Corrosive Sulphur in Insulation Oil
  Development of Faults
  Detection Mechanisms
  Current Research Focus
Transformer Oil Passivation
  Physical Property Changes
  Short & Long-term Effects
Conclusion and Further Work
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 3: Corrosive Sulphur Impacts
Notes: Use divider pages to break up your presentation into logical sections and to provide a visual break for the viewer. The title can be one or two lines long.

## Slide 4: Corrosive Sulphur
“Elemental sulfur and thermally unstable sulfur compounds in electrical insulating oil that can cause corrosion of certain transformer metals such as copper and silver” ASTM D2864
Not formed in transformer’s normal operational conditions
  Known sources of contamination: poorly refined crude oil, addition of chemical compounds
  Other Suspected sources: gaskets, water-based glues, copper and Kraft paper
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 5: Sulphur Compounds
Multiple Sources = Multiple Compounds
Thiophens, Disulphides, Thio-ethers, Mercaptans, Sulphur
Dibenzyl-disulphide (DBDS) was identified experimentally to be primary compound in corrosive sulphur related faults
Increasing order of corrosion
Contaminated Conductors (G. Wilson, National Grid)
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 6: Cu2S Faults Development
DBDS
DBS
Schematic of Cu2S formation mechanism (CIGRE Final Report 2009, WG A2-32)
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 7: Fault Location in Transformer
Cu2S transformer fault (G. Wilson, National Grid)
Copper Conductor
Cu2S
Insulating Paper
Copper Conductor
Cu2S
Short-Circuited
Copper Sulphide accumulates and bridges two coil turns
Due to the semiconductive nature of Cu2S a short circuit occurs and a turn-to-turn fault is developed

## Slide 8: Detection Methods
Qualitative Plain Copper ASTM D1275A/B & Covered Conductor Deposition (CCD) IEC 62535 Tests
Quantitative Test
  Alumina-based solid phase extraction + Gas Chromatography-Mass Spectrometry (GC-MS) detect DBDS to a level of 0.1 ppm (Toyama et al., 2009)
  Copper strip immersed in oil, accelerated aging conditions
  CCD has a layer of Kraft paper around the copper strip
ASTM copper strip corrosion standard
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 9: Mitigating Techniques
Oil Replacement
  5-12% of contaminated oil remains after retro filling
  Quantity of oil absorption materials, shape of the transformer tank, the location of the drainage valve
Oil Depolarisation
  Combination of solid reagents, chemicals and sorbents
  Reduces DBDS content to 5 mg/kg (5 ppm)
  Transformer can be on or off-load
  Also removes metal passivator and water content
Passivation
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 10: Research Objectives for Cu2S
Relationship of variables such as Temperature and Oxygen
Measurable electrical property changes
Model the degradation process
Cu2S Deposition on Insulation Paper (G. Wilson, National Grid)
Develop an online condition monitoring technique for Cu2S
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 11: Transformer Oil Passivation
Notes: Use divider pages to break up your presentation into logical sections and to provide a visual break for the viewer. The title can be one or two lines long.

## Slide 12: Oil Passivation
Passivation is a technical term used to define the formation of non-permeable surface layers on metal
Triazole-based passivators
  1,2,3-benzotriazole (BTA)
  Irgamet 39TM (CIBA Speciality, Basel, Switzerland)
Previous use of passivators:
  Japan for reducing streaming charging tendency, Australia for improved oxidation inhibition
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 13: Effects of Passivation
Short-term
  Suppress Copper Sulphide
  The increase of H2, CO and CO2 concentration is occurs in the first seven days after passivating the insulation oil.
Long-term
  The passivation is depleted and oil returns to its corrosive level
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 14: Research Objectives for Passivation
Stability of the non-permeable surface layers on metal
Effects on Oil and Paper insulation
Relationship of passivator to metal (m2) and to DBDS(ppm)
Thermal & Electrical property alterations
Analytical tools to quantify the degradation of passivator
Notes: If using a school logo, make sure that if you have a long page title, it does not encroach on the logo. Allow about 2cm around the logo. Run the page title onto two lines if necessary.

## Slide 15: Conclusion & Future Work
Notes: Use divider pages to break up your presentation into logical sections and to provide a visual break for the viewer. The title can be one or two lines long.

## Slide 16: Conclusion
Corrosive Sulphur & Oil Passivation
  Define Relationship between enviromental variables
  Detect electrical properties changes
  Model degradation process
Current stage of research project
  Assessment of the corrosive sulphur and oil passivation state-of-the-art knowledge

## Slide 17: Future Work
Frequency Dielectric Spectroscopy (FDS)
  Use low frequency range spectrum to evaluate paper, pressboard dielectric loss and oil conductivity
  Previous experiments have been able to identify different moisture contents in Kraft paper
Polarisation Depolarisation Currents (PDC)
  Applied dc , short circuit to ground, voltage build-up
  Each materials has specific relaxation times

## Slide 18: Thank you
Notes: You can use a full-bleed image to create impact on a page. Caption the image as shown.