# Control of Grid-Connected inverters using Adaptive Repetitive and Proportional Resonant Schemes

Abstract

Both repetitive and proportional-resonant controllers can effectively reject grid harmonics in grid–connected inverters thanks to their high gains at the fundamental frequency and its harmonics. However, their performances can seriously deteriorate if the grid frequency deviates from its nominal value. Non-ideal proportional-resonant controllers provide better immunity to variation in grid frequency by widening the resonant peaks but at the expense of reducing the gains of the peaks  thus reducing the controller’s effectiveness. In this paper repetitive control scheme for grid-connected inverters which has the ability to track changes in grid frequency and keep the resonant peaks lined up with the grid frequency harmonics. The proposed controller was implemented using a Digital Signal Processor. Simulation and practical results are presented to demonstrate the controller capabilities. The results show that the performance of the proposed controller is superior to that of a proportional-resonant controller.

Key words: grid-connected inverters; repetitive control; adaptive frequency control.

# Nomenclature

n	Number of samples on one fundamental cycle

Ncpu	PWM counter period

Ncpu_o	Nominal PWM counter period

Tcpu, fcpu 	DSP clock period and frequency

Tg, fg	Grid voltage fundamental period and frequecny

Tinv, finv	inverter modulating signal period and frequency

Td	DSP computational time delay

Ts , fs 	Sampling period and frequency

Tso, fso	Nominal sampling period and frequency

Tsw , fsw 	Switching period and frequency

# Introduction

In grid-connected inverters (see Fig. 1), classical PID controllers and their derivatives suffer from relatively low loop gain athe fundamental frequency and its harmonics. As a result they inveters using they types of controller tend to have poor grid harmonic disturbance rejection which results in poor output current THD if the grid voltage is heavily distorted.   Different controller and topologies have been proposed, e.g., [1]-[4] to provide high quality output current that complies with national and international standards [5],[6].   Proportional–Resonant (PR) controllers have also been widely used [7]-[13].  A PR control  has theoretically and infinite gain at a selected frequency. By having multiple PR controllers tuned at the fundamental frequency and its main harmonics, accurate tracking of the demanded current waveform can be achieved. But such a controller is complex to implement in practice.

Repetitive Control (RC) has been widely used in many practical industrial systems such as manufacturing [14], disk drives [15] and robotics [16]. RC has also been used in power electronics such as Uninterruptable Power Supplies (UPS) [17], [18], active filters [19]-[21], DC/DC converters [22], [23], and grid-connected inverters [24], [25]. In these controllers, which are based on the concept of iterative learning control, error between the reference and the output over one fundamental cycle is used to generate a new reference for the next fundamental cycle. RC is mathematically equivalent to a parallel combination of an integral controller, many resonant controllers and a proportional controller [26]. Hence, it is as effective as PR controllers at producing high quality output current in a grid-connected inverter with the addedadvantage of being simpler and easier to implement than PR controllers.

However, if the grid frequency deviates slightly from its nominal value the performance of both PR and RC deteriorates significantly as their high resonant gains will not line up with the grid’s fundamental frequency and its harmonics which  deteriorates the controller’s performance.

The frequency output from a Phase Locked Loop (PLL) can be used as input into PR controllers in order to have adaptive tuning with respect to the grid frequency as suggested in [12] and [13]. However, all controller parameters must be made adaptive which makes the practical implementation of such mechanism quite complicated especially if a bank of resonant controllers is used to reject a high number of harmonics. Non-ideal proportional-resonant controllers provide better immunity to variation in grid frequency by widening the resonant peaks but at the expense of reducing the gains of the peaks but this reduces the controller’s effectiveness it tacking the demanded waveform [7].

Voltage control of grid connected inverters with a frequency adaptive mechanism based on H∞ repetitive control was proposed by Hornik and Zhong [24], [25]. The internal model of the system consists of a delay unit e-TDs cascaded with a low-pass filter,   W(s)=ωcs+ωc . The adaptive mechanisim is based on varying the cut-off frequency of the filter ωc according to the varying grid frequency. According to the authors, this mechanism is effective for a grid frequency variation of only ±0.2Hz. If the grid variation is higher than this limit, the controller delay TD needs to be changed. However, for low sampling frequency, an adaptive delay is impossible to be implemented without further deterioration of the controller performance [24].

Conventional RC structure [27]-[29] inherently presents a control delay of one fundamental period and thus suffers from slow dynamic response. Odd-harmonic RC [18]-[20], [30],[31] makes use of the fact that most AC systems have only odd harmonics in their spectrum, which reduces the time delay to one half of the fundamental cycle thus improving the dynamic response. Jiang et al. [17] proposed a RC that makea use of the frequency shift characteristics of the DQ transformations into three synchronous frames rotating at frequencies ω1+ , ω1-, and ω3+ are used and thus all odd harmonics in the stationary frame are shifted and become of the order of six times the fundamental frequency. This reduces the time delay to one-sixth of the fundamental cycle thus improving the transient response substantially compared to conventional RC.

However, using RC alone in grid-connected inverters would not be able provide satisfactory transient response. Disturbance caused by the fundamental component of the grid voltage will result in the inverter generating output current that is much higher than the reference current. Relying on RC to deal with this disturbance means that high current error will be produced during the RC convergence time. This error might not be acceptable as it might be several times the reference current. The same problem exists in case of grid disturbances such as voltage sag and swell, where fast response is required in order for the inverter to ride through the disturbance event.

To overcome the deficiencies of conventional RC this paper proposes an odd-harmonic frequency adaptive repetitive controller (ARC) for a grid-connected inverter suitable for DSP implementation. The frequency adaptive feature is based on varying both switching and sampling frequencies according to the grid frequency and thus keeping the number of delay samples of the RC constant. This mechanism is able to precisely track changes in the grid frequency and keep the high resonant gains always lined up with the grid harmonics. The design procedure of the controller is explained in detail and the practical DSP implementation of the proposed controller is also discussed. A feedforward loop that compensates for the disturbance caused by the fundamental component of the grid voltage is implemented to make sure that the current is bounded during the convergence time of the RC. The design results in a fast convergence within only one fundamental cycle. The performance of the proposed controller is compared to that of  a proportional resonance controller.

# Controller Structure and System Modelling

Fig. 1 shows the circuit diagram of a conventional 2-level grid-connected inverter with LCL filter. The inverter parameters used in this paper are listed in Table I. Fig. 2 shows the block diagram that represents the control scheme implemented in each phase. The controller consists of an outer loop of the output current and an inner loop of the capacitor current to provide active damping. This structure increases the degree of freedom in designing the controller compared with the widely used one-feedback loop of L1 current because two controller gains (KC and K) can be optimized instead of only one controller gain. A plug-in repetitive controller transfer function (GRC) is implemented to reject current harmonics caused by grid voltage harmonics. The repetitive controller is capable of rejecting the disturbance of the fundamental harmonic and its multiples. However, the convergence time of the repetitive controller is relatively long and therefore a feedforward loop of the fundamental nominal component of the grid voltage is implemented to reduce the current error during the convergence time of the RC as will be explained later. Note that the controller in Fig. 2 has the form of K+GR(z) which means it is proportional + repetitive controller but it will be simply abbreviated as RC in this paper.

The block diagram of Fig. 2 can be simplified as shown in Fig. 3a. The transfer functions that appear in Fig. 3a are given by

Fig. 1. Grid-connected inverter

Table I

Inverter Parameters

| Description | Symbol | Value |
| --- | --- | --- |
| Inverter side filter inductor | L1 | 350µH |
| Filter capacitor | C | 80µF |
| Grid side filter inductor | L2 | 50µH |
| Nominal grid voltage | Vgo | 230 V (rms) |
| Inverter dc voltage | Vdc | 700 Vdc |
| Nominal grid frequency | fgo | 50Hz |
| Nominal switching frequency | fswo | 8kHz |
| Nominal sampling frequency | fso | 16kHz |
| Computational time delay | Td | 10µs |

Fig. 2. Block diagram of one phase and its controller

Fig. 3. Block diagram. (a) one phase and its controller. (b) simplified block diagram

Fig. 4. Block diagram of the system error

From Fig 3a, the disturbance caused by the grid voltage is given by Vg(s)B(s). There are two options to reject this disturbance: RC and feedforward. For RC to deal with the grid disturbance at the fundamental frequency means that there will be a delay of at least one fundamental cycle (or half fundamental cycle in case of an Odd harmonic RC) for the controller to feed the error created by one fundamental cycle back to the system for the next cycle. But the error caused by the fundamental component of the grid voltage will be high and the inverter might generate current that is several times the reference current during the first cycle. Considering the feedforward option and to completely compensate for the grid disturbance, the feedforward loop should ideally take the form of Vg(s)B(s) as can be seen from Fig. 3a. The second derivative component L1Cs2 in (3) is practically very small and can be neglected.  Therefore, feedforward of the component (1+ KCCs)Vg should effectively reject grid disturbance. This, however, involves the differentiation of the grid voltage signal, which is undesirable in practice due to the well-known problem of noise amplification. In order to avoid the differentiation in the feedforward and also to overcome the long delay of the RC, the proposed strategy is to use the feeforward to compensate for the disturbance caused by the fundamental frequency using a pre-known value of the nominal grid voltage and to rely on the RC to compensate for the disturbance caused by all other harmonics. Using the known nominal value of the grid rms voltage Vgo and frequency fgo, the feedforward component that will compensate for the fundamental component according to (3) (neglecting L1Cs2) is given by

If the grid voltage is slightly different from its nominal value, the RC will compensate for this.

Fig. 3a can be further simplified as in Fig. 3b considering a fully discretized system. The disturbance Dg(z) represents any grid disturbance that has not be compensated for using the feedforward Vf. The physical plant discretized transfer function Gp(z) can be calculated as in  (5)

where G(z) and GH(z) are the Z-transforms of G(s) and  G(s)H(s) respectively, taking into account the Zero-Order-Hold (ZOH) method with sampling time Ts and computational time delay Td such as

The transfer function of the odd harmonic repetitive controller is given in [30] as

Where Q(z) is a low pass filter, KR is the repetitive controller gain, n is the number of samples in one fundamental cycle and zm is a non-causal phase lead unit.

# System Analysis and Controller Design

The controller design involves the determination of KC, K, Q(z), KR, and m. From Fig. 3b, the error signal E can be expressed as

Substituting (8) in (9) and rearranging gives

Where

Equation (10) can be represented by the block diagram in Fig. 4 which consists of three cascaded transfer functions: T1(z), T2(z), and T3(z). T1(z) is the closed loop transfer function without the repetitive controller and its stability can be guaranteed by choosing KC and K. The stability of the second transfer function T2(z) can be guaranteed by choosing a stable low pass filter Q(z). The stability of the third transfer function T3(z) which contains a positive feedback loop can be guaranteed using the small gain theorem, i.e., the error signal will be bounded if the magnitude of the open loop transfer function is less than 1 for all values of frequencies. Hence

- Selection of KC and K

If RC is not implemented, the selection of the capacitor current loop gain KC and the output current loop gain K would be a compromise between good stability margins and good harmonics rejection; increasing KC will improve stability but will worsen harmonics rejection while increasing K will worsen stability but will improve harmonics rejection [3]. In this paper, the RC will take care of harmonics rejection and hence it is important to choose KC and K to maximize the stability margins. The gains KC and K have been chosen to give good stability margins for T1(z). Typical control system design criteria have been used i.e., a phase margin between 40 to 70 degrees and a damping ratio between 0.3 to 0.7. By analysing Gp(z) in Matlab SISO Design Tool, the gains KC and K have been set to 5 and 3, respectively. This selection gives gain margin of 5.6dB, phase margin of 51 deg, damping ratio ζ = 0.33, and settling time ts = 0.5 ms.

- Selection of Q(z)

The bode diagram of the open loop transfer function K+GRC(z)Gp(z) with, Q(z) =1 is shown in Fig. 5. It can be noticed that the system is unstable due to the resonant peaks near the crossover frequency which means that Q(z) needs to be modified to attenuate the high frequency peaks. A zero-phase low pass filter is used which has the following structure [32]

,

By setting z=ejωTs (Ts is the sampling period) in (13), the frequency response of Q(z) can be obtained as

Therefore,

From (15), the magnitude  can be written as

In order to get a unity gain at zero frequency then αo and α1 must be chosen to satisfy . Also, to get zero gain at high frequencies  ωTs>π, then then αo and α1 must be chosen to satisfy . Therefore, αo and α1 are set to 0.5, and 0.25, respectively. For the full frequency range, is given by

The filter is now given by

The bode diagram of Q(ejωTs) as described in (17) is shown in Fig. 6. The bode diagram of the open loop transfer function K+GRC(z)Gp(z) with, Q(z) as described in (18) is shown in Fig. 7 which confirms the system’s stability as the high gains near the crossover frequency have been attenuated and the system has positive stability margins.

Fig. 5. Bode diagram of the open loop transfer function K+GRC(z)Gp(z), with, m=1,

Fig. 6. Bode diagram of Q(z) = 0.25z+0.5+0.25z-1

Fig. 7. Bode diagram of the open loop transfer function K+GRC(z)Gp(z), with, m=1, (GM = 5.0dB, PM = 44.1 deg)

Fig. 8. The locus of the vector RejωTs

Fig. 9. R(z)∞ versus KR and m

- Selection of KR and m

The value of the RC gain KR needs to be carefully selected as it is a key parameter for error convergence and system stability. A high repetitive controller gain KR results in fast error convergence but the feedback system becomes less stable. The non-causal phase lead unit of m is normally used to compensate for any delay or phase lag introduced by the physical plant and controller transfer function. Implementing zm is not possible practically unless it is cascaded with the delay units of the RC. The design criterion used in this paper is maximizing KR so as to reduce the RC convergence time but at the same time minimizing R(z)∞ so as to increase the stability margins. Fig. 8 shows the locus of the vector RejωTs  for different values of KR when m = 3. It can be noticed that as KR increases, the stability margin decreases until the system becomes unstable when KR > 4.8 as RejωTs becomes greater than unity. In Fig. 9, R(z)∞ is plotted versus KR and m. For m = 0, the system is only stable when KR < 0.6 (R(z)∞= 0.99 when KR = 0.6). This indicates poor stability. Increasing m does improve stability and the best value is m = 3 as this corresponds to the lowest possible R(z)∞. The minimum value for R(z)∞ occurs when KR = 2.8 and m = 3 and hence they have been chosen for this design.

# Frequency adaptive Repetitive Control (ARC)

In this section, a frequency adaptive repetitive control is proposed to track the variations in grid frequency.

- Effect of grid frequency variation on repetitive controller performance

As was mentioned before, RC is equivalent to a parallel combination of resonant controllers with high gain at the fundamental frequency and its harmonics. RC is implemented in this paper to reject inverter output current harmonics caused by the presence of grid voltage harmonics. However, the grid frequency can vary with time due to variation of loads, or the connection or disconnection of big generators. Typically, the grid frequency can oscillate by ±2%. Fig. 10 shows the Bode diagram of the open loop transfer function of the system. The magnified portion of the diagram shows the resonant peak around the 5th harmonic. The benefit from this high gain happens when the 5th harmonic is exactly 250Hz. However, if the grid frequency changes by ±2%, the resonant peak will not line up with the 5th harmonic and consequently the RC becomes ineffective.  The linearized inverter model described in Fig. 2 has been simulated in Matlab/Simulink with the PWM block set to unity gain. Some grid harmonics are included in the grid voltage Vg and four causes are simulated for different grid frequency fg. The simulation results of the output current after the RC has converged are shown in Fig. 11. It is quite clear that the performance of the repetitive controller deteriorates dramatically if the grid frequency deviates from its nominal value. In order to keep the RC effective, it has to adapt to the varying grid frequency.

Fig. 10. Effect of grid frequency variation

Fig. 11. Simulated output current for different grid frequencies

Fig. 12. PWM implementation in the DSP

Fig. 13. PWM period control

- Proposed frequency adaptive repetitive controller

The performance of the RC is not guaranteed unless the high resonant gains line up with the grid harmonics. Therefore, the time delay of the repetitive controller needs to adapt to the changes in grid voltage fundamental period. The number of delay samples n can be changed with respect to the grid frequency. However, unless the switching frequency (and hence the sampling frequency) are very high with respect to the fundamental frequency, this mechanism will not result in precise control of the time delay used by the repetitive controller. For example, if the sampling frequency is 4 kHz, for a fundamental frequency of 50Hz, the number of samples per cycle is 4000/50 = 80 samples. Each sample is equivalent to 0.253ms which means that the minimum change in grid frequency that this scheme can deal with is approximately 0.63Hz. According to the Bode diagram in Fig 10, if the grid frequency deviates by only 0.15Hz from its nominal value, the RC gain at the 5th harmonic reduces by about 20% of its nominal value.  For 0.60 Hz deviation, the RC becomes completely ineffective. Also by looking at Fig. 11, the deterioration in the RC performance starts to be noticeable when the grid frequency deviates by only 0.2 Hz from its nominal value. Therefore, varying the number of samples will not provide good tracking of grid frequency without deteriorating the RC performance. The mechanism proposed in this paper is to change the switching frequency and the sampling frequency with respect to the grid frequency. The ratio of the sampling frequency to the fundamental frequency remains constant and hence n does not need to change. Taking into account that the grid frequency can vary by up to ±2%, the sampling and switching frequencies can vary by the same ratio. Therefore, the switching frequency can vary from 7.84kHz to 8.16kHz.  The attenuation of the LCL filter will change very slightly as the switching frequency varies within this range.

The mechanism benefits form the high precision of the DSP clock used to implement the controller. Fig. 12 shows how the PWM carrier is implemented in the DSP. In this paper, the sampling frequency fs is set to be twice the switching frequency such as fs =2 fsw. A counter that is based on the Central Processing Unit (CPU) clock is set to count up and down periodically. The PWM counter period Ncpu is set to determine the required sampling period. Hence

where Ts and Tcpu are the sampling and CPU clock periods, respectively. The number of samples n per one fundamental cycle is given by,

where Tg is the grid voltage fundamental period. The inverter modulating signal period is given by

Substituting (19) into (21) gives

According to (22), in order to vary the inverter’s modulating signal period Tinv and hence the frequency finv while maintaining n constant, the number of counts Ncpu needs to be changed.

Fig. 13 shows the proposed controller of the PWM counter period Ncpu. The grid voltage fundamental period Tg is sensed (by a PLL or zero crossing detector) and divided by nTcpu to calculate the demand PWM counter period Ncpu*. The period error EN is fed into a Proportional-Integrator (PI) controller to calculate ∆Ncpu which is added to the nominal PWM counter period Ncpu_o to produce Ncpu. The nominal PWM counter period Ncpu_o is calculated as in (23)

where Tso is the nominal switching period.

To highlight the advantage of this mechanism over changing n, consider the case where the CPU frequency fcpu =150MHz, n = 320, the nominal switching frequency  fso = 16kHz, according to (23) the nominal PWM counter period Ncpu_o  = 150MHz/16kHz = 9375. If the inverter modulating signal frequency finv is controlled by varying n then by reducing n by 1, finv will be given by

However, if finv is controlled by varying Ncpu as proposed here, by reducing Ncpu by 1 count, then finv will be given by

It can be noticed that varying Ncpu gives 29 times more precision in controlling the frequency.

- Frequency controller design

According to most of the grid codes of practice, the grid frequency variation has a maximum slope of 1 Hz/sec [12]. This is nearly equivalent to increasing or decreasing the grid period by about 0.4ms per second. The design objective is to track this variation and maintain the error signal between the PWM counter period Ncpu and its demand Ncpu* to the minimum of one count. The deviation in grid frequency and hence the PWM counter period demand Ncpu* will be modeled as a ramp function as:

where D is the rate of change of Ncpu* in count/sec. From Fig. 13 the error EN (error signal between the PWM counter period Ncpu and its demand Ncpu*) is given by

The steady state error ENss for a ramp input of Ncpu* can be calculated by substituting (26) in (27) and using the final–value theorem such as

Maximum D is 184 count/sec (equivalent to 0.4ms per second). The integral gain ki is chosen to give the minimum possible steady state frequency error which is one count. Therefore ki is set to 184. The proportional gain kp is normally set to deal with transient response to a step input, In this case, a step change in grid frequency is unlikely and the proportional gain is set to 10.

Fig. 14. Effect of different sampling frequency on , fs = 15.7, 16.0, and 16.3 kHz, KR=2.8, m=3.

Table II

Proportional resonant controller gains

| K1 | K3 | K5 | K7 | K9 | K11 | K13 | K15 | K17 | K19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110 | 100 | 90 | 80 | 70 | 60 | 50 | 40 | 30 | 20 |

Fig. 15. Bode diagram of the open loop transfer function K+GRh(z)Gp(z), (GM = 2.5dB, PM = 21.0 deg)

- Effect of varying sampling on system stability

It is essential to check the effect of varying sampling frequency on the stability of the repetitive controller. Fig. 14 shows how R(z)∞ varies for three different sampling frequencies corresponding to the nominal, +2%, and -2% deviation in grid frequency. It is quite clear that the effect of changing the sampling frequency on the stability of the ARC is very minimal and the R(z)∞ is well inside the unit circle. The stability of T1(z) and T1(z) are not affected by varying the sampling frequency.

# Design of a Proportional Resonant Controller

In order to compare the performance of the proposed ARC with other controllers reported in the literature, a PR controller is designed for the same inverter considered in this paper. PR controller has been widely considered for its ability to reject harmonics by creating high resonant peaks at specific frequencies. The ideal resonant controller is given by

where ωh is the selected harmonic frequency to be compensated for and Kh is the controller gain. Equation (29) gives infinite gain at ωh. To avoid stability problems that might arise because of the infinite gain, a non-ideal resonant controller can be used such as [7]

where ωc is the cut-off frequency of the non-ideal resonant controller. The insertion of ωc reduces the resonant peaks and widen their bandwidth which makes the controller less sensitive to frequency variations. By using several resonant controllers tuned at the desired odd harmonic frequencies a resonant controller can be created such as

A bank of resonant controllers that are tuned at the low order odd harmonics up to H=19 is used. The design involve the determination of the cut-off frequency ωc and the controller gains Kh. Smaller ωc will make the controller more sensitive to frequency variation and more difficult to implement in a fixed point DSP [7]. On the other hand, high value of ωc will reduce the resonant peaks and hence the controller performance. In practice, ωc value of 5-15 rad/sec have been found to provide a good compromise [33]. In this design, ωc is set to 10 rad/sec. The gains Kh are chosen to give a good compromise between stability and performance. High gains will increase the resonance peaks and hence improves harmonics rejection but at the same time they will left up the bode diagram of the open loop transfer function which reduces the stability margins. The gains are set to reduce gradually as h increases. This is to reduce the effect of the resonant peaks in the vicinity of the crossover frequency in an attempt to reduce the effect on the stability margins The gains used are shown in Table. II.

The resonant controller is discretized using the bilinear ‘Tustin’ transformation [34] such as

The PR controller is obtained by adding the proportional gain K to GRh(z). The bode diagram of the system open loop transfer function K+GRh(z)Gp(z) is shown in Fig. 15.  The gain margin and the phase margin of this design are 2.5dB and 21.0 deg, respectively.

# Simulation Results

Detailed simulation model of the 3-phase inverter presented in Fig. 1 has been built using the MATLAB SimPowerSystems. The inverter parameters were listed in Table I. Grid voltage harmonics were measured in the laboratory and similar values were included in the simulation model. The total grid voltage THD was measured to be 1.9%. The controller parameters for RC and ARC used in the simulation are listed in Table III. The simulation parameters for the resonant controller are the same as the ones listed in Table II.

- Performance comparison between P, PR and RC at a fixed grid frequency

In this section, a performance comparison is carried out between three different controllers: Proportional (P), PR and RC.  Fig. 16 shows the output current with P controller for a 14A (rms) demand. The output current THD is 14.2%. The magnitude and phase angle of the 50Hz fundamental component are 8.3A and -7.9 deg, respectively. Fig. 17 shows the output current with PR controller. The current THD is 2.6%. The magnitude and phase angle of the 50Hz fundamental component are 13A and +8.0 deg, respectively.  Fig. 18 shows the output current with RC after the controller has converged. The current THD is reduced to only 0.8%. The magnitude and phase angle of the 50Hz fundamental component are 14A and   -0.9 deg, respectively. The effectiveness of the RC in improving the current THD and reference tracking is clearly noticed. Fig. 19 shows the grid voltage harmonics used in the simulation model and Fig. 20 shows the output current harmonics with P, PR, and RC.

- Performance comparison between PR, RC, and ARC at varying grid frequency

To test the effectiveness of the ARC, the grid frequency is set to start to change from 50Hz to 50.2Hz at simulation time t=0.1sec. The slope of change is 1Hz/sec. Fig. 21 shows the output current THD with PR, RC, and ARC. The THD is measured using the built-in Simulink block. With PR, the THD increased with frequency deviation and it reached 3.5% before it dropped to 2.8% when the grid frequency settled at 50.2Hz. With RC, the current THD increased as the frequency deviation increased and it reached 3.2%. Once the grid frequency reaches 50.2Hz and stopped deviating, the THD dropped to 1.8%. The ARC on the other hand was able to keep the output current THD at 0.8% at all time.

Fig. 22 shows how the steady state output current THD varies as the grid frequency deviates by ±2%. It can be noticed that the PR is less sensitive to the variation in grid frequency than RC thanks to its wider resonant peaks. It can also be noticed that the lowest THD with PR occurs at 49.8Hz and not 50.0Hz. This is due to the quantization error of the discretization process. The superiority of ARC over PR and RC is quite clear as it can always keep the THD low regardless of the variation in grid frequency.

- Feedforward Loop,

Fig. 23 shows the output current with RC during starting when the feedforward is deactivated. It can be noticed that during the first half cycle the output current is nearly five times the reference current. This is due to the disturbance caused by the fundamental component of the grid voltage. Fig. 24 shows the output current when the feedforward of the nominal fundamental component of the grid voltage is activated. The error in the first half cycle is small and it is due to the disturbance caused by the grid higher harmonics. With the feedforward, the RC converges in half fundamental cycle while without the feedforward the error converges within one complete fundamental cycle.

Table III

Controller parameters

|  | Description | Symbol | Value |
| --- | --- | --- | --- |
| Inner Controller | Output current feedback gain | K | 3 |
|  | Capacitor current feedback gain | KC | 5 |
| RC | RC gain | KR | 2.8 |
|  | Noncausal phase lead | m | 3 |
|  | Number of samples in one cycle | n | 320 |
|  | Filter Q(z) coefficient 1 | ∝0 | 0.5 |
|  | Filter Q(z) coefficient 2 | ∝1 | 0.25 |
| ARC | CPU frequency | fcpu | 150MHz |
|  | Nominal CPU timer period | Ncpu_o | 9375 |
|  | Frequency control proportional gain | kp | 10 |
|  | Frequency control integral gain | ki | 184 |

Fig. 16. Simulated steady state output current with proportional only controller (THD = 14.2%)

Fig. 17. Simulated steady state output current with PR (THD = 2.6%)

Fig. 18. Simulated steady state output current with RC (THD = 0.8%)

Fig. 19. Grid voltage harmonics (percentage of fundamental)

Fig. 20. Output current harmonics (percentage of fundamental)

Fig. 21. Output current THD (Grid frequency started to change from 50Hz to 50.2Hz at t = 0.1s with a slope of 1Hz/sec)

Fig. 22. Output current THD versus grid frequency

Fig. 23. Simulated output current with RC but without the feedforward

Fig. 24. Simulated output current with RC and feedforward

# Practical Implementation and Experimental Results

The proposed repetitive controller was tested experimentally with the grid-connected inverter described in Fig. 1 and Table I. The control parameters were listed in Table III. The controller was implemented using a Texas Instrument TMS320F2812 32-bit fixed point DSP. The three-phase reference sine waves were generated internally by the DSP using lookup tables of n = 320 samples. The sine waves amplitude is set externally (by a setting in the user interface) and sent via Controller Area Network (CAN)-bus. The input DC is regulated by an external boost circuit to 700V dc so current can be injected into the 230Vrms grid.

The RC controller has been realized by programming as follow: from (8), the discreet transfer function the relates the RC output Y(z) to the RC input E(z) is given by

Substituting (18) in (33) and rearranging gives

where X(z) is given by

Equations (34) and (35) represent the indirect (standard) realization of digital controllers [34] and they are represented by the block diagram in Fig. 25. The RC controller is implemented in software by creating 3 arrays x(i) (one per phase) each is 160 (320/2) entries long. At the discrete time i, the RC output y(i) is calculated using the difference equation (36) and the array entry x(i) is filled using the difference equation (37)

where e(i) is the current error at discrete time i.

In order to implement the proposed frequency adaptive control, a high precision measurement of the grid voltage frequency is required. The grid voltage signal is sensed and the Positive-Going Zero Crossing (PGZC) is detected. The fundamental period of the grid voltage Tg is measured by calculating the number of samples between two consecutive PGZCs. In order to increase the measurement accuracy, the PGZC is detected every 15 fundamental cycles. In this way, the measurement error is reduced to Ts/15 (compared to Ts if the PGZC is detected every cycle). For the nominal sampling frequency of 16kHz, the measurement error is only ±62.5µs/15 = ±4.16µs, which is equivalent to ±0.01Hz.

Fig. 26 shows the output current when the RC is de-activated (i.e. proportional only controller P). The demand current is set to 15A (rms). The current THD is measured to be 13.0%. Fig. 27 shows the output current but when the RC is activated. The current THD is measured to be only 1.1%. In the system reported in [3] (which is similar to this one but without RC and K(z) is a phase lag), such low THD was only achievable when the output current equals the rated current, i.e., 90A (rms).  Fig. 28 shows the measured output current harmonics with P and RC controller.

The feedforward loop was activated all the time to avoid damaging high currents (see the simulation results in Fig. 23). Fig. 29 shows the moment when the inverter connects to the grid. Before the main contactor is closed, the inverter was producing output voltage that was matching exactly the grid voltage thanks to the feedforward loop of the nominal voltage of the fundamental component. This guaranteed smooth connection transient and low current when the contactor closed.

The grid frequency was monitored in the laboratory and the maximum deviation recorded was ±0.1Hz. The current THD was always maintained below 1.2%. In order to test the performance of the ARC against higher grid frequency deviation, an AC voltage source would need to be used to emulate the grid.

Fig. 25. RC Implementation

Fig. 26. Output current without RC (10A/div)

Fig. 27. Output current with RC (10A/div)

Fig. 28. Experimental output current harmonics

Fig. 29. Inverter output voltage before and after connecting to the grid (5A/div)

# Conclusion

The design and practical implementation of a frequency adaptive odd-harmonic repetitive controller for a grid-connected inverter was discussed. The adaptive mechanism was found to be very effective in tracking the changes in grid frequency and hence maintaining the effectiveness of the repetitive controller. The performance of the proposed controller was found to superior to that of proportional resonant controller. The proposed mechanism presents a straightforward implementation using a DSP system. The inherent long delay feature of the repetitive controller has been overcome by implementing a feedforward loop at the fundamental frequency to ensure that the current is bounded during the convergence period of the repetitive controller.

##### References

- J. C. Moreno, J. M. E. Huerta, R. G. Gil and S.A. Gonzalez, “A robust predictive current control for three-phase grid-connected inverters," IEEE Trans. Ind. Electron., vol. 56, no. 6 pp. 1993-2004, 2009.

- W. Zhao, D. D.C. Lu and V. G. Agelidis, "current control of grid-connected boost inverter with zero steady-state error," IEEE Trans. on Power Electron. vol. 26, no.10, pp. 2825-2834, 2011.

- M. A. Abusara and S. M. Sharkh, "Digital control of a three-phase grid connected inverter," Int. J Power Electronics, vol. 3, no. 3, 2011, pp. 299-319, 2011.

- Y. Shuitao, L. Qin, F. Z. Peng, Q. Zhaoming, "A robust control scheme for grid-connected voltage-source inverters," IEEE Trans. Ind. Electron vol. 58, no. 1, pp. 202-212, 2011.

- IEEE1547.1, “IEEE standard for interconnecting distributed resources with electric power systems,” July 2003.

- IEC1727, “Characteristic of the utility interface for photovoltaic (PV) systems,” November 2002.

- R. Teodorescu, F. Blaabjerg, M. Liserre and P. C. Loh, “Proportional-resonant controllers and filters for grid-connected voltage-source converters,” IEE Proceedings on Electric Power Applications. vol. 153 pp. 750-762, 2006.

- J. G. Hwang, P. W. Lehn, and M. Winkelnkemper, “A generalized class of stationary frame-current controllers for utility-connected AC-DC converters,” IEEE Trans. on Power Delivery. vol. 25 pp. 2742-2751. 2010.

- S. Eren, A. Bakhshai and P. Jain, “Control of three-phase voltage source inverter for renewable energy applications,”  IEEE International Telecommunications Energy Conference (INTELEC), Amsterdam, 2011.

- G. Shen, X. Zhu, J. Zhang and D. Xu, “A new feedback method for PR current control of LCL-filter based utility-connected inverter,” IEEE Trans. Ind Electron., vol.57, no. 6, pp. 2033-2041, 2010.

- M. Liserre, R. Teodorescu, and F. Blaabjerg, “Multiple harmonics control for three phase utility converter systems with the use of PI-RES current controller in a rotating frame,” IEEE Trans. Power Electron., vol. 21, no.3, pp. 836-841, 2006.

- A. Timbus, M. Ciobotaru, R. Teodorescu, and F. Blaabjerg, “Adaptive resonant controller for grid-connected converters in distributed power generation systems,” in Proc. 21st Annu. IEEE Appl. Power Electron.Conf., 2006, pp. 1601–1606.

- F. Gonzalez-Espin, G. Garcera,  I. Patrao, and E. Figueres,” An adaptive control system for three-phase photovoltaic inverters working in a polluted and variable frequency electric grid,” IEEE Trans. Power Electron. vol. 27, no. 10 pp. 4248-4261, Oct. 2012.

- S.L. Chen, T. H. Hsieh, “Repetitive Control Design and Implementation for Linear Motor Machine Tool,” International Journal of Machine Tools and Manufacture, vol. 47, pp. 1807-16. 2007.

- V. Alexandrov, G. van Albada, P. Sloot, J. Dongarra, K. Chang, G. Park, A Novel Method of Adaptive Repetitive Control for Optical Disk Drivers, The 6th International Conference on Computational Science ~ICCS 2006~, May 28-31, 2006, Reading, U.K.

- H. Tinone,  and N. Aoshima . “Parameter identification of robot arm with repetitive control,” International Journal of Control. vol. 63 pp. 225 – 238, 1996.

- S. Jiang, D. Cao, Y. Li, J. Liu, and F. Z. Peng, “Low-THD, Fast-transient, and cost-effective synchronous-frame repetitive controller for three-phase UPS inverters,” IEEE Trans. Power Electron. vol. 27 pp. 2994-3005, 2012.

- G. Escobar, A. A. Valdez, J. Leyva-Ramos, and P. Mattavelli, “Repetitive based controller for a UPS inverter to compensate unbalance and harmonic distortion,” IEEE Trans. Ind. Electron., vol. 54, no. 1, pp. 504–510, Feb. 2007.

- R. Gri˜n´o, R. Cardoner, R. Costa-Castell´o, and E. Fossas, “Digital repetitive control of a three-phase four-wire shunt active filter,” IEEE Trans. Ind. Electron., vol. 54, no. 3, pp. 1495–1503, Jun. 2007.

- R. Castello, R.Grino, and E. Fossas, “Odd-harmonic digital repetitive control of a single-phase current active filter,” IEEE Trans. Power Electron., vol. 19, no. 4, pp. 1060–1068, Jul. 2004.

- P. Mattavelli and F. P.Marafao, “Repetitive-based control for selective harmonic compensation in active power filters,” IEEE Trans. Ind. Electron.,vol. 51, no. 5, pp. 1018–1024, Oct. 2004.

- G. Escobar, J. Leyva-Ramos, P. R. Mart´ınez, and A. A. Valdez, “A repetitive-based controller for the boost converter to compensate the harmonic distortion of the output voltage,” IEEE Trans. Control Syst. Technol., vol. 13, no. 3, pp. 500–508, May 2005.

- G. Escobar, M. Hern´andez-G´omez, P. R. Mart´ınez, and M. F. Mart´ınez- Montejano, “A repetitive-based controller for a power factor precompensator,” IEEE Trans. Circuits Syst. I, Reg. Papers, vol. 54, no. 9, pp. 1968–1976, Sep. 2007.

- T. Hornik and Q. C. Zhong, “H∞ repetitive voltage control of grid connected inverters with a frequency adaptive mechanism,” IET Power Electron., vol.3, no. 6, pp. 925-935, 2010.

- T. Hornik, and Q.C. Zhong, “A current-control strategy for voltage-source inverters in microgrid based on H-infinity and repetitive control,” IEEE Trans. Power Electron. vol. 26 pp. 943-952, 2011.

- Lu, W., Zhou, K. and Yang, Y,. "A general internal model principle based control scheme for CVCF PWM converters," 2nd IEEE International Symposium on Power Electronics for Distributed Generation Systems (PEDG) . Hefei China. 2010.

- K. Zhou and D. Wang, “Digital repetitive learning controller for three phase CVCF PWM inverter,” IEEE Trans. Ind. Electron., vol. 48, no. 4,pp. 820–830, Aug. 2001.

- K. Zhang, Y. Kang, J. Xiong, and J. Chen, “Direct repetitive control of SPWM inverters for UPS purpose,” IEEE Trans. Power Electron., vol. 18, no. 3, pp. 784–792, May 2003.

- H. Deng, R. Oruganti, and D. Srinivasan, “Analysis and design of iterative learning control strategies for UPS inverters,” IEEE Trans. Ind. Electron.,vol. 54, no. 3, pp. 1739–1751, Jun. 2007.

- R. Costa-Castello, R. Grino, and E. Fossas, “Odd-harmonic digital repetitive control of a single-phase current active filter,” IEEE Trans. Power Electron., vol. 19, no. 4, pp. 1060–1068, Jul. 2004.

- K. Zhou, K. Low, D. Wang, F. Luo, B. Zhang, and Y. Wang, “Zerophase odd-harmonic repetitive controller for a single-phase PWM inverter,” IEEE Trans. Power Electron., vol. 21, no. 1, pp. 193–201, Jan. 2006.

- Michels, H. Pinheiro, and H. Grundling, “Design of plug-in repetitive controllers for single-phase PWM inverters,” 39th IAS Annual Meeting:Industry Applications Conference, 2004.

- P. Tan, P. Loh, and D. Holmes, “High-performance harmonic extraction algorithm for a 25kV traction power quality conditioner,” IEEE Trans. Electric Power Applications, Vol. 20, no. 2, pp. 1703-10, 2005.

- Ogata K.: ‘Discrete-time control systems’, Prentice-Hall, 1995.