## MetaData
This spreadsheet contains the imported raw data and subsequent analysis from:
Heat Recovery Proof of Concept Test 2 500/1000
The analysis of each set of raw data consists of:
Calculation of average heat exchanger water flow measurement from timed results taken during testing
Converting gauge pressure readings to absolute
Plotting pressures vs. time and determining visually where equilibrium is established
Plotting temperatrues vs time and determining visually where equilibrium is established
Using Excel functions to find min, max, and average pressure and temperature values during equilibrium
The final analysis calculates the efficiency of the heat recovery in the heat exchanger from this data.
An analysis calculates the uncertainty and/or variability of calculated/measured values to allow for error bars to be plotted on the graphs in the efficiency analysis
The raw data analysed in this spreadsheet is as follows:
Date Created | Test Reference | Comments
2019-09-04 | 9.6mL/s
2019-09-04 | 7.2mL/s
2019-09-04 | 17.3mL/s
2019-09-04 | 14.7mL/s
2019-09-04 | 13.1mL/s
2019-10-01 | 10.5mL/s
2019-10-01 | 13.3mL/s | The vacuum pump breaking meant that this test has no point where equilibrium can be taken and therefore this data is not used in final analysis

## 9.6mL s
|  |  | BoilerPressure |  | HEPressure |  | SCPressure
Date | Clock | Timer | Gauge (raw) | Absolute (edit) | Gauge (raw) | Absolute (edit) | Gauge (raw) | Absolute (edit) | HETemperature | SCTemperature
2019-09-04 | 9:51 | 1.1172 | 0.07 | 1.07 | -0.29 | 0.71 | -0.25 | 0.75 | 22.46 | 28.32
2019-09-04 | 9:51 | 1.1602 | 0.07 | 1.07 | -0.3 | 0.7 | -0.26 | 0.74 | 22.46 | 27.34 |  | Flow
2019-09-04 | 9:51 | 1.2695 | 0.07 | 1.07 | -0.3 | 0.7 | -0.25 | 0.75 | 23.44 | 28.32 |  | mL | seconds | flow
2019-09-04 | 9:51 | 1.3906 | 0.01 | 1.01 | -0.26 | 0.74 | -0.25 | 0.75 | 22.46 | 27.34 |  | 100 | 10 | 10 | start
2019-09-04 | 9:51 | 1.4805 | 0.01 | 1.01 | -0.24 | 0.76 | -0.26 | 0.74 | 23.44 | 28.32 |  | 100 | 10 | 10
2019-09-04 | 9:51 | 1.5977 | -0.01 | 0.99 | -0.25 | 0.75 | -0.23 | 0.77 | 23.44 | 28.32 |  | 100 | 10 | 10
2019-09-04 | 9:51 | 1.6797 | 0 | 1 | -0.24 | 0.76 | -0.23 | 0.77 | 23.44 | 26.37
2019-09-04 | 9:51 | 1.7969 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 23.44 | 28.32 |  | 100 | 11 | 9.1 | end
2019-09-04 | 9:51 | 1.8906 | 0.05 | 1.05 | -0.27 | 0.73 | -0.24 | 0.76 | 22.46 | 28.32 |  | 100 | 11 | 9.1
2019-09-04 | 9:51 | 1.9883 | 0.05 | 1.05 | -0.26 | 0.74 | -0.23 | 0.77 | 23.44 | 27.34 |  | 100 | 11 | 9.1
2019-09-04 | 9:51 | 2.0898 | 0.06 | 1.06 | -0.29 | 0.71 | -0.25 | 0.75 | 24.41 | 27.34
2019-09-04 | 9:51 | 2.2188 | 0.08 | 1.08 | -0.28 | 0.72 | -0.25 | 0.75 | 23.44 | 29.3 |  |  |  | 9.55 | average
2019-09-04 | 9:51 | 2.2969 | 0.07 | 1.07 | -0.27 | 0.73 | -0.26 | 0.74 | 22.46 | 29.3
2019-09-04 | 9:51 | 2.3984 | 0.05 | 1.05 | -0.3 | 0.7 | -0.25 | 0.75 | 22.46 | 28.32
2019-09-04 | 9:51 | 2.5195 | 0.08 | 1.08 | -0.29 | 0.71 | -0.26 | 0.74 | 25.39 | 29.3
2019-09-04 | 9:51 | 2.6094 | 0.05 | 1.05 | -0.28 | 0.72 | -0.27 | 0.73 | 23.44 | 30.27
2019-09-04 | 9:51 | 2.7188 | 0.08 | 1.08 | -0.29 | 0.71 | -0.27 | 0.73 | 23.44 | 28.32
2019-09-04 | 9:51 | 2.8203 | 0.05 | 1.05 | -0.27 | 0.73 | -0.25 | 0.75 | 22.46 | 27.34
2019-09-04 | 9:51 | 2.918 | 0 | 1 | -0.26 | 0.74 | -0.24 | 0.76 | 23.44 | 27.34
2019-09-04 | 9:51 | 3.0195 | 0 | 1 | -0.24 | 0.76 | -0.24 | 0.76 | 23.44 | 27.34
2019-09-04 | 9:51 | 3.1484 | 0 | 1 | -0.23 | 0.77 | -0.24 | 0.76 | 21.48 | 26.37
2019-09-04 | 9:51 | 3.2188 | 0 | 1 | -0.24 | 0.76 | -0.24 | 0.76 | 22.46 | 27.34
2019-09-04 | 9:51 | 3.3281 | 0.04 | 1.04 | -0.26 | 0.74 | -0.24 | 0.76 | 22.46 | 27.34
2019-09-04 | 9:51 | 3.4297 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 23.44 | 27.34
2019-09-04 | 9:51 | 3.5273 | 0.07 | 1.07 | -0.29 | 0.71 | -0.25 | 0.75 | 22.46 | 26.37
2019-09-04 | 9:51 | 3.6484 | 0.07 | 1.07 | -0.29 | 0.71 | -0.25 | 0.75 | 22.46 | 27.34
2019-09-04 | 9:51 | 3.7578 | 0.09 | 1.09 | -0.28 | 0.72 | -0.24 | 0.76 | 22.46 | 27.34
2019-09-04 | 9:51 | 3.8398 | 0.07 | 1.07 | -0.3 | 0.7 | -0.26 | 0.74 | 22.46 | 28.32
2019-09-04 | 9:51 | 3.9375 | 0.06 | 1.06 | -0.28 | 0.72 | -0.25 | 0.75 | 22.46 | 27.34
2019-09-04 | 9:51 | 4.0469 | 0.06 | 1.06 | -0.28 | 0.72 | -0.26 | 0.74 | 23.44 | 27.34
2019-09-04 | 9:51 | 4.1484 | 0.07 | 1.07 | -0.29 | 0.71 | -0.26 | 0.74 | 22.46 | 26.37
2019-09-04 | 9:51 | 4.2578 | 0.06 | 1.06 | -0.3 | 0.7 | -0.25 | 0.75 | 22.46 | 27.34
2019-09-04 | 9:51 | 4.3594 | 0.02 | 1.02 | -0.25 | 0.75 | -0.25 | 0.75 | 22.46 | 27.34
2019-09-04 | 9:51 | 4.457 | 0.02 | 1.02 | -0.25 | 0.75 | -0.24 | 0.76 | 23.44 | 29.3 |  | Pressure equilibrium from 175 seconds
2019-09-04 | 9:51 | 4.5781 | 0 | 1 | -0.24 | 0.76 | -0.23 | 0.77 | 23.44 | 27.34
2019-09-04 | 9:51 | 4.668 | -0.01 | 0.99 | -0.25 | 0.75 | -0.22 | 0.78 | 22.46 | 27.34
2019-09-04 | 9:51 | 4.7695 | 0.01 | 1.01 | -0.23 | 0.77 | -0.22 | 0.78 | 22.46 | 28.32
2019-09-04 | 9:51 | 4.8789 | 0.05 | 1.05 | -0.27 | 0.73 | -0.23 | 0.77 | 23.44 | 27.34
2019-09-04 | 9:51 | 4.9805 | 0.06 | 1.06 | -0.27 | 0.73 | -0.24 | 0.76 | 23.44 | 28.32
2019-09-04 | 9:51 | 5.0781 | 0.04 | 1.04 | -0.28 | 0.72 | -0.24 | 0.76 | 22.46 | 27.34
2019-09-04 | 9:51 | 5.1875 | 0.09 | 1.09 | -0.28 | 0.72 | -0.24 | 0.76 | 22.46 | 27.34
2019-09-04 | 9:51 | 5.2773 | 0.06 | 1.06 | -0.29 | 0.71 | -0.25 | 0.75 | 23.44 | 27.34
2019-09-04 | 9:51 | 5.3906 | 0.08 | 1.08 | -0.29 | 0.71 | -0.24 | 0.76 | 22.46 | 27.34
2019-09-04 | 9:51 | 5.4883 | 0.07 | 1.07 | -0.29 | 0.71 | -0.25 | 0.75 | 22.46 | 27.34
2019-09-04 | 9:51 | 5.5898 | 0.07 | 1.07 | -0.28 | 0.72 | -0.26 | 0.74 | 22.46 | 27.34
2019-09-04 | 9:51 | 5.6875 | 0.08 | 1.08 | -0.3 | 0.7 | -0.26 | 0.74 | 22.46 | 27.34
2019-09-04 | 9:51 | 5.7891 | 0.07 | 1.07 | -0.28 | 0.72 | -0.26 | 0.74 | 23.44 | 28.32
2019-09-04 | 9:51 | 5.8984 | 0.01 | 1.01 | -0.24 | 0.76 | -0.25 | 0.75 | 22.46 | 28.32
2019-09-04 | 9:51 | 6 | 0.01 | 1.01 | -0.23 | 0.77 | -0.23 | 0.77 | 23.44 | 29.3
2019-09-04 | 9:51 | 6.1094 | 0 | 1 | -0.24 | 0.76 | -0.24 | 0.76 | 23.44 | 28.32
2019-09-04 | 9:51 | 6.207 | -0.02 | 0.98 | -0.23 | 0.77 | -0.22 | 0.78 | 22.46 | 28.32
2019-09-04 | 9:51 | 6.3203 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 23.44 | 29.3
2019-09-04 | 9:51 | 6.4375 | 0.05 | 1.05 | -0.27 | 0.73 | -0.23 | 0.77 | 22.46 | 26.37
2019-09-04 | 9:51 | 6.5391 | 0.06 | 1.06 | -0.27 | 0.73 | -0.24 | 0.76 | 22.46 | 28.32
2019-09-04 | 9:51 | 6.6406 | 0.08 | 1.08 | -0.28 | 0.72 | -0.25 | 0.75 | 22.46 | 27.34
2019-09-04 | 9:51 | 6.7383 | 0.06 | 1.06 | -0.28 | 0.72 | -0.25 | 0.75 | 22.46 | 28.32
2019-09-04 | 9:51 | 6.8398 | 0.08 | 1.08 | -0.28 | 0.72 | -0.25 | 0.75 | 23.44 | 28.32
2019-09-04 | 9:51 | 6.9375 | 0.08 | 1.08 | -0.28 | 0.72 | -0.26 | 0.74 | 23.44 | 28.32
2019-09-04 | 9:51 | 7.0273 | 0.07 | 1.07 | -0.29 | 0.71 | -0.24 | 0.76 | 22.46 | 28.32
2019-09-04 | 9:51 | 7.1289 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 22.46 | 27.34
2019-09-04 | 9:51 | 7.2383 | 0.05 | 1.05 | -0.29 | 0.71 | -0.26 | 0.74 | 23.44 | 28.32
2019-09-04 | 9:51 | 7.3594 | 0.04 | 1.04 | -0.26 | 0.74 | -0.24 | 0.76 | 22.46 | 28.32
2019-09-04 | 9:51 | 7.4375 | 0.02 | 1.02 | -0.24 | 0.76 | -0.24 | 0.76 | 22.46 | 29.3
2019-09-04 | 9:51 | 7.5469 | 0 | 1 | -0.24 | 0.76 | -0.24 | 0.76 | 22.46 | 29.3 |  | Temperature equilibrium from 50 seconds
2019-09-04 | 9:51 | 7.6484 | 0.01 | 1.01 | -0.24 | 0.76 | -0.23 | 0.77 | 22.46 | 29.3
2019-09-04 | 9:51 | 7.75 | -0.02 | 0.98 | -0.23 | 0.77 | -0.22 | 0.78 | 22.46 | 29.3 |  | Min HE outlet temperature between 50 and 240 seconds is: |  |  |  | 72.27 |  |  | average SC bath temp: | 26.8991
2019-09-04 | 9:51 | 7.8477 | 0.06 | 1.06 | -0.26 | 0.74 | -0.23 | 0.77 | 24.41 | 28.32 |  | Max HE outlet temperature between 50 and 240 seconds is: |  |  |  | 76.17
2019-09-04 | 9:51 | 7.9492 | 0.08 | 1.08 | -0.27 | 0.73 | -0.24 | 0.76 | 22.46 | 29.3
2019-09-04 | 9:51 | 8.0469 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 23.44 | 29.3 |  | The average HE outlet temperature between 50 and 240 seonds is: |  |  |  |  | 73.8371
2019-09-04 | 9:51 | 8.1602 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 22.46 | 29.3
2019-09-04 | 9:51 | 8.2695 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 22.46 | 29.3 |  | The number of temperature data points measured is: |  |  |  | 1852
2019-09-04 | 9:51 | 8.3594 | 0.11 | 1.11 | -0.29 | 0.71 | -0.25 | 0.75 | 23.44 | 29.3
2019-09-04 | 9:51 | 8.4688 | 0.06 | 1.06 | -0.28 | 0.72 | -0.25 | 0.75 | 23.44 | 30.27 |  | STDEV | 0.80951
2019-09-04 | 9:51 | 8.5703 | 0.08 | 1.08 | -0.28 | 0.72 | -0.25 | 0.75 | 23.44 | 30.27
2019-09-04 | 9:51 | 8.6797 | 0.07 | 1.07 | -0.29 | 0.71 | -0.24 | 0.76 | 23.44 | 30.27
2019-09-04 | 9:51 | 8.7891 | 0.07 | 1.07 | -0.28 | 0.72 | -0.26 | 0.74 | 23.44 | 31.25
2019-09-04 | 9:51 | 8.8906 | 0.02 | 1.02 | -0.25 | 0.75 | -0.24 | 0.76 | 22.46 | 32.23 |  | Obersvere smaller sample of pressure data to see what is happening with regards to pulses
2019-09-04 | 9:51 | 8.9805 | 0 | 1 | -0.25 | 0.75 | -0.24 | 0.76 | 25.39 | 32.23
2019-09-04 | 9:51 | 9.0781 | 0.01 | 1.01 | -0.22 | 0.78 | -0.24 | 0.76 | 23.44 | 32.23
2019-09-04 | 9:51 | 9.1875 | 0 | 1 | -0.24 | 0.76 | -0.22 | 0.78 | 23.44 | 32.23
2019-09-04 | 9:51 | 9.2891 | 0.04 | 1.04 | -0.24 | 0.76 | -0.22 | 0.78 | 23.44 | 29.3
2019-09-04 | 9:51 | 9.3906 | 0.05 | 1.05 | -0.27 | 0.73 | -0.23 | 0.77 | 23.44 | 31.25
2019-09-04 | 9:51 | 9.4883 | 0.07 | 1.07 | -0.27 | 0.73 | -0.24 | 0.76 | 23.44 | 32.23
2019-09-04 | 9:51 | 9.5977 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 23.44 | 31.25
2019-09-04 | 9:51 | 9.7305 | 0.05 | 1.05 | -0.26 | 0.74 | -0.24 | 0.76 | 22.46 | 31.25
2019-09-04 | 9:51 | 9.8281 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 23.44 | 32.23
2019-09-04 | 9:51 | 9.9297 | 0.08 | 1.08 | -0.27 | 0.73 | -0.24 | 0.76 | 23.44 | 32.23
2019-09-04 | 9:51 | 10.0195 | 0.08 | 1.08 | -0.29 | 0.71 | -0.24 | 0.76 | 25.39 | 31.25
2019-09-04 | 9:51 | 10.1406 | 0.07 | 1.07 | -0.29 | 0.71 | -0.26 | 0.74 | 22.46 | 32.23
2019-09-04 | 9:51 | 10.2305 | 0.07 | 1.07 | -0.29 | 0.71 | -0.27 | 0.73 | 22.46 | 33.2
2019-09-04 | 9:51 | 10.3203 | 0.05 | 1.05 | -0.27 | 0.73 | -0.26 | 0.74 | 23.44 | 32.23
2019-09-04 | 9:51 | 10.4297 | 0.03 | 1.03 | -0.24 | 0.76 | -0.23 | 0.77 | 22.46 | 32.23
2019-09-04 | 9:51 | 10.5195 | 0.03 | 1.03 | -0.23 | 0.77 | -0.24 | 0.76 | 22.46 | 32.23
2019-09-04 | 9:51 | 10.6172 | 0.03 | 1.03 | -0.24 | 0.76 | -0.23 | 0.77 | 22.46 | 33.2
2019-09-04 | 9:51 | 10.7305 | 0 | 1 | -0.2 | 0.8 | -0.23 | 0.77 | 23.44 | 31.25
2019-09-04 | 9:51 | 10.8281 | 0.06 | 1.06 | -0.25 | 0.75 | -0.23 | 0.77 | 22.46 | 32.23
2019-09-04 | 9:51 | 10.9297 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 22.46 | 34.18
2019-09-04 | 9:51 | 11.0391 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 22.46 | 33.2 |  | The flat time periods is the period the valve is shut.
2019-09-04 | 9:51 | 11.1406 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 23.44 | 33.2
2019-09-04 | 9:51 | 11.2383 | 0.08 | 1.08 | -0.27 | 0.73 | -0.24 | 0.76 | 24.41 | 33.2 |  | 2 seconds
2019-09-04 | 9:51 | 11.3398 | 0.07 | 1.07 | -0.29 | 0.71 | -0.24 | 0.76 | 22.46 | 34.18 |  | 5 intervals
2019-09-04 | 9:51 | 11.4492 | 0.06 | 1.06 | -0.27 | 0.73 | -0.26 | 0.74 | 22.46 | 31.25 |  | each interval is 400ms
2019-09-04 | 9:51 | 11.5469 | 0.08 | 1.08 | -0.29 | 0.71 | -0.25 | 0.75 | 23.44 | 33.2
2019-09-04 | 9:51 | 11.6484 | 0.05 | 1.05 | -0.27 | 0.73 | -0.25 | 0.75 | 23.44 | 34.18 |  | when the valve opens the boiler outlet pressure drops as steam enters the heat exchanger and condenses to create negative pressure
2019-09-04 | 9:51 | 11.75 | 0.07 | 1.07 | -0.29 | 0.71 | -0.26 | 0.74 | 22.46 | 33.2 |  | when the valve closes the boiler pressure rises again towards atmospheric
2019-09-04 | 9:51 | 11.8594 | 0.03 | 1.03 | -0.25 | 0.75 | -0.24 | 0.76 | 23.44 | 33.2
2019-09-04 | 9:51 | 11.957 | 0.01 | 1.01 | -0.23 | 0.77 | -0.23 | 0.77 | 23.44 | 34.18 |  | when the valve opens the heat exchanger pressure increases as steam is admitted to the heat exchanger
2019-09-04 | 9:51 | 12.0586 | 0.01 | 1.01 | -0.24 | 0.76 | -0.22 | 0.78 | 22.46 | 34.18 |  | once the valve shuts the steam is condensed and returns to equilibrium pressure. This is the pressure that would be seen in the condenser
2019-09-04 | 9:51 | 12.168 | -0.01 | 0.99 | -0.23 | 0.77 | -0.23 | 0.77 | 22.46 | 32.23
2019-09-04 | 9:51 | 12.2695 | -0.01 | 0.99 | -0.21 | 0.79 | -0.22 | 0.78 | 23.44 | 33.2
2019-09-04 | 9:51 | 12.3672 | 0.07 | 1.07 | -0.27 | 0.73 | -0.23 | 0.77 | 23.44 | 34.18
2019-09-04 | 9:51 | 12.4805 | 0.06 | 1.06 | -0.27 | 0.73 | -0.24 | 0.76 | 23.44 | 34.18 |  | importantly, the condensation happens quickly
2019-09-04 | 9:51 | 12.5781 | 0.08 | 1.08 | -0.27 | 0.73 | -0.24 | 0.76 | 22.46 | 34.18
2019-09-04 | 9:51 | 12.6797 | 0.07 | 1.07 | -0.27 | 0.73 | -0.25 | 0.75 | 22.46 | 34.18 |  | minimum boiler pressure after 175 seconds is: |  |  |  | 0.77 |  | average Pb | 0.95432
2019-09-04 | 9:51 | 12.7891 | 0.07 | 1.07 | -0.27 | 0.73 | -0.25 | 0.75 | 22.46 | 35.16 |  | maximum boiler pressure after 175 seconds is: |  |  |  | 1.04
2019-09-04 | 9:51 | 12.8789 | 0.08 | 1.08 | -0.28 | 0.72 | -0.23 | 0.77 | 23.44 | 32.23
2019-09-04 | 9:51 | 12.9883 | 0.08 | 1.08 | -0.28 | 0.72 | -0.25 | 0.75 | 22.46 | 35.16 |  | minimum heat exchanger pressure after 175 seconds is: |  |  |  | 0.17 |  | average Phe | 0.2311
2019-09-04 | 9:51 | 13.0898 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 22.46 | 36.13 |  | maximum heat exchanger pressure after 175 seconds is: |  |  |  | 0.38
2019-09-04 | 9:51 | 13.1875 | 0.08 | 1.08 | -0.28 | 0.72 | -0.25 | 0.75 | 24.41 | 35.16
2019-09-04 | 9:51 | 13.2891 | 0.08 | 1.08 | -0.27 | 0.73 | -0.26 | 0.74 | 23.44 | 36.13
2019-09-04 | 9:51 | 13.4102 | 0.02 | 1.02 | -0.26 | 0.74 | -0.26 | 0.74 | 23.44 | 36.13
2019-09-04 | 9:51 | 13.5195 | 0.01 | 1.01 | -0.25 | 0.75 | -0.23 | 0.77 | 23.44 | 36.13
2019-09-04 | 9:51 | 13.6094 | 0 | 1 | -0.25 | 0.75 | -0.23 | 0.77 | 22.46 | 34.18
2019-09-04 | 9:51 | 13.707 | 0 | 1 | -0.24 | 0.76 | -0.23 | 0.77 | 24.41 | 35.16
2019-09-04 | 9:51 | 13.8203 | 0.05 | 1.05 | -0.27 | 0.73 | -0.24 | 0.76 | 22.46 | 36.13
2019-09-04 | 9:51 | 13.918 | 0.09 | 1.09 | -0.29 | 0.71 | -0.26 | 0.74 | 24.41 | 36.13
2019-09-04 | 9:51 | 14.0391 | 0.07 | 1.07 | -0.31 | 0.69 | -0.27 | 0.73 | 24.41 | 36.13
2019-09-04 | 9:51 | 14.1484 | 0.07 | 1.07 | -0.32 | 0.68 | -0.27 | 0.73 | 24.41 | 37.11
2019-09-04 | 9:51 | 14.2383 | 0.07 | 1.07 | -0.33 | 0.67 | -0.29 | 0.71 | 26.37 | 36.13
2019-09-04 | 9:51 | 14.3398 | 0.06 | 1.06 | -0.34 | 0.66 | -0.3 | 0.7 | 27.34 | 33.2
2019-09-04 | 9:51 | 14.4492 | 0.07 | 1.07 | -0.35 | 0.65 | -0.32 | 0.68 | 29.3 | 36.13
2019-09-04 | 9:51 | 14.5469 | 0.07 | 1.07 | -0.36 | 0.64 | -0.33 | 0.67 | 31.25 | 35.16
2019-09-04 | 9:51 | 14.6406 | 0.07 | 1.07 | -0.37 | 0.63 | -0.34 | 0.66 | 33.2 | 37.11
2019-09-04 | 9:51 | 14.7383 | 0.06 | 1.06 | -0.37 | 0.63 | -0.35 | 0.65 | 36.13 | 37.11
2019-09-04 | 9:51 | 14.8398 | 0.06 | 1.06 | -0.36 | 0.64 | -0.35 | 0.65 | 40.04 | 38.09
2019-09-04 | 9:51 | 14.9375 | 0.02 | 1.02 | -0.33 | 0.67 | -0.33 | 0.67 | 41.99 | 39.06
2019-09-04 | 9:51 | 15.0391 | -0.01 | 0.99 | -0.31 | 0.69 | -0.32 | 0.68 | 43.95 | 36.13
2019-09-04 | 9:51 | 15.1484 | -0.02 | 0.98 | -0.32 | 0.68 | -0.34 | 0.66 | 46.88 | 37.11
2019-09-04 | 9:51 | 15.25 | -0.02 | 0.98 | -0.31 | 0.69 | -0.34 | 0.66 | 48.83 | 37.11
2019-09-04 | 9:51 | 15.3477 | 0.05 | 1.05 | -0.4 | 0.6 | -0.37 | 0.63 | 51.76 | 38.09
2019-09-04 | 9:51 | 15.457 | 0.05 | 1.05 | -0.4 | 0.6 | -0.38 | 0.62 | 51.76 | 37.11
2019-09-04 | 9:51 | 15.5469 | 0.07 | 1.07 | -0.43 | 0.57 | -0.39 | 0.61 | 54.69 | 37.11
2019-09-04 | 9:51 | 15.6602 | 0.04 | 1.04 | -0.44 | 0.56 | -0.4 | 0.6 | 56.64 | 37.11
2019-09-04 | 9:51 | 15.7695 | 0.08 | 1.08 | -0.45 | 0.55 | -0.41 | 0.59 | 58.59 | 36.13
2019-09-04 | 9:51 | 15.8672 | 0.07 | 1.07 | -0.45 | 0.55 | -0.42 | 0.58 | 59.57 | 38.09
2019-09-04 | 9:51 | 15.9688 | 0.07 | 1.07 | -0.47 | 0.53 | -0.42 | 0.58 | 60.55 | 38.09
2019-09-04 | 9:51 | 16.0703 | 0.06 | 1.06 | -0.47 | 0.53 | -0.43 | 0.57 | 61.52 | 37.11
2019-09-04 | 9:51 | 16.1797 | 0.08 | 1.08 | -0.49 | 0.51 | -0.43 | 0.57 | 62.5 | 38.09
2019-09-04 | 9:51 | 16.2773 | 0.06 | 1.06 | -0.49 | 0.51 | -0.44 | 0.56 | 62.5 | 38.09
2019-09-04 | 9:51 | 16.3789 | 0.03 | 1.03 | -0.43 | 0.57 | -0.44 | 0.56 | 64.45 | 39.06
2019-09-04 | 9:51 | 16.4805 | -0.01 | 0.99 | -0.4 | 0.6 | -0.42 | 0.58 | 65.43 | 37.11
2019-09-04 | 9:51 | 16.5781 | -0.03 | 0.97 | -0.38 | 0.62 | -0.42 | 0.58 | 65.43 | 38.09
2019-09-04 | 9:51 | 16.6875 | -0.06 | 0.94 | -0.37 | 0.63 | -0.41 | 0.59 | 64.45 | 38.09
2019-09-04 | 9:51 | 16.7891 | 0.04 | 1.04 | -0.42 | 0.58 | -0.42 | 0.58 | 64.45 | 38.09
2019-09-04 | 9:51 | 16.8906 | 0.06 | 1.06 | -0.49 | 0.51 | -0.45 | 0.55 | 64.45 | 37.11
2019-09-04 | 9:51 | 17 | 0.08 | 1.08 | -0.49 | 0.51 | -0.46 | 0.54 | 65.43 | 37.11
2019-09-04 | 9:51 | 17.0977 | 0.05 | 1.05 | -0.5 | 0.5 | -0.45 | 0.55 | 65.43 | 38.09
2019-09-04 | 9:51 | 17.1992 | 0.07 | 1.07 | -0.49 | 0.51 | -0.46 | 0.54 | 65.43 | 35.16
2019-09-04 | 9:51 | 17.2969 | 0.06 | 1.06 | -0.52 | 0.48 | -0.46 | 0.54 | 65.43 | 38.09
2019-09-04 | 9:51 | 17.4102 | 0.06 | 1.06 | -0.52 | 0.48 | -0.49 | 0.51 | 67.38 | 37.11
2019-09-04 | 9:51 | 17.5078 | 0.08 | 1.08 | -0.52 | 0.48 | -0.49 | 0.51 | 65.43 | 37.11
2019-09-04 | 9:51 | 17.6094 | 0.06 | 1.06 | -0.52 | 0.48 | -0.48 | 0.52 | 65.43 | 39.06
2019-09-04 | 9:51 | 17.7188 | 0.08 | 1.08 | -0.52 | 0.48 | -0.49 | 0.51 | 66.41 | 37.11
2019-09-04 | 9:51 | 17.8203 | 0.07 | 1.07 | -0.52 | 0.48 | -0.48 | 0.52 | 66.41 | 38.09
2019-09-04 | 9:51 | 17.918 | 0 | 1 | -0.43 | 0.57 | -0.46 | 0.54 | 67.38 | 35.16
2019-09-04 | 9:51 | 18.0273 | -0.02 | 0.98 | -0.42 | 0.58 | -0.45 | 0.55 | 65.43 | 38.09
2019-09-04 | 9:51 | 18.1602 | -0.03 | 0.97 | -0.42 | 0.58 | -0.45 | 0.55 | 64.45 | 37.11
2019-09-04 | 9:51 | 18.2305 | -0.06 | 0.94 | -0.4 | 0.6 | -0.43 | 0.57 | 66.41 | 37.11
2019-09-04 | 9:51 | 18.3398 | 0.05 | 1.05 | -0.51 | 0.49 | -0.47 | 0.53 | 65.43 | 38.09
2019-09-04 | 9:51 | 18.457 | 0.05 | 1.05 | -0.53 | 0.47 | -0.48 | 0.52 | 64.45 | 38.09
2019-09-04 | 9:51 | 18.5586 | 0.07 | 1.07 | -0.53 | 0.47 | -0.5 | 0.5 | 63.48 | 37.11
2019-09-04 | 9:51 | 18.6602 | 0.07 | 1.07 | -0.54 | 0.46 | -0.49 | 0.51 | 63.48 | 34.18
2019-09-04 | 9:51 | 18.7578 | 0.07 | 1.07 | -0.54 | 0.46 | -0.49 | 0.51 | 63.48 | 38.09
2019-09-04 | 9:51 | 18.8477 | 0.09 | 1.09 | -0.53 | 0.47 | -0.5 | 0.5 | 64.45 | 36.13
2019-09-04 | 9:51 | 18.957 | 0.07 | 1.07 | -0.53 | 0.47 | -0.49 | 0.51 | 63.48 | 35.16
2019-09-04 | 9:51 | 19.0586 | 0.06 | 1.06 | -0.53 | 0.47 | -0.5 | 0.5 | 64.45 | 36.13
2019-09-04 | 9:51 | 19.1484 | 0.08 | 1.08 | -0.54 | 0.46 | -0.5 | 0.5 | 64.45 | 36.13
2019-09-04 | 9:51 | 19.2578 | 0.04 | 1.04 | -0.55 | 0.45 | -0.51 | 0.49 | 63.48 | 36.13
2019-09-04 | 9:51 | 19.3594 | 0.05 | 1.05 | -0.53 | 0.47 | -0.5 | 0.5 | 64.45 | 33.2
2019-09-04 | 9:51 | 19.457 | -0.03 | 0.97 | -0.45 | 0.55 | -0.49 | 0.51 | 64.45 | 35.16
2019-09-04 | 9:51 | 19.5586 | -0.05 | 0.95 | -0.44 | 0.56 | -0.48 | 0.52 | 65.43 | 36.13
2019-09-04 | 9:51 | 19.668 | -0.04 | 0.96 | -0.44 | 0.56 | -0.48 | 0.52 | 64.45 | 36.13
2019-09-04 | 9:51 | 19.7695 | -0.05 | 0.95 | -0.41 | 0.59 | -0.49 | 0.51 | 65.43 | 35.16
2019-09-04 | 9:51 | 19.8672 | 0.08 | 1.08 | -0.55 | 0.45 | -0.51 | 0.49 | 65.43 | 37.11
2019-09-04 | 9:51 | 19.9688 | 0.05 | 1.05 | -0.56 | 0.44 | -0.52 | 0.48 | 65.43 | 36.13
2019-09-04 | 9:51 | 20.0781 | 0.06 | 1.06 | -0.55 | 0.45 | -0.52 | 0.48 | 65.43 | 33.2
2019-09-04 | 9:51 | 20.1797 | 0.05 | 1.05 | -0.56 | 0.44 | -0.53 | 0.47 | 64.45 | 36.13
2019-09-04 | 9:51 | 20.2773 | 0.07 | 1.07 | -0.56 | 0.44 | -0.52 | 0.48 | 63.48 | 34.18
2019-09-04 | 9:51 | 20.3906 | 0.07 | 1.07 | -0.56 | 0.44 | -0.53 | 0.47 | 64.45 | 35.16
2019-09-04 | 9:51 | 20.4883 | 0.06 | 1.06 | -0.56 | 0.44 | -0.53 | 0.47 | 64.45 | 34.18
2019-09-04 | 9:51 | 20.6172 | 0.07 | 1.07 | -0.57 | 0.43 | -0.53 | 0.47 | 64.45 | 35.16
2019-09-04 | 9:51 | 20.7188 | 0.07 | 1.07 | -0.58 | 0.42 | -0.54 | 0.46 | 64.45 | 34.18
2019-09-04 | 9:51 | 20.8086 | 0.06 | 1.06 | -0.57 | 0.43 | -0.54 | 0.46 | 64.45 | 32.23
2019-09-04 | 9:51 | 20.9297 | 0 | 1 | -0.5 | 0.5 | -0.53 | 0.47 | 64.45 | 34.18
2019-09-04 | 9:51 | 21 | -0.04 | 0.96 | -0.46 | 0.54 | -0.52 | 0.48 | 64.45 | 34.18
2019-09-04 | 9:51 | 21.1094 | -0.05 | 0.95 | -0.43 | 0.57 | -0.52 | 0.48 | 64.45 | 34.18
2019-09-04 | 9:51 | 21.207 | -0.09 | 0.91 | -0.44 | 0.56 | -0.51 | 0.49 | 64.45 | 34.18
2019-09-04 | 9:51 | 21.3086 | 0.05 | 1.05 | -0.55 | 0.45 | -0.53 | 0.47 | 64.45 | 34.18
2019-09-04 | 9:51 | 21.4102 | 0.06 | 1.06 | -0.56 | 0.44 | -0.53 | 0.47 | 65.43 | 35.16
2019-09-04 | 9:51 | 21.5195 | 0.07 | 1.07 | -0.58 | 0.42 | -0.56 | 0.44 | 65.43 | 32.23
2019-09-04 | 9:51 | 21.6172 | 0.06 | 1.06 | -0.58 | 0.42 | -0.55 | 0.45 | 65.43 | 35.16
2019-09-04 | 9:51 | 21.7188 | 0.07 | 1.07 | -0.58 | 0.42 | -0.54 | 0.46 | 64.45 | 34.18
2019-09-04 | 9:51 | 21.8281 | 0.07 | 1.07 | -0.58 | 0.42 | -0.55 | 0.45 | 66.41 | 35.16
2019-09-04 | 9:51 | 21.9297 | 0.08 | 1.08 | -0.58 | 0.42 | -0.55 | 0.45 | 65.43 | 34.18
2019-09-04 | 9:51 | 22.0273 | 0.08 | 1.08 | -0.58 | 0.42 | -0.56 | 0.44 | 66.41 | 34.18
2019-09-04 | 9:51 | 22.1406 | 0.07 | 1.07 | -0.6 | 0.4 | -0.56 | 0.44 | 66.41 | 33.2
2019-09-04 | 9:51 | 22.2383 | 0.05 | 1.05 | -0.6 | 0.4 | -0.55 | 0.45 | 65.43 | 30.27
2019-09-04 | 9:51 | 22.3398 | 0.06 | 1.06 | -0.61 | 0.39 | -0.55 | 0.45 | 64.45 | 32.23
2019-09-04 | 9:51 | 22.4805 | -0.04 | 0.96 | -0.49 | 0.51 | -0.55 | 0.45 | 64.45 | 34.18
2019-09-04 | 9:51 | 22.5586 | -0.06 | 0.94 | -0.47 | 0.53 | -0.53 | 0.47 | 64.45 | 33.2
2019-09-04 | 9:51 | 22.6484 | -0.07 | 0.93 | -0.47 | 0.53 | -0.54 | 0.46 | 65.43 | 33.2
2019-09-04 | 9:51 | 22.7695 | -0.05 | 0.95 | -0.45 | 0.55 | -0.52 | 0.48 | 64.45 | 33.2
2019-09-04 | 9:51 | 22.8594 | 0.06 | 1.06 | -0.59 | 0.41 | -0.55 | 0.45 | 65.43 | 32.23
2019-09-04 | 9:51 | 22.957 | 0.06 | 1.06 | -0.6 | 0.4 | -0.57 | 0.43 | 64.45 | 30.27
2019-09-04 | 9:51 | 23.0586 | 0.07 | 1.07 | -0.61 | 0.39 | -0.57 | 0.43 | 64.45 | 33.2
2019-09-04 | 9:51 | 23.1602 | 0.06 | 1.06 | -0.6 | 0.4 | -0.58 | 0.42 | 64.45 | 32.23
2019-09-04 | 9:51 | 23.2695 | 0.06 | 1.06 | -0.61 | 0.39 | -0.59 | 0.41 | 65.43 | 33.2
2019-09-04 | 9:51 | 23.3672 | 0.08 | 1.08 | -0.63 | 0.37 | -0.59 | 0.41 | 64.45 | 32.23
2019-09-04 | 9:51 | 23.4688 | 0.08 | 1.08 | -0.63 | 0.37 | -0.59 | 0.41 | 64.45 | 32.23
2019-09-04 | 9:51 | 23.5703 | 0.06 | 1.06 | -0.63 | 0.37 | -0.6 | 0.4 | 65.43 | 32.23
2019-09-04 | 9:51 | 23.6797 | 0.08 | 1.08 | -0.64 | 0.36 | -0.6 | 0.4 | 64.45 | 31.25
2019-09-04 | 9:51 | 23.7773 | 0.08 | 1.08 | -0.64 | 0.36 | -0.6 | 0.4 | 67.38 | 33.2
2019-09-04 | 9:51 | 23.8789 | 0.04 | 1.04 | -0.62 | 0.38 | -0.6 | 0.4 | 66.41 | 32.23
2019-09-04 | 9:51 | 23.9805 | -0.02 | 0.98 | -0.5 | 0.5 | -0.58 | 0.42 | 64.45 | 32.23
2019-09-04 | 9:51 | 24.1094 | -0.08 | 0.92 | -0.48 | 0.52 | -0.57 | 0.43 | 65.43 | 33.2
2019-09-04 | 9:51 | 24.207 | -0.08 | 0.92 | -0.49 | 0.51 | -0.57 | 0.43 | 64.45 | 31.25
2019-09-04 | 9:51 | 24.3086 | -0.02 | 0.98 | -0.53 | 0.47 | -0.56 | 0.44 | 64.45 | 32.23
2019-09-04 | 9:51 | 24.3906 | 0.05 | 1.05 | -0.63 | 0.37 | -0.6 | 0.4 | 65.43 | 31.25
2019-09-04 | 9:51 | 24.5 | 0.06 | 1.06 | -0.63 | 0.37 | -0.6 | 0.4 | 65.43 | 31.25
2019-09-04 | 9:51 | 24.5977 | 0.07 | 1.07 | -0.65 | 0.35 | -0.58 | 0.42 | 65.43 | 31.25
2019-09-04 | 9:51 | 24.707 | 0.08 | 1.08 | -0.64 | 0.36 | -0.59 | 0.41 | 65.43 | 31.25
2019-09-04 | 9:51 | 24.8086 | 0.05 | 1.05 | -0.64 | 0.36 | -0.61 | 0.39 | 65.43 | 32.23
2019-09-04 | 9:51 | 24.9102 | 0.07 | 1.07 | -0.65 | 0.35 | -0.61 | 0.39 | 64.45 | 31.25
2019-09-04 | 9:51 | 25.0078 | 0.06 | 1.06 | -0.66 | 0.34 | -0.62 | 0.38 | 64.45 | 31.25
2019-09-04 | 9:51 | 25.1094 | 0.07 | 1.07 | -0.66 | 0.34 | -0.61 | 0.39 | 64.45 | 29.3
2019-09-04 | 9:51 | 25.207 | 0.07 | 1.07 | -0.66 | 0.34 | -0.62 | 0.38 | 64.45 | 30.27
2019-09-04 | 9:51 | 25.3203 | 0.07 | 1.07 | -0.65 | 0.35 | -0.63 | 0.37 | 66.41 | 31.25
2019-09-04 | 9:51 | 25.4297 | -0.01 | 0.99 | -0.58 | 0.42 | -0.61 | 0.39 | 64.45 | 31.25
2019-09-04 | 9:51 | 25.5273 | -0.05 | 0.95 | -0.54 | 0.46 | -0.59 | 0.41 | 64.45 | 31.25
2019-09-04 | 9:51 | 25.6289 | -0.06 | 0.94 | -0.5 | 0.5 | -0.58 | 0.42 | 65.43 | 31.25
2019-09-04 | 9:51 | 25.7383 | -0.09 | 0.91 | -0.48 | 0.52 | -0.57 | 0.43 | 66.41 | 30.27
2019-09-04 | 9:51 | 25.8398 | 0.04 | 1.04 | -0.62 | 0.38 | -0.61 | 0.39 | 65.43 | 29.3
2019-09-04 | 9:51 | 25.9297 | 0.07 | 1.07 | -0.64 | 0.36 | -0.6 | 0.4 | 64.45 | 31.25
2019-09-04 | 9:51 | 26.0391 | 0.08 | 1.08 | -0.66 | 0.34 | -0.6 | 0.4 | 64.45 | 30.27
2019-09-04 | 9:51 | 26.1406 | 0.05 | 1.05 | -0.66 | 0.34 | -0.61 | 0.39 | 65.43 | 31.25
2019-09-04 | 9:51 | 26.2383 | 0.06 | 1.06 | -0.66 | 0.34 | -0.62 | 0.38 | 63.48 | 31.25
2019-09-04 | 9:51 | 26.3398 | 0.08 | 1.08 | -0.66 | 0.34 | -0.63 | 0.37 | 64.45 | 32.23
2019-09-04 | 9:51 | 26.4688 | 0.08 | 1.08 | -0.67 | 0.33 | -0.62 | 0.38 | 64.45 | 31.25
2019-09-04 | 9:51 | 26.5586 | 0.07 | 1.07 | -0.66 | 0.34 | -0.64 | 0.36 | 65.43 | 29.3
2019-09-04 | 9:51 | 26.668 | 0.06 | 1.06 | -0.67 | 0.33 | -0.62 | 0.38 | 64.45 | 31.25
2019-09-04 | 9:51 | 26.7891 | 0.06 | 1.06 | -0.67 | 0.33 | -0.64 | 0.36 | 65.43 | 30.27
2019-09-04 | 9:51 | 26.8984 | 0.09 | 1.09 | -0.66 | 0.34 | -0.64 | 0.36 | 66.41 | 33.2
2019-09-04 | 9:51 | 26.9883 | -0.04 | 0.96 | -0.55 | 0.45 | -0.62 | 0.38 | 65.43 | 31.25
2019-09-04 | 9:51 | 27.0898 | -0.08 | 0.92 | -0.51 | 0.49 | -0.62 | 0.38 | 66.41 | 31.25
2019-09-04 | 9:51 | 27.1875 | -0.1 | 0.9 | -0.51 | 0.49 | -0.61 | 0.39 | 64.45 | 31.25
2019-09-04 | 9:51 | 27.2891 | -0.09 | 0.91 | -0.48 | 0.52 | -0.59 | 0.41 | 65.43 | 31.25
2019-09-04 | 9:51 | 27.3789 | 0.05 | 1.05 | -0.66 | 0.34 | -0.62 | 0.38 | 65.43 | 31.25
2019-09-04 | 9:51 | 27.4688 | 0.05 | 1.05 | -0.65 | 0.35 | -0.63 | 0.37 | 64.45 | 30.27
2019-09-04 | 9:51 | 27.5781 | 0.06 | 1.06 | -0.66 | 0.34 | -0.63 | 0.37 | 65.43 | 31.25
2019-09-04 | 9:51 | 27.6875 | 0.08 | 1.08 | -0.68 | 0.32 | -0.63 | 0.37 | 66.41 | 30.27
2019-09-04 | 9:51 | 27.7891 | 0.07 | 1.07 | -0.68 | 0.32 | -0.64 | 0.36 | 65.43 | 32.23
2019-09-04 | 9:51 | 27.8906 | 0.06 | 1.06 | -0.68 | 0.32 | -0.65 | 0.35 | 65.43 | 32.23
2019-09-04 | 9:51 | 27.9883 | 0.07 | 1.07 | -0.7 | 0.3 | -0.65 | 0.35 | 65.43 | 30.27
2019-09-04 | 9:51 | 28.0977 | 0.08 | 1.08 | -0.69 | 0.31 | -0.65 | 0.35 | 65.43 | 32.23
2019-09-04 | 9:51 | 28.1992 | 0.08 | 1.08 | -0.69 | 0.31 | -0.65 | 0.35 | 67.38 | 32.23
2019-09-04 | 9:51 | 28.2969 | 0.06 | 1.06 | -0.68 | 0.32 | -0.65 | 0.35 | 65.43 | 32.23
2019-09-04 | 9:51 | 28.4102 | 0.04 | 1.04 | -0.67 | 0.33 | -0.65 | 0.35 | 64.45 | 30.27
2019-09-04 | 9:51 | 28.5078 | -0.05 | 0.95 | -0.56 | 0.44 | -0.65 | 0.35 | 64.45 | 29.3
2019-09-04 | 9:51 | 28.6094 | -0.09 | 0.91 | -0.53 | 0.47 | -0.63 | 0.37 | 64.45 | 32.23
2019-09-04 | 9:51 | 28.707 | -0.1 | 0.9 | -0.51 | 0.49 | -0.61 | 0.39 | 64.45 | 29.3
2019-09-04 | 9:51 | 28.8203 | 0.03 | 1.03 | -0.65 | 0.35 | -0.63 | 0.37 | 63.48 | 29.3
2019-09-04 | 9:51 | 28.9102 | 0.07 | 1.07 | -0.69 | 0.31 | -0.65 | 0.35 | 64.45 | 29.3
2019-09-04 | 9:51 | 29.0273 | 0.05 | 1.05 | -0.69 | 0.31 | -0.66 | 0.34 | 64.45 | 30.27
2019-09-04 | 9:51 | 29.1289 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 64.45 | 30.27
2019-09-04 | 9:51 | 29.2188 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 65.43 | 31.25
2019-09-04 | 9:51 | 29.3281 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 63.48 | 29.3
2019-09-04 | 9:51 | 29.4297 | 0.06 | 1.06 | -0.7 | 0.3 | -0.64 | 0.36 | 63.48 | 28.32
2019-09-04 | 9:51 | 29.5469 | 0.07 | 1.07 | -0.69 | 0.31 | -0.66 | 0.34 | 64.45 | 30.27
2019-09-04 | 9:51 | 29.6484 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 64.45 | 30.27
2019-09-04 | 9:51 | 29.75 | 0.06 | 1.06 | -0.71 | 0.29 | -0.65 | 0.35 | 65.43 | 30.27
2019-09-04 | 9:51 | 29.8477 | 0.09 | 1.09 | -0.71 | 0.29 | -0.67 | 0.33 | 64.45 | 29.3
2019-09-04 | 9:51 | 29.957 | 0 | 1 | -0.63 | 0.37 | -0.66 | 0.34 | 66.41 | 30.27
2019-09-04 | 9:51 | 30.0469 | -0.08 | 0.92 | -0.55 | 0.45 | -0.64 | 0.36 | 64.45 | 29.3
2019-09-04 | 9:51 | 30.1484 | -0.09 | 0.91 | -0.54 | 0.46 | -0.64 | 0.36 | 64.45 | 29.3
2019-09-04 | 9:51 | 30.25 | -0.11 | 0.89 | -0.51 | 0.49 | -0.61 | 0.39 | 64.45 | 30.27
2019-09-04 | 9:51 | 30.3594 | 0.04 | 1.04 | -0.67 | 0.33 | -0.64 | 0.36 | 64.45 | 29.3
2019-09-04 | 9:51 | 30.457 | 0.05 | 1.05 | -0.69 | 0.31 | -0.64 | 0.36 | 65.43 | 29.3
2019-09-04 | 9:51 | 30.5781 | 0.07 | 1.07 | -0.69 | 0.31 | -0.65 | 0.35 | 65.43 | 30.27
2019-09-04 | 9:51 | 30.6797 | 0.05 | 1.05 | -0.7 | 0.3 | -0.66 | 0.34 | 64.45 | 30.27
2019-09-04 | 9:51 | 30.7695 | 0.06 | 1.06 | -0.69 | 0.31 | -0.68 | 0.32 | 64.45 | 29.3
2019-09-04 | 9:51 | 30.8672 | 0.09 | 1.09 | -0.71 | 0.29 | -0.66 | 0.34 | 63.48 | 30.27
2019-09-04 | 9:51 | 30.9805 | 0.05 | 1.05 | -0.72 | 0.28 | -0.66 | 0.34 | 63.48 | 30.27
2019-09-04 | 9:51 | 31.0781 | 0.07 | 1.07 | -0.7 | 0.3 | -0.67 | 0.33 | 63.48 | 30.27
2019-09-04 | 9:51 | 31.1797 | 0.06 | 1.06 | -0.72 | 0.28 | -0.67 | 0.33 | 64.45 | 29.3
2019-09-04 | 9:51 | 31.2969 | 0.07 | 1.07 | -0.71 | 0.29 | -0.66 | 0.34 | 64.45 | 29.3
2019-09-04 | 9:51 | 31.3906 | 0.06 | 1.06 | -0.7 | 0.3 | -0.67 | 0.33 | 64.45 | 31.25
2019-09-04 | 9:51 | 31.5 | -0.02 | 0.98 | -0.61 | 0.39 | -0.66 | 0.34 | 64.45 | 29.3
2019-09-04 | 9:51 | 31.6094 | -0.06 | 0.94 | -0.58 | 0.42 | -0.64 | 0.36 | 64.45 | 29.3
2019-09-04 | 9:51 | 31.6875 | -0.1 | 0.9 | -0.53 | 0.47 | -0.63 | 0.37 | 65.43 | 29.3
2019-09-04 | 9:51 | 31.7891 | -0.04 | 0.96 | -0.58 | 0.42 | -0.63 | 0.37 | 65.43 | 30.27
2019-09-04 | 9:51 | 31.8906 | 0.05 | 1.05 | -0.67 | 0.33 | -0.63 | 0.37 | 65.43 | 30.27
2019-09-04 | 9:51 | 32 | 0.06 | 1.06 | -0.68 | 0.32 | -0.65 | 0.35 | 64.45 | 30.27
2019-09-04 | 9:51 | 32.0977 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 64.45 | 29.3
2019-09-04 | 9:51 | 32.1992 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 64.45 | 28.32
2019-09-04 | 9:51 | 32.3086 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 63.48 | 29.3
2019-09-04 | 9:51 | 32.4102 | 0.07 | 1.07 | -0.7 | 0.3 | -0.66 | 0.34 | 63.48 | 29.3
2019-09-04 | 9:51 | 32.5273 | 0.06 | 1.06 | -0.69 | 0.31 | -0.67 | 0.33 | 64.45 | 31.25
2019-09-04 | 9:51 | 32.6172 | 0.05 | 1.05 | -0.71 | 0.29 | -0.66 | 0.34 | 63.48 | 29.3
2019-09-04 | 9:51 | 32.7188 | 0.06 | 1.06 | -0.71 | 0.29 | -0.65 | 0.35 | 64.45 | 30.27
2019-09-04 | 9:51 | 32.8281 | 0.05 | 1.05 | -0.71 | 0.29 | -0.66 | 0.34 | 63.48 | 29.3
2019-09-04 | 9:51 | 32.9297 | 0.03 | 1.03 | -0.67 | 0.33 | -0.66 | 0.34 | 63.48 | 28.32
2019-09-04 | 9:51 | 33.0391 | -0.05 | 0.95 | -0.58 | 0.42 | -0.65 | 0.35 | 65.43 | 29.3
2019-09-04 | 9:51 | 33.1484 | -0.06 | 0.94 | -0.55 | 0.45 | -0.64 | 0.36 | 63.48 | 29.3
2019-09-04 | 9:51 | 33.25 | -0.1 | 0.9 | -0.52 | 0.48 | -0.62 | 0.38 | 65.43 | 29.3
2019-09-04 | 9:51 | 33.3398 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 64.45 | 29.3
2019-09-04 | 9:51 | 33.4375 | 0.04 | 1.04 | -0.68 | 0.32 | -0.65 | 0.35 | 64.45 | 29.3
2019-09-04 | 9:51 | 33.5391 | 0.06 | 1.06 | -0.69 | 0.31 | -0.64 | 0.36 | 65.43 | 30.27
2019-09-04 | 9:51 | 33.6602 | 0.07 | 1.07 | -0.69 | 0.31 | -0.64 | 0.36 | 64.45 | 27.34
2019-09-04 | 9:51 | 33.7578 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 63.48 | 29.3
2019-09-04 | 9:51 | 33.8477 | 0.07 | 1.07 | -0.7 | 0.3 | -0.66 | 0.34 | 65.43 | 30.27
2019-09-04 | 9:51 | 33.9492 | 0.07 | 1.07 | -0.7 | 0.3 | -0.66 | 0.34 | 64.45 | 31.25
2019-09-04 | 9:51 | 34.0469 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 65.43 | 31.25
2019-09-04 | 9:51 | 34.1602 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 64.45 | 30.27
2019-09-04 | 9:51 | 34.25 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 66.41 | 31.25
2019-09-04 | 9:51 | 34.3672 | 0.09 | 1.09 | -0.71 | 0.29 | -0.67 | 0.33 | 65.43 | 27.34
2019-09-04 | 9:51 | 34.5 | -0.01 | 0.99 | -0.62 | 0.38 | -0.66 | 0.34 | 65.43 | 29.3
2019-09-04 | 9:51 | 34.5898 | -0.07 | 0.93 | -0.56 | 0.44 | -0.64 | 0.36 | 64.45 | 29.3
2019-09-04 | 9:51 | 34.6797 | -0.08 | 0.92 | -0.55 | 0.45 | -0.65 | 0.35 | 65.43 | 30.27
2019-09-04 | 9:51 | 34.7773 | -0.11 | 0.89 | -0.52 | 0.48 | -0.63 | 0.37 | 65.43 | 29.3
2019-09-04 | 9:51 | 34.8789 | 0.04 | 1.04 | -0.68 | 0.32 | -0.64 | 0.36 | 64.45 | 29.3
2019-09-04 | 9:51 | 34.9805 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 65.43 | 30.27
2019-09-04 | 9:51 | 35.0781 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 66.41 | 28.32
2019-09-04 | 9:51 | 35.1875 | 0.05 | 1.05 | -0.7 | 0.3 | -0.65 | 0.35 | 66.41 | 29.3
2019-09-04 | 9:51 | 35.2891 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 65.43 | 29.3
2019-09-04 | 9:51 | 35.3906 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 65.43 | 30.27
2019-09-04 | 9:51 | 35.5 | 0.08 | 1.08 | -0.71 | 0.29 | -0.66 | 0.34 | 66.41 | 29.3
2019-09-04 | 9:51 | 35.5898 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 66.41 | 29.3
2019-09-04 | 9:51 | 35.707 | 0.08 | 1.08 | -0.7 | 0.3 | -0.67 | 0.33 | 67.38 | 30.27
2019-09-04 | 9:51 | 35.8086 | 0.07 | 1.07 | -0.72 | 0.28 | -0.67 | 0.33 | 67.38 | 28.32
2019-09-04 | 9:51 | 35.918 | 0.09 | 1.09 | -0.72 | 0.28 | -0.67 | 0.33 | 67.38 | 28.32
2019-09-04 | 9:51 | 36.0195 | -0.03 | 0.97 | -0.61 | 0.39 | -0.66 | 0.34 | 67.38 | 31.25
2019-09-04 | 9:51 | 36.1172 | -0.09 | 0.91 | -0.56 | 0.44 | -0.65 | 0.35 | 68.36 | 28.32
2019-09-04 | 9:51 | 36.207 | -0.08 | 0.92 | -0.53 | 0.47 | -0.64 | 0.36 | 67.38 | 29.3
2019-09-04 | 9:51 | 36.3203 | 0.04 | 1.04 | -0.65 | 0.35 | -0.63 | 0.37 | 67.38 | 29.3
2019-09-04 | 9:51 | 36.418 | 0.04 | 1.04 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 30.27
2019-09-04 | 9:51 | 36.5469 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 67.38 | 27.34
2019-09-04 | 9:51 | 36.6484 | 0.08 | 1.08 | -0.69 | 0.31 | -0.66 | 0.34 | 67.38 | 28.32
2019-09-04 | 9:51 | 36.7383 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 67.38 | 29.3
2019-09-04 | 9:51 | 36.8477 | 0.07 | 1.07 | -0.69 | 0.31 | -0.66 | 0.34 | 69.34 | 28.32
2019-09-04 | 9:51 | 36.9492 | 0.05 | 1.05 | -0.7 | 0.3 | -0.66 | 0.34 | 69.34 | 29.3
2019-09-04 | 9:51 | 37.0273 | 0.08 | 1.08 | -0.7 | 0.3 | -0.66 | 0.34 | 68.36 | 29.3
2019-09-04 | 9:51 | 37.1289 | 0.06 | 1.06 | -0.72 | 0.28 | -0.66 | 0.34 | 68.36 | 29.3
2019-09-04 | 9:51 | 37.2383 | 0.07 | 1.07 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 28.32
2019-09-04 | 9:51 | 37.3398 | 0.09 | 1.09 | -0.71 | 0.29 | -0.68 | 0.32 | 68.36 | 28.32
2019-09-04 | 9:51 | 37.4492 | 0.05 | 1.05 | -0.68 | 0.32 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 9:51 | 37.5781 | -0.06 | 0.94 | -0.59 | 0.41 | -0.65 | 0.35 | 69.34 | 29.3
2019-09-04 | 9:51 | 37.6797 | -0.07 | 0.93 | -0.57 | 0.43 | -0.64 | 0.36 | 69.34 | 29.3
2019-09-04 | 9:51 | 37.7695 | -0.1 | 0.9 | -0.54 | 0.46 | -0.64 | 0.36 | 69.34 | 29.3
2019-09-04 | 9:51 | 37.8477 | 0.04 | 1.04 | -0.67 | 0.33 | -0.64 | 0.36 | 70.31 | 31.25
2019-09-04 | 9:51 | 37.957 | 0.05 | 1.05 | -0.68 | 0.32 | -0.65 | 0.35 | 70.31 | 29.3
2019-09-04 | 9:51 | 38.0586 | 0.07 | 1.07 | -0.7 | 0.3 | -0.65 | 0.35 | 72.27 | 29.3
2019-09-04 | 9:51 | 38.1602 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 28.32
2019-09-04 | 9:51 | 38.2695 | 0.06 | 1.06 | -0.7 | 0.3 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 9:51 | 38.3672 | 0.05 | 1.05 | -0.69 | 0.31 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 9:51 | 38.4883 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 9:51 | 38.5781 | 0.08 | 1.08 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 9:51 | 38.6797 | 0.07 | 1.07 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 9:51 | 38.7773 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 9:51 | 38.8906 | 0.06 | 1.06 | -0.72 | 0.28 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 9:51 | 38.9883 | -0.02 | 0.98 | -0.6 | 0.4 | -0.66 | 0.34 | 71.29 | 28.32
2019-09-04 | 9:51 | 39.0898 | -0.07 | 0.93 | -0.58 | 0.42 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 9:51 | 39.1875 | -0.09 | 0.91 | -0.54 | 0.46 | -0.65 | 0.35 | 69.34 | 28.32
2019-09-04 | 9:51 | 39.2891 | -0.12 | 0.88 | -0.53 | 0.47 | -0.63 | 0.37 | 70.31 | 29.3
2019-09-04 | 9:51 | 39.3984 | 0.04 | 1.04 | -0.68 | 0.32 | -0.64 | 0.36 | 70.31 | 28.32
2019-09-04 | 9:51 | 39.5 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 70.31 | 29.3
2019-09-04 | 9:51 | 39.5977 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 70.31 | 28.32
2019-09-04 | 9:51 | 39.707 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 70.31 | 30.27
2019-09-04 | 9:51 | 39.7969 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 9:51 | 39.9102 | 0.06 | 1.06 | -0.7 | 0.3 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 9:51 | 40.0273 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:51 | 40.1172 | 0.07 | 1.07 | -0.7 | 0.3 | -0.66 | 0.34 | 70.31 | 30.27
2019-09-04 | 9:51 | 40.2188 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 9:51 | 40.3203 | 0.06 | 1.06 | -0.72 | 0.28 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 9:51 | 40.4297 | 0.04 | 1.04 | -0.68 | 0.32 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 9:51 | 40.5273 | -0.08 | 0.92 | -0.59 | 0.41 | -0.65 | 0.35 | 71.29 | 28.32
2019-09-04 | 9:51 | 40.6289 | -0.09 | 0.91 | -0.55 | 0.45 | -0.64 | 0.36 | 71.29 | 29.3
2019-09-04 | 9:51 | 40.7305 | -0.11 | 0.89 | -0.54 | 0.46 | -0.64 | 0.36 | 70.31 | 27.34
2019-09-04 | 9:51 | 40.8398 | 0.03 | 1.03 | -0.67 | 0.33 | -0.66 | 0.34 | 71.29 | 28.32
2019-09-04 | 9:51 | 40.9375 | 0.05 | 1.05 | -0.68 | 0.32 | -0.65 | 0.35 | 70.31 | 29.3
2019-09-04 | 9:51 | 41.0391 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 71.29 | 28.32
2019-09-04 | 9:51 | 41.1484 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 71.29 | 29.3
2019-09-04 | 9:51 | 41.25 | 0.06 | 1.06 | -0.69 | 0.31 | -0.67 | 0.33 | 71.29 | 28.32
2019-09-04 | 9:51 | 41.3477 | 0.08 | 1.08 | -0.7 | 0.3 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 9:51 | 41.4492 | 0.05 | 1.05 | -0.7 | 0.3 | -0.67 | 0.33 | 71.29 | 27.34
2019-09-04 | 9:51 | 41.5469 | 0.07 | 1.07 | -0.71 | 0.29 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 9:51 | 41.6602 | 0.05 | 1.05 | -0.71 | 0.29 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 9:51 | 41.75 | 0.09 | 1.09 | -0.71 | 0.29 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 9:51 | 41.8594 | 0.06 | 1.06 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 9:51 | 41.9688 | -0.01 | 0.99 | -0.64 | 0.36 | -0.65 | 0.35 | 71.29 | 29.3
2019-09-04 | 9:51 | 42.0703 | -0.08 | 0.92 | -0.56 | 0.44 | -0.65 | 0.35 | 72.27 | 29.3
2019-09-04 | 9:51 | 42.1875 | -0.11 | 0.89 | -0.55 | 0.45 | -0.63 | 0.37 | 71.29 | 28.32
2019-09-04 | 9:51 | 42.2969 | -0.11 | 0.89 | -0.53 | 0.47 | -0.63 | 0.37 | 71.29 | 30.27
2019-09-04 | 9:51 | 42.3906 | 0.04 | 1.04 | -0.68 | 0.32 | -0.65 | 0.35 | 71.29 | 28.32
2019-09-04 | 9:51 | 42.4883 | 0.04 | 1.04 | -0.68 | 0.32 | -0.64 | 0.36 | 71.29 | 30.27
2019-09-04 | 9:51 | 42.5781 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 71.29 | 29.3
2019-09-04 | 9:51 | 42.6875 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 30.27
2019-09-04 | 9:51 | 42.7891 | 0.05 | 1.05 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 29.3
2019-09-04 | 9:51 | 42.8906 | 0.07 | 1.07 | -0.69 | 0.31 | -0.65 | 0.35 | 70.31 | 28.32
2019-09-04 | 9:51 | 43 | 0.07 | 1.07 | -0.7 | 0.3 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 9:51 | 43.0977 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 71.29 | 28.32
2019-09-04 | 9:51 | 43.1992 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 72.27 | 29.3
2019-09-04 | 9:51 | 43.3281 | 0.07 | 1.07 | -0.72 | 0.28 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 9:51 | 43.4297 | 0.05 | 1.05 | -0.69 | 0.31 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 9:51 | 43.5195 | -0.06 | 0.94 | -0.59 | 0.41 | -0.67 | 0.33 | 73.24 | 29.3
2019-09-04 | 9:52 | 43.6289 | -0.1 | 0.9 | -0.55 | 0.45 | -0.64 | 0.36 | 72.27 | 30.27
2019-09-04 | 9:52 | 43.7383 | -0.1 | 0.9 | -0.54 | 0.46 | -0.64 | 0.36 | 71.29 | 28.32
2019-09-04 | 9:52 | 43.8281 | 0.01 | 1.01 | -0.64 | 0.36 | -0.63 | 0.37 | 72.27 | 29.3
2019-09-04 | 9:52 | 43.918 | 0.04 | 1.04 | -0.68 | 0.32 | -0.65 | 0.35 | 71.29 | 29.3
2019-09-04 | 9:52 | 44.0195 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 28.32
2019-09-04 | 9:52 | 44.1602 | 0.05 | 1.05 | -0.7 | 0.3 | -0.65 | 0.35 | 72.27 | 30.27
2019-09-04 | 9:52 | 44.25 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 72.27 | 27.34
2019-09-04 | 9:52 | 44.3398 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 44.4297 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 72.27 | 28.32
2019-09-04 | 9:52 | 44.5469 | 0.05 | 1.05 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 9:52 | 44.6484 | 0.07 | 1.07 | -0.71 | 0.29 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 44.7383 | 0.07 | 1.07 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 44.8477 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 9:52 | 44.9492 | 0.01 | 1.01 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 45.0586 | -0.04 | 0.96 | -0.59 | 0.41 | -0.65 | 0.35 | 73.24 | 29.3
2019-09-04 | 9:52 | 45.1602 | -0.06 | 0.94 | -0.56 | 0.44 | -0.64 | 0.36 | 74.22 | 29.3
2019-09-04 | 9:52 | 45.2773 | -0.09 | 0.91 | -0.54 | 0.46 | -0.64 | 0.36 | 72.27 | 29.3
2019-09-04 | 9:52 | 45.3789 | 0.03 | 1.03 | -0.67 | 0.33 | -0.64 | 0.36 | 72.27 | 28.32
2019-09-04 | 9:52 | 45.457 | 0.04 | 1.04 | -0.68 | 0.32 | -0.65 | 0.35 | 72.27 | 29.3
2019-09-04 | 9:52 | 45.5586 | 0.06 | 1.06 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 30.27
2019-09-04 | 9:52 | 45.668 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 72.27 | 27.34
2019-09-04 | 9:52 | 45.7695 | 0.04 | 1.04 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 45.8672 | 0.08 | 1.08 | -0.69 | 0.31 | -0.64 | 0.36 | 72.27 | 28.32
2019-09-04 | 9:52 | 45.9688 | 0.07 | 1.07 | -0.71 | 0.29 | -0.65 | 0.35 | 72.27 | 29.3
2019-09-04 | 9:52 | 46.0781 | 0.05 | 1.05 | -0.72 | 0.28 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 46.1875 | 0.07 | 1.07 | -0.72 | 0.28 | -0.67 | 0.33 | 72.27 | 28.32
2019-09-04 | 9:52 | 46.3203 | 0.07 | 1.07 | -0.7 | 0.3 | -0.66 | 0.34 | 72.27 | 29.3
2019-09-04 | 9:52 | 46.3984 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 72.27 | 27.34
2019-09-04 | 9:52 | 46.5078 | -0.05 | 0.95 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 46.6094 | -0.1 | 0.9 | -0.57 | 0.43 | -0.65 | 0.35 | 72.27 | 29.3
2019-09-04 | 9:52 | 46.6992 | -0.1 | 0.9 | -0.55 | 0.45 | -0.64 | 0.36 | 72.27 | 29.3
2019-09-04 | 9:52 | 46.7969 | -0.09 | 0.91 | -0.54 | 0.46 | -0.63 | 0.37 | 72.27 | 28.32
2019-09-04 | 9:52 | 46.8984 | 0.04 | 1.04 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 29.3
2019-09-04 | 9:52 | 47 | 0.05 | 1.05 | -0.7 | 0.3 | -0.64 | 0.36 | 72.27 | 28.32
2019-09-04 | 9:52 | 47.1094 | 0.05 | 1.05 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 47.207 | 0.05 | 1.05 | -0.7 | 0.3 | -0.64 | 0.36 | 72.27 | 28.32
2019-09-04 | 9:52 | 47.3203 | 0.05 | 1.05 | -0.7 | 0.3 | -0.65 | 0.35 | 72.27 | 29.3
2019-09-04 | 9:52 | 47.4375 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 29.3
2019-09-04 | 9:52 | 47.5391 | 0.07 | 1.07 | -0.7 | 0.3 | -0.67 | 0.33 | 72.27 | 28.32
2019-09-04 | 9:52 | 47.6172 | 0.07 | 1.07 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 9:52 | 47.707 | 0.06 | 1.06 | -0.72 | 0.28 | -0.67 | 0.33 | 72.27 | 28.32
2019-09-04 | 9:52 | 47.8281 | 0.08 | 1.08 | -0.71 | 0.29 | -0.66 | 0.34 | 75.2 | 30.27
2019-09-04 | 9:52 | 47.9297 | 0.04 | 1.04 | -0.69 | 0.31 | -0.67 | 0.33 | 75.2 | 29.3
2019-09-04 | 9:52 | 48.0391 | -0.06 | 0.94 | -0.59 | 0.41 | -0.65 | 0.35 | 74.22 | 28.32
2019-09-04 | 9:52 | 48.1406 | -0.08 | 0.92 | -0.57 | 0.43 | -0.64 | 0.36 | 74.22 | 29.3
2019-09-04 | 9:52 | 48.2383 | -0.1 | 0.9 | -0.55 | 0.45 | -0.63 | 0.37 | 73.24 | 28.32
2019-09-04 | 9:52 | 48.3398 | 0.03 | 1.03 | -0.68 | 0.32 | -0.65 | 0.35 | 72.27 | 28.32
2019-09-04 | 9:52 | 48.4492 | 0.05 | 1.05 | -0.7 | 0.3 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 48.5391 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 72.27 | 28.32
2019-09-04 | 9:52 | 48.6406 | 0.05 | 1.05 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 48.75 | 0.07 | 1.07 | -0.69 | 0.31 | -0.65 | 0.35 | 72.27 | 29.3
2019-09-04 | 9:52 | 48.8477 | 0.07 | 1.07 | -0.7 | 0.3 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 48.9492 | 0.09 | 1.09 | -0.71 | 0.29 | -0.67 | 0.33 | 72.27 | 28.32
2019-09-04 | 9:52 | 49.0703 | 0.08 | 1.08 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 49.1797 | 0.07 | 1.07 | -0.72 | 0.28 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:52 | 49.2695 | 0.07 | 1.07 | -0.72 | 0.28 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 9:52 | 49.3672 | 0.06 | 1.06 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 49.5 | -0.02 | 0.98 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 49.5898 | -0.08 | 0.92 | -0.58 | 0.42 | -0.64 | 0.36 | 73.24 | 28.32
2019-09-04 | 9:52 | 49.6875 | -0.1 | 0.9 | -0.57 | 0.43 | -0.65 | 0.35 | 75.2 | 29.3
2019-09-04 | 9:52 | 49.7773 | -0.11 | 0.89 | -0.55 | 0.45 | -0.63 | 0.37 | 73.24 | 28.32
2019-09-04 | 9:52 | 49.8789 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 74.22 | 28.32
2019-09-04 | 9:52 | 49.9805 | 0.04 | 1.04 | -0.7 | 0.3 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 50.0898 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 75.2 | 29.3 | CWT2 Equilibirum
2019-09-04 | 9:52 | 50.1797 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 73.24 | 28.32
2019-09-04 | 9:52 | 50.2891 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 72.27 | 28.32
2019-09-04 | 9:52 | 50.3984 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 50.5 | 0.08 | 1.08 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 50.6094 | 0.07 | 1.07 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 50.6992 | 0.06 | 1.06 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 50.8086 | 0.07 | 1.07 | -0.71 | 0.29 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 9:52 | 50.9102 | 0.04 | 1.04 | -0.72 | 0.28 | -0.68 | 0.32 | 73.24 | 29.3
2019-09-04 | 9:52 | 51.0078 | -0.04 | 0.96 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 29.3
2019-09-04 | 9:52 | 51.1289 | -0.11 | 0.89 | -0.58 | 0.42 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 9:52 | 51.2305 | -0.11 | 0.89 | -0.58 | 0.42 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 51.3203 | -0.01 | 0.99 | -0.65 | 0.35 | -0.63 | 0.37 | 73.24 | 29.3
2019-09-04 | 9:52 | 51.4297 | 0.04 | 1.04 | -0.71 | 0.29 | -0.64 | 0.36 | 72.27 | 28.32
2019-09-04 | 9:52 | 51.5273 | 0.04 | 1.04 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 51.6289 | 0.05 | 1.05 | -0.7 | 0.3 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 51.7305 | 0.05 | 1.05 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 51.8398 | 0.07 | 1.07 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 29.3
2019-09-04 | 9:52 | 51.9375 | 0.07 | 1.07 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 30.27
2019-09-04 | 9:52 | 52.0391 | 0.07 | 1.07 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 29.3
2019-09-04 | 9:52 | 52.1602 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 75.2 | 28.32
2019-09-04 | 9:52 | 52.2578 | 0.06 | 1.06 | -0.72 | 0.28 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:52 | 52.3594 | 0.07 | 1.07 | -0.72 | 0.28 | -0.69 | 0.31 | 74.22 | 29.3
2019-09-04 | 9:52 | 52.457 | 0.03 | 1.03 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 29.3
2019-09-04 | 9:52 | 52.5469 | -0.07 | 0.93 | -0.6 | 0.4 | -0.65 | 0.35 | 74.22 | 30.27
2019-09-04 | 9:52 | 52.6602 | -0.11 | 0.89 | -0.58 | 0.42 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 52.7578 | -0.1 | 0.9 | -0.58 | 0.42 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 9:52 | 52.8594 | 0.04 | 1.04 | -0.72 | 0.28 | -0.65 | 0.35 | 73.24 | 28.32
2019-09-04 | 9:52 | 52.957 | 0.04 | 1.04 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 53.0703 | 0.05 | 1.05 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 53.168 | 0.06 | 1.06 | -0.73 | 0.27 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 53.2695 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 53.3789 | 0.06 | 1.06 | -0.73 | 0.27 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 9:52 | 53.4805 | 0.05 | 1.05 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 53.5898 | 0.05 | 1.05 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 53.6797 | 0.06 | 1.06 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 53.7969 | 0.07 | 1.07 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 9:52 | 53.8984 | 0.05 | 1.05 | -0.74 | 0.26 | -0.67 | 0.33 | 75.2 | 29.3
2019-09-04 | 9:52 | 54.0078 | -0.01 | 0.99 | -0.65 | 0.35 | -0.65 | 0.35 | 75.2 | 29.3
2019-09-04 | 9:52 | 54.1094 | -0.09 | 0.91 | -0.6 | 0.4 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 54.1992 | -0.08 | 0.92 | -0.58 | 0.42 | -0.63 | 0.37 | 73.24 | 28.32
2019-09-04 | 9:52 | 54.3086 | -0.11 | 0.89 | -0.57 | 0.43 | -0.64 | 0.36 | 72.27 | 29.3
2019-09-04 | 9:52 | 54.4102 | 0.04 | 1.04 | -0.71 | 0.29 | -0.65 | 0.35 | 73.24 | 29.3
2019-09-04 | 9:52 | 54.5195 | 0.06 | 1.06 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 54.6094 | 0.05 | 1.05 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 54.7188 | 0.07 | 1.07 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 54.8203 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 54.918 | 0.05 | 1.05 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 55.0391 | 0.06 | 1.06 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 29.3
2019-09-04 | 9:52 | 55.1172 | 0.07 | 1.07 | -0.73 | 0.27 | -0.67 | 0.33 | 72.27 | 28.32
2019-09-04 | 9:52 | 55.2188 | 0.08 | 1.08 | -0.73 | 0.27 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 55.3398 | 0.06 | 1.06 | -0.73 | 0.27 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 55.457 | 0.04 | 1.04 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 55.5273 | -0.05 | 0.95 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 55.6406 | -0.1 | 0.9 | -0.6 | 0.4 | -0.65 | 0.35 | 74.22 | 29.3
2019-09-04 | 9:52 | 55.75 | -0.11 | 0.89 | -0.59 | 0.41 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 9:52 | 55.8398 | 0.02 | 1.02 | -0.69 | 0.31 | -0.65 | 0.35 | 75.2 | 28.32
2019-09-04 | 9:52 | 55.9375 | 0.04 | 1.04 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 29.3
2019-09-04 | 9:52 | 56.0391 | 0.05 | 1.05 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 29.3
2019-09-04 | 9:52 | 56.1484 | 0.07 | 1.07 | -0.72 | 0.28 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 56.2695 | 0.07 | 1.07 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 56.3594 | 0.07 | 1.07 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 56.4688 | 0.06 | 1.06 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 56.5703 | 0.08 | 1.08 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 56.668 | 0.07 | 1.07 | -0.73 | 0.27 | -0.68 | 0.32 | 74.22 | 29.3
2019-09-04 | 9:52 | 56.7773 | 0.06 | 1.06 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 56.8672 | 0.06 | 1.06 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 56.9688 | 0.02 | 1.02 | -0.7 | 0.3 | -0.67 | 0.33 | 73.24 | 29.3
2019-09-04 | 9:52 | 57.0703 | -0.02 | 0.98 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 57.168 | -0.11 | 0.89 | -0.6 | 0.4 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 57.2773 | -0.09 | 0.91 | -0.61 | 0.39 | -0.65 | 0.35 | 74.22 | 28.32
2019-09-04 | 9:52 | 57.3789 | 0.04 | 1.04 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 28.32
2019-09-04 | 9:52 | 57.4805 | 0.04 | 1.04 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 29.3
2019-09-04 | 9:52 | 57.5898 | 0.04 | 1.04 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 57.6875 | 0.06 | 1.06 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 57.7891 | 0.06 | 1.06 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 57.8906 | 0.06 | 1.06 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 29.3
2019-09-04 | 9:52 | 58 | 0.06 | 1.06 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 58.0977 | 0.06 | 1.06 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 58.1992 | 0.07 | 1.07 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 29.3
2019-09-04 | 9:52 | 58.3086 | 0.07 | 1.07 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 58.4102 | 0.06 | 1.06 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 58.5078 | -0.02 | 0.98 | -0.65 | 0.35 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 58.6172 | -0.08 | 0.92 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 58.7188 | -0.09 | 0.91 | -0.62 | 0.38 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 58.8086 | -0.03 | 0.97 | -0.69 | 0.31 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 9:52 | 58.918 | 0.05 | 1.05 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 59.0273 | 0.05 | 1.05 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 27.34
2019-09-04 | 9:52 | 59.1289 | 0.06 | 1.06 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 59.2305 | 0.07 | 1.07 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 29.3
2019-09-04 | 9:52 | 59.3594 | 0.07 | 1.07 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 59.457 | 0.07 | 1.07 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 59.5586 | 0.06 | 1.06 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 59.6406 | 0.05 | 1.05 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 59.7383 | 0.06 | 1.06 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 59.8477 | 0.05 | 1.05 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 29.3
2019-09-04 | 9:52 | 59.9492 | 0.04 | 1.04 | -0.73 | 0.27 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 60.0469 | -0.06 | 0.94 | -0.64 | 0.36 | -0.67 | 0.33 | 75.2 | 29.3
2019-09-04 | 9:52 | 60.1602 | -0.08 | 0.92 | -0.63 | 0.37 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 60.2578 | -0.1 | 0.9 | -0.6 | 0.4 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 60.3594 | 0.04 | 1.04 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 60.457 | 0.04 | 1.04 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 60.5703 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 60.6797 | 0.05 | 1.05 | -0.74 | 0.26 | -0.66 | 0.34 | 72.27 | 27.34
2019-09-04 | 9:52 | 60.7773 | 0.06 | 1.06 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 60.8789 | 0.06 | 1.06 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 60.9805 | 0.05 | 1.05 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 29.3
2019-09-04 | 9:52 | 61.0781 | 0.06 | 1.06 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 61.1797 | 0.09 | 1.09 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 61.2891 | 0.07 | 1.07 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 61.3906 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 29.3
2019-09-04 | 9:52 | 61.5 | 0 | 1 | -0.69 | 0.31 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 61.5977 | -0.1 | 0.9 | -0.66 | 0.34 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 61.7188 | -0.09 | 0.91 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 29.3
2019-09-04 | 9:52 | 61.8203 | -0.11 | 0.89 | -0.64 | 0.36 | -0.64 | 0.36 | 73.24 | 27.34
2019-09-04 | 9:52 | 61.918 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 62.0195 | 0.05 | 1.05 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 29.3
2019-09-04 | 9:52 | 62.1172 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 62.2188 | 0.08 | 1.08 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 62.3086 | 0.05 | 1.05 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 62.418 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 62.5391 | 0.06 | 1.06 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 62.6406 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:52 | 62.7305 | 0.07 | 1.07 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 62.8398 | 0.07 | 1.07 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 62.9297 | 0.08 | 1.08 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 63.0273 | -0.05 | 0.95 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 63.1406 | -0.09 | 0.91 | -0.72 | 0.28 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 63.2383 | -0.1 | 0.9 | -0.71 | 0.29 | -0.64 | 0.36 | 73.24 | 28.32
2019-09-04 | 9:52 | 63.3398 | 0.02 | 1.02 | -0.82 | 0.18 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 9:52 | 63.4492 | 0.05 | 1.05 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 63.5391 | 0.05 | 1.05 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 29.3
2019-09-04 | 9:52 | 63.668 | 0.05 | 1.05 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 63.7695 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 63.8789 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 29.3
2019-09-04 | 9:52 | 63.957 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 64.0586 | 0.07 | 1.07 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 64.1602 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 9:52 | 64.2578 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 64.3672 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:52 | 64.4688 | -0.01 | 0.99 | -0.7 | 0.3 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:52 | 64.5781 | -0.09 | 0.91 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 64.707 | -0.1 | 0.9 | -0.68 | 0.32 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 64.8086 | -0.13 | 0.87 | -0.65 | 0.35 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 64.9102 | 0.03 | 1.03 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 65.0078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 65.0898 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 65.1875 | 0.05 | 1.05 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 65.2891 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 65.3906 | 0.05 | 1.05 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 65.5 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 29.3
2019-09-04 | 9:52 | 65.6094 | 0.06 | 1.06 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 65.707 | 0.07 | 1.07 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 9:52 | 65.8281 | 0.06 | 1.06 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 65.9297 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 29.3
2019-09-04 | 9:52 | 66.0273 | -0.04 | 0.96 | -0.69 | 0.31 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:52 | 66.1289 | -0.1 | 0.9 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 66.2188 | -0.09 | 0.91 | -0.7 | 0.3 | -0.64 | 0.36 | 72.27 | 28.32
2019-09-04 | 9:52 | 66.3203 | -0.06 | 0.94 | -0.75 | 0.25 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 66.418 | 0.04 | 1.04 | -0.84 | 0.16 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 66.5195 | 0.04 | 1.04 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 66.6289 | 0.05 | 1.05 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 28.32
2019-09-04 | 9:52 | 66.7305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 27.34
2019-09-04 | 9:52 | 66.8398 | 0.06 | 1.06 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 66.9492 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 9:52 | 67.0703 | 0.08 | 1.08 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 67.168 | 0.07 | 1.07 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 67.25 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 67.3477 | 0.08 | 1.08 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 67.457 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 67.5586 | -0.06 | 0.94 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 67.6602 | -0.07 | 0.93 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 29.3
2019-09-04 | 9:52 | 67.7578 | -0.12 | 0.88 | -0.79 | 0.21 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 67.8672 | 0.03 | 1.03 | -0.92 | 0.08 | -0.65 | 0.35 | 74.22 | 28.32
2019-09-04 | 9:52 | 67.957 | 0.08 | 1.08 | -0.88 | 0.12 | -0.66 | 0.34 | 75.2 | 28.32
2019-09-04 | 9:52 | 68.0586 | 0.05 | 1.05 | -0.84 | 0.16 | -0.66 | 0.34 | 76.17 | 28.32
2019-09-04 | 9:52 | 68.168 | 0.07 | 1.07 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 68.2695 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 68.3672 | 0.06 | 1.06 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 68.4805 | 0.06 | 1.06 | -0.81 | 0.19 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 68.5781 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 28.32
2019-09-04 | 9:52 | 68.6875 | 0.06 | 1.06 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 68.7773 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 68.8906 | 0.07 | 1.07 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 69.0078 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 69.1094 | -0.08 | 0.92 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:52 | 69.1992 | -0.11 | 0.89 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 69.2969 | -0.11 | 0.89 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 69.3984 | 0.03 | 1.03 | -0.92 | 0.08 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 69.5078 | 0.05 | 1.05 | -0.87 | 0.13 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 69.6094 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 69.7188 | 0.05 | 1.05 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 69.8203 | 0.06 | 1.06 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 69.918 | 0.07 | 1.07 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 70.0273 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 75.2 | 29.3
2019-09-04 | 9:52 | 70.1172 | 0.08 | 1.08 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 9:52 | 70.2305 | 0.06 | 1.06 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 70.3281 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 70.4297 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 70.5273 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 28.32
2019-09-04 | 9:52 | 70.6406 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 29.3
2019-09-04 | 9:52 | 70.7383 | -0.09 | 0.91 | -0.81 | 0.19 | -0.65 | 0.35 | 73.24 | 29.3
2019-09-04 | 9:52 | 70.8398 | 0.03 | 1.03 | -0.95 | 0.05 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 70.9492 | 0.04 | 1.04 | -0.9 | 0.1 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 71.0469 | 0.06 | 1.06 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 71.1484 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:52 | 71.25 | 0.05 | 1.05 | -0.84 | 0.16 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 71.3477 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 71.457 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 71.5586 | 0.06 | 1.06 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 71.6797 | 0.06 | 1.06 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:52 | 71.7773 | 0.06 | 1.06 | -0.82 | 0.18 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 9:52 | 71.8789 | 0.06 | 1.06 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 71.9805 | 0 | 1 | -0.76 | 0.24 | -0.67 | 0.33 | 76.17 | 28.32
2019-09-04 | 9:52 | 72.0977 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 29.3
2019-09-04 | 9:52 | 72.1875 | -0.1 | 0.9 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 72.2773 | -0.11 | 0.89 | -0.84 | 0.16 | -0.65 | 0.35 | 73.24 | 28.32
2019-09-04 | 9:52 | 72.3789 | 0.03 | 1.03 | -0.94 | 0.06 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 72.4805 | 0.05 | 1.05 | -0.88 | 0.12 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:52 | 72.5898 | 0.04 | 1.04 | -0.86 | 0.14 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 72.6875 | 0.05 | 1.05 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 72.8086 | 0.05 | 1.05 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 72.9102 | 0.07 | 1.07 | -0.82 | 0.18 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:52 | 73.0078 | 0.05 | 1.05 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 73.1094 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:52 | 73.207 | 0.09 | 1.09 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:52 | 73.3086 | 0.09 | 1.09 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 9:52 | 73.4102 | 0.09 | 1.09 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 73.5391 | -0.05 | 0.95 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 73.6406 | -0.07 | 0.93 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 73.7188 | -0.11 | 0.89 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 73.8281 | -0.09 | 0.91 | -0.84 | 0.16 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 73.918 | 0.05 | 1.05 | -0.93 | 0.07 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 74.0273 | 0.05 | 1.05 | -0.88 | 0.12 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 74.1289 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 74.2305 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 9:52 | 74.3281 | 0.06 | 1.06 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 74.4297 | 0.07 | 1.07 | -0.83 | 0.17 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 74.5391 | 0.07 | 1.07 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 74.6406 | 0.06 | 1.06 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 74.75 | 0.07 | 1.07 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 74.8477 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 74.9492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 75.0586 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 75.1602 | -0.11 | 0.89 | -0.85 | 0.15 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 9:52 | 75.2695 | -0.11 | 0.89 | -0.81 | 0.19 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 75.3789 | 0.04 | 1.04 | -0.91 | 0.09 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:52 | 75.4688 | 0.04 | 1.04 | -0.88 | 0.12 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 75.5703 | 0.04 | 1.04 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 75.668 | 0.06 | 1.06 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 75.7695 | 0.04 | 1.04 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 75.8789 | 0.06 | 1.06 | -0.85 | 0.15 | -0.66 | 0.34 | 75.2 | 29.3
2019-09-04 | 9:52 | 75.9805 | 0.06 | 1.06 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 76.0781 | 0.07 | 1.07 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 76.1797 | 0.07 | 1.07 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 76.2891 | 0.08 | 1.08 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 76.3906 | 0.08 | 1.08 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 76.5195 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 29.3
2019-09-04 | 9:52 | 76.6172 | -0.09 | 0.91 | -0.7 | 0.3 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 76.707 | -0.09 | 0.91 | -0.69 | 0.31 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:52 | 76.7969 | -0.13 | 0.87 | -0.69 | 0.31 | -0.65 | 0.35 | 75.2 | 27.34
2019-09-04 | 9:52 | 76.9102 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 77.0078 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 77.1172 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:52 | 77.207 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 77.3086 | 0.07 | 1.07 | -0.81 | 0.19 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:52 | 77.418 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 77.5195 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 77.6289 | 0.06 | 1.06 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 77.7305 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 77.8281 | 0.07 | 1.07 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 29.3
2019-09-04 | 9:52 | 77.9375 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:52 | 78.0391 | -0.05 | 0.95 | -0.72 | 0.28 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:52 | 78.1406 | -0.09 | 0.91 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 78.2383 | -0.1 | 0.9 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 78.3398 | 0.01 | 1.01 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 78.4492 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 9:52 | 78.5469 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 78.6484 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 78.7773 | 0.07 | 1.07 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 78.8906 | 0.07 | 1.07 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 78.9688 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:52 | 79.0781 | 0.07 | 1.07 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:52 | 79.1797 | 0.07 | 1.07 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 79.2695 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 79.3672 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 79.4805 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 79.5781 | -0.07 | 0.93 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 79.6797 | -0.1 | 0.9 | -0.67 | 0.33 | -0.65 | 0.35 | 72.27 | 27.34
2019-09-04 | 9:52 | 79.7891 | -0.11 | 0.89 | -0.68 | 0.32 | -0.64 | 0.36 | 73.24 | 27.34
2019-09-04 | 9:52 | 79.8789 | 0.02 | 1.02 | -0.81 | 0.19 | -0.65 | 0.35 | 76.17 | 28.32
2019-09-04 | 9:52 | 80 | 0.04 | 1.04 | -0.83 | 0.17 | -0.65 | 0.35 | 76.17 | 28.32
2019-09-04 | 9:52 | 80.1094 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:52 | 80.207 | 0.08 | 1.08 | -0.81 | 0.19 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:52 | 80.2969 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 80.3984 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 80.5 | 0.06 | 1.06 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 80.5977 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:52 | 80.707 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 80.8086 | 0.07 | 1.07 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 80.9102 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 81.0391 | -0.05 | 0.95 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 81.1406 | -0.08 | 0.92 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 81.2305 | -0.11 | 0.89 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 81.3398 | -0.13 | 0.87 | -0.68 | 0.32 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 9:52 | 81.4375 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 81.5391 | 0.05 | 1.05 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 81.6289 | 0.04 | 1.04 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 81.7383 | 0.06 | 1.06 | -0.81 | 0.19 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 81.8398 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 81.9375 | 0.06 | 1.06 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:52 | 82.0391 | 0.07 | 1.07 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 82.1406 | 0.06 | 1.06 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 82.2383 | 0.08 | 1.08 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 82.3477 | 0.06 | 1.06 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 82.457 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 82.5586 | -0.05 | 0.95 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 82.668 | -0.11 | 0.89 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 82.7773 | -0.13 | 0.87 | -0.7 | 0.3 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:52 | 82.8672 | 0.03 | 1.03 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 82.9688 | 0.04 | 1.04 | -0.81 | 0.19 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:52 | 83.0703 | 0.07 | 1.07 | -0.82 | 0.18 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:52 | 83.1875 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 83.2969 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 83.3789 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 83.4805 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 83.5781 | 0.07 | 1.07 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:52 | 83.6875 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 83.7891 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:52 | 83.8906 | 0.06 | 1.06 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 84 | 0.02 | 1.02 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 84.1289 | -0.05 | 0.95 | -0.71 | 0.29 | -0.67 | 0.33 | 76.17 | 28.32
2019-09-04 | 9:52 | 84.2305 | -0.12 | 0.88 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 84.3281 | -0.1 | 0.9 | -0.69 | 0.31 | -0.65 | 0.35 | 76.17 | 27.34
2019-09-04 | 9:52 | 84.418 | 0.04 | 1.04 | -0.81 | 0.19 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 84.5078 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 84.6172 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 84.7188 | 0.05 | 1.05 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 84.8281 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 84.918 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 85.0273 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 85.1289 | 0.08 | 1.08 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 85.2305 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 85.3281 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 85.4297 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 85.5273 | -0.03 | 0.97 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 85.6406 | -0.1 | 0.9 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 85.7578 | -0.09 | 0.91 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 85.8594 | 0 | 1 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:52 | 85.957 | 0.05 | 1.05 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 86.0469 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 86.1602 | 0.05 | 1.05 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:52 | 86.2578 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 86.3594 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 86.4805 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:52 | 86.5703 | 0.07 | 1.07 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 86.6602 | 0.05 | 1.05 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 86.7695 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 86.8672 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 86.9805 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 87.1094 | -0.03 | 0.97 | -0.72 | 0.28 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 87.207 | -0.08 | 0.92 | -0.7 | 0.3 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 87.3086 | -0.09 | 0.91 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 87.4102 | 0.03 | 1.03 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:52 | 87.5078 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 87.6094 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 9:52 | 87.707 | 0.05 | 1.05 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 87.7969 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:52 | 87.8984 | 0.07 | 1.07 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 88 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:52 | 88.0977 | 0.06 | 1.06 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:52 | 88.207 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 88.3086 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 88.418 | 0.06 | 1.06 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 88.5195 | -0.01 | 0.99 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 88.6172 | -0.08 | 0.92 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 88.7188 | -0.11 | 0.89 | -0.69 | 0.31 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:52 | 88.8281 | -0.13 | 0.87 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 88.9297 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 89.0273 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:52 | 89.1289 | 0.05 | 1.05 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 89.2383 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 89.3398 | 0.07 | 1.07 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 89.4375 | 0.06 | 1.06 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 89.5469 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 89.668 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 89.7695 | 0.08 | 1.08 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 89.8594 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:52 | 89.957 | 0.07 | 1.07 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 90.0586 | -0.04 | 0.96 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 90.168 | -0.1 | 0.9 | -0.7 | 0.3 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 90.2578 | -0.12 | 0.88 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 28.32
2019-09-04 | 9:52 | 90.3672 | 0 | 1 | -0.82 | 0.18 | -0.65 | 0.35 | 74.22 | 25.39
2019-09-04 | 9:52 | 90.4688 | 0.05 | 1.05 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 90.5703 | 0.05 | 1.05 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 90.6992 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 90.7969 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 90.8984 | 0.07 | 1.07 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 91 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 91.0898 | 0.08 | 1.08 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 91.1992 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 73.24 | 28.32
2019-09-04 | 9:52 | 91.2969 | 0.05 | 1.05 | -0.81 | 0.19 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:52 | 91.3984 | 0.06 | 1.06 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 91.5078 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 91.5977 | -0.08 | 0.92 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 91.6992 | -0.12 | 0.88 | -0.69 | 0.31 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 91.8086 | -0.1 | 0.9 | -0.71 | 0.29 | -0.65 | 0.35 | 74.22 | 25.39
2019-09-04 | 9:52 | 91.9102 | 0.04 | 1.04 | -0.84 | 0.16 | -0.66 | 0.34 | 74.22 | 29.3
2019-09-04 | 9:52 | 92.0078 | 0.05 | 1.05 | -0.84 | 0.16 | -0.65 | 0.35 | 74.22 | 28.32
2019-09-04 | 9:52 | 92.1094 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 92.2188 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 92.3281 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 92.4297 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 92.5273 | 0.07 | 1.07 | -0.82 | 0.18 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:52 | 92.6289 | 0.07 | 1.07 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 92.7305 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 92.8398 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:52 | 92.9375 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 93.0391 | -0.03 | 0.97 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 93.1406 | -0.1 | 0.9 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 93.2383 | -0.12 | 0.88 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 93.3594 | -0.04 | 0.96 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:52 | 93.4805 | 0.06 | 1.06 | -0.83 | 0.17 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 93.5703 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 93.6484 | 0.05 | 1.05 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 93.7578 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 93.8594 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 93.957 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 9:52 | 94.0703 | 0.07 | 1.07 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 94.1797 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 94.2773 | 0.07 | 1.07 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 9:52 | 94.3906 | 0.07 | 1.07 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:52 | 94.4883 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 94.5898 | -0.07 | 0.93 | -0.73 | 0.27 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 94.6797 | -0.12 | 0.88 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 94.7891 | -0.12 | 0.88 | -0.7 | 0.3 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 94.8906 | 0.04 | 1.04 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 94.9883 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:52 | 95.1094 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 95.207 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 95.3086 | 0.06 | 1.06 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 95.4102 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 95.5078 | 0.06 | 1.06 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 95.6094 | 0.06 | 1.06 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 95.6992 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:52 | 95.8203 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 95.9492 | 0.07 | 1.07 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 96.0469 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 96.1406 | -0.07 | 0.93 | -0.73 | 0.27 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:52 | 96.2305 | -0.09 | 0.91 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 96.3398 | -0.13 | 0.87 | -0.69 | 0.31 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 96.4492 | 0.04 | 1.04 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 96.5586 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 96.6484 | 0.05 | 1.05 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 96.7383 | 0.05 | 1.05 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 96.8398 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 96.957 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 97.0781 | 0.07 | 1.07 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 97.1602 | 0.09 | 1.09 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 97.25 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 97.3594 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 97.457 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:52 | 97.5586 | -0.05 | 0.95 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 97.6602 | -0.12 | 0.88 | -0.71 | 0.29 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:52 | 97.7695 | -0.11 | 0.89 | -0.73 | 0.27 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 97.8672 | 0.02 | 1.02 | -0.83 | 0.17 | -0.65 | 0.35 | 75.2 | 28.32
2019-09-04 | 9:52 | 98 | 0.04 | 1.04 | -0.84 | 0.16 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 98.0898 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 98.1992 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 98.2773 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 98.3789 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 98.4805 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 98.5898 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:52 | 98.6875 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 98.7891 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 98.8906 | 0.07 | 1.07 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:52 | 99 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 99.0977 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:52 | 99.207 | -0.11 | 0.89 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:52 | 99.3086 | -0.13 | 0.87 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:52 | 99.418 | 0.03 | 1.03 | -0.88 | 0.12 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 99.5195 | 0.04 | 1.04 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 99.6094 | 0.06 | 1.06 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 99.7188 | 0.04 | 1.04 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 99.8281 | 0.07 | 1.07 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 29.3
2019-09-04 | 9:52 | 99.918 | 0.06 | 1.06 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 100.0195 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:52 | 100.1289 | 0.06 | 1.06 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 100.2578 | 0.07 | 1.07 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 100.3594 | 0.08 | 1.08 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 100.4375 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 100.5391 | -0.06 | 0.94 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 100.6406 | -0.08 | 0.92 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 100.7383 | -0.12 | 0.88 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:52 | 100.8477 | -0.07 | 0.93 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 100.9492 | 0.04 | 1.04 | -0.89 | 0.11 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 9:52 | 101.0469 | 0.04 | 1.04 | -0.89 | 0.11 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 101.1484 | 0.05 | 1.05 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:52 | 101.25 | 0.06 | 1.06 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 101.3906 | 0.06 | 1.06 | -0.86 | 0.14 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:52 | 101.4883 | 0.07 | 1.07 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 101.5781 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 101.668 | 0.06 | 1.06 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:52 | 101.7891 | 0.07 | 1.07 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:52 | 101.8906 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 101.9805 | 0.03 | 1.03 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:52 | 102.0781 | -0.05 | 0.95 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:52 | 102.1875 | -0.11 | 0.89 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 102.2969 | -0.14 | 0.86 | -0.81 | 0.19 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:52 | 102.3984 | 0.01 | 1.01 | -0.92 | 0.08 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:52 | 102.4883 | 0.04 | 1.04 | -0.91 | 0.09 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 102.5977 | 0.04 | 1.04 | -0.89 | 0.11 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 102.6992 | 0.06 | 1.06 | -0.88 | 0.12 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 102.7969 | 0.07 | 1.07 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 102.8984 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 103 | 0.06 | 1.06 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 25.39
2019-09-04 | 9:52 | 103.1094 | 0.05 | 1.05 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:52 | 103.207 | 0.05 | 1.05 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 103.3086 | 0.06 | 1.06 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:52 | 103.418 | 0.05 | 1.05 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:52 | 103.5195 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:52 | 103.6289 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:52 | 103.7305 | -0.13 | 0.87 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:52 | 103.8477 | -0.13 | 0.87 | -0.79 | 0.21 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:52 | 103.9492 | 0.04 | 1.04 | -0.93 | 0.07 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:52 | 104.0469 | 0.05 | 1.05 | -0.89 | 0.11 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:52 | 104.1406 | 0.04 | 1.04 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:52 | 104.25 | 0.06 | 1.06 | -0.88 | 0.12 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:52 | 104.3477 | 0.04 | 1.04 | -0.87 | 0.13 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:52 | 104.4492 | 0.06 | 1.06 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:52 | 104.5469 | 0.06 | 1.06 | -0.87 | 0.13 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:53 | 104.668 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 104.7695 | 0.06 | 1.06 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 104.8789 | 0.06 | 1.06 | -0.85 | 0.15 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 9:53 | 104.9688 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 105.0586 | -0.05 | 0.95 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 105.168 | -0.12 | 0.88 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 105.2695 | -0.12 | 0.88 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 28.32
2019-09-04 | 9:53 | 105.3672 | 0.01 | 1.01 | -0.93 | 0.07 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 105.4805 | 0.04 | 1.04 | -0.93 | 0.07 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:53 | 105.5703 | 0.04 | 1.04 | -0.9 | 0.1 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:53 | 105.6797 | 0.05 | 1.05 | -0.88 | 0.12 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 105.7773 | 0.06 | 1.06 | -0.88 | 0.12 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:53 | 105.8789 | 0.08 | 1.08 | -0.87 | 0.13 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 105.9805 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 106.0898 | 0.06 | 1.06 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 106.1875 | 0.06 | 1.06 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 106.3086 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:53 | 106.3984 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 106.5 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 106.6094 | -0.09 | 0.91 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 106.707 | -0.11 | 0.89 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:53 | 106.8203 | -0.13 | 0.87 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 106.9375 | 0.02 | 1.02 | -0.91 | 0.09 | -0.66 | 0.34 | 72.27 | 26.37
2019-09-04 | 9:53 | 107.0391 | 0.04 | 1.04 | -0.9 | 0.1 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 107.1406 | 0.04 | 1.04 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 107.2305 | 0.05 | 1.05 | -0.87 | 0.13 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 107.3398 | 0.08 | 1.08 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 107.4297 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 107.5391 | 0.07 | 1.07 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 107.6406 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 107.7305 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 107.8398 | 0.07 | 1.07 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 107.9375 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 108.0391 | 0 | 1 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 108.1406 | -0.09 | 0.91 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 108.25 | -0.12 | 0.88 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 108.3477 | -0.12 | 0.88 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:53 | 108.4492 | 0.03 | 1.03 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:53 | 108.5586 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:53 | 108.6602 | 0.05 | 1.05 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 108.7578 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 108.8594 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 108.9688 | 0.08 | 1.08 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 109.0703 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 109.168 | 0.06 | 1.06 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 109.2695 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 109.3789 | 0.06 | 1.06 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 109.4805 | 0.03 | 1.03 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:53 | 109.5781 | -0.06 | 0.94 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:53 | 109.6875 | -0.11 | 0.89 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 109.7891 | -0.12 | 0.88 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:53 | 109.8906 | 0.02 | 1.02 | -0.89 | 0.11 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:53 | 110 | 0.03 | 1.03 | -0.89 | 0.11 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 110.0898 | 0.06 | 1.06 | -0.88 | 0.12 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:53 | 110.2188 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 110.3203 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 110.3984 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 110.5 | 0.07 | 1.07 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 110.6094 | 0.08 | 1.08 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 110.707 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 110.8203 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:53 | 110.918 | 0.06 | 1.06 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 111.0195 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 111.1172 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 111.2305 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 111.3281 | -0.12 | 0.88 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 111.4375 | 0.02 | 1.02 | -0.91 | 0.09 | -0.66 | 0.34 | 72.27 | 26.37
2019-09-04 | 9:53 | 111.5586 | 0.03 | 1.03 | -0.89 | 0.11 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 111.6484 | 0.04 | 1.04 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 111.7383 | 0.04 | 1.04 | -0.88 | 0.12 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 111.8398 | 0.06 | 1.06 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 111.9375 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 112.0469 | 0.05 | 1.05 | -0.86 | 0.14 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 112.1484 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 112.25 | 0.05 | 1.05 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 112.3594 | 0.06 | 1.06 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 9:53 | 112.457 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 112.5586 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 112.6602 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 112.7695 | -0.13 | 0.87 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:53 | 112.8672 | 0 | 1 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 112.9688 | 0.04 | 1.04 | -0.9 | 0.1 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 113.0781 | 0.04 | 1.04 | -0.88 | 0.12 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 113.207 | 0.04 | 1.04 | -0.88 | 0.12 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 113.3086 | 0.04 | 1.04 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 113.3984 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 113.5078 | 0.05 | 1.05 | -0.87 | 0.13 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:53 | 113.5898 | 0.07 | 1.07 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 113.6875 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:53 | 113.7969 | 0.05 | 1.05 | -0.86 | 0.14 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 113.8984 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 114 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 114.0977 | -0.04 | 0.96 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 114.207 | -0.11 | 0.89 | -0.75 | 0.25 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 114.3281 | -0.13 | 0.87 | -0.73 | 0.27 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 114.4297 | 0.03 | 1.03 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 114.5273 | 0.04 | 1.04 | -0.87 | 0.13 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:53 | 114.6172 | 0.05 | 1.05 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 114.7188 | 0.06 | 1.06 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 114.8281 | 0.06 | 1.06 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 114.918 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 115.0273 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 115.1289 | 0.06 | 1.06 | -0.85 | 0.15 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 115.2188 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 115.3398 | 0.06 | 1.06 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 115.4375 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 115.5391 | -0.02 | 0.98 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 115.6484 | -0.11 | 0.89 | -0.75 | 0.25 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 115.75 | -0.09 | 0.91 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 115.8672 | -0.13 | 0.87 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:53 | 115.957 | 0.04 | 1.04 | -0.87 | 0.13 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 116.0703 | 0.05 | 1.05 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:53 | 116.1602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:53 | 116.2773 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 116.3594 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 116.4688 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 116.5703 | 0.05 | 1.05 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 116.668 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 116.7695 | 0.07 | 1.07 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 116.8789 | 0.06 | 1.06 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:53 | 116.9805 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 117.0781 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:53 | 117.1875 | -0.09 | 0.91 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 117.2891 | -0.12 | 0.88 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 117.3906 | 0.01 | 1.01 | -0.87 | 0.13 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 117.4883 | 0.03 | 1.03 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 117.6172 | 0.05 | 1.05 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 117.707 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 117.8203 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 117.9297 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 118.0195 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 118.1406 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 29.3
2019-09-04 | 9:53 | 118.2305 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 118.3203 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 118.418 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 118.5078 | 0.03 | 1.03 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 118.6172 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 118.7305 | -0.12 | 0.88 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 118.8398 | -0.14 | 0.86 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 118.9297 | 0.03 | 1.03 | -0.88 | 0.12 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 119.0391 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 119.1484 | 0.07 | 1.07 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 119.25 | 0.06 | 1.06 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 119.3594 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:53 | 119.4492 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:53 | 119.5469 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 119.6484 | 0.06 | 1.06 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 119.75 | 0.07 | 1.07 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 119.8594 | 0.06 | 1.06 | -0.85 | 0.15 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 9:53 | 119.957 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 120.0898 | -0.03 | 0.97 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 120.1875 | -0.09 | 0.91 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:53 | 120.2891 | -0.09 | 0.91 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 120.3789 | -0.03 | 0.97 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 120.4883 | 0.03 | 1.03 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 120.5898 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:53 | 120.6797 | 0.08 | 1.08 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 120.7773 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 120.8789 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 120.9883 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 9:53 | 121.1094 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:53 | 121.2188 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 121.3203 | 0.07 | 1.07 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 121.4102 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 74.22 | 26.37
2019-09-04 | 9:53 | 121.5078 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 121.6094 | -0.04 | 0.96 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 121.707 | -0.11 | 0.89 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 121.8203 | -0.11 | 0.89 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 121.9102 | 0.02 | 1.02 | -0.84 | 0.16 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 122.0195 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:53 | 122.1289 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 122.2383 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 122.3398 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 122.4375 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 122.5391 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 122.6484 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 122.7383 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 122.8398 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 122.9688 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 123.0586 | -0.01 | 0.99 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 123.1602 | -0.09 | 0.91 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:53 | 123.2695 | -0.13 | 0.87 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 123.3789 | -0.13 | 0.87 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 123.4688 | 0.03 | 1.03 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-09-04 | 9:53 | 123.5703 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:53 | 123.668 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 123.7695 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:53 | 123.8672 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 123.957 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 124.0977 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 124.1992 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 124.2773 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 124.3789 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 124.4805 | 0.07 | 1.07 | -0.84 | 0.16 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 124.5781 | -0.06 | 0.94 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 124.6875 | -0.11 | 0.89 | -0.72 | 0.28 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:53 | 124.7891 | -0.11 | 0.89 | -0.73 | 0.27 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:53 | 124.8906 | 0.01 | 1.01 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 27.34
2019-09-04 | 9:53 | 124.9883 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 125.0898 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 125.1992 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 125.3086 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 125.4102 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 125.5078 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 125.6094 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 125.7305 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 125.8281 | 0.09 | 1.09 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 125.9297 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 126.0273 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:53 | 126.1406 | -0.07 | 0.93 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 126.2305 | -0.12 | 0.88 | -0.71 | 0.29 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:53 | 126.3281 | -0.12 | 0.88 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 126.4375 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 126.5469 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 126.6602 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 126.7578 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 126.8477 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 126.9492 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 127.0469 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 127.1602 | 0.06 | 1.06 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 127.2578 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:53 | 127.3594 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 9:53 | 127.4805 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 127.5781 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 127.668 | -0.08 | 0.92 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 127.7695 | -0.12 | 0.88 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 127.8672 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 127.9805 | 0.04 | 1.04 | -0.84 | 0.16 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:53 | 128.0781 | 0.03 | 1.03 | -0.83 | 0.17 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:53 | 128.168 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 128.2891 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 128.3789 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 128.4883 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 128.5977 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 128.7188 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 128.8203 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 128.9102 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 74.22 | 26.37
2019-09-04 | 9:53 | 129.0195 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 74.22 | 27.34
2019-09-04 | 9:53 | 129.1094 | -0.05 | 0.95 | -0.74 | 0.26 | -0.68 | 0.32 | 76.17 | 27.34
2019-09-04 | 9:53 | 129.2188 | -0.13 | 0.87 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 129.3086 | -0.12 | 0.88 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 129.4102 | 0.03 | 1.03 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:53 | 129.5195 | 0.03 | 1.03 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 26.37
2019-09-04 | 9:53 | 129.6172 | 0.05 | 1.05 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 129.7188 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 129.8281 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 129.9297 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 130.0273 | 0.06 | 1.06 | -0.83 | 0.17 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:53 | 130.1289 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 130.2383 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 130.3398 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 130.4688 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 130.5703 | -0.01 | 0.99 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 130.6406 | -0.09 | 0.91 | -0.73 | 0.27 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 130.7773 | -0.11 | 0.89 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 130.8789 | -0.13 | 0.87 | -0.71 | 0.29 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:53 | 130.9805 | 0.03 | 1.03 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 131.0703 | 0.03 | 1.03 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:53 | 131.1602 | 0.04 | 1.04 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 131.2578 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 131.3672 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 131.5 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 131.5781 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 131.6992 | 0.07 | 1.07 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 131.8086 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 131.8984 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 131.9883 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 76.17 | 27.34
2019-09-04 | 9:53 | 132.0898 | -0.07 | 0.93 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 132.1875 | -0.1 | 0.9 | -0.73 | 0.27 | -0.65 | 0.35 | 74.22 | 26.37
2019-09-04 | 9:53 | 132.2969 | -0.12 | 0.88 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 132.3984 | 0.02 | 1.02 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 132.5 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:53 | 132.5977 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 132.707 | 0.05 | 1.05 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 132.8203 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 132.9297 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 133.0273 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 133.1289 | 0.08 | 1.08 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 133.2188 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 133.3281 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 133.4492 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 133.5273 | -0.03 | 0.97 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 9:53 | 133.6289 | -0.08 | 0.92 | -0.71 | 0.29 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 133.7305 | -0.12 | 0.88 | -0.7 | 0.3 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:53 | 133.8398 | -0.14 | 0.86 | -0.71 | 0.29 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 133.9492 | 0.02 | 1.02 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 134.0586 | 0.04 | 1.04 | -0.84 | 0.16 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:53 | 134.1602 | 0.03 | 1.03 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 134.2695 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:53 | 134.3672 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 134.457 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 134.5586 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:53 | 134.668 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 134.7578 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 134.8594 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 134.957 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 135.0703 | -0.03 | 0.97 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 9:53 | 135.168 | -0.1 | 0.9 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 135.2695 | -0.14 | 0.86 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:53 | 135.3789 | -0.1 | 0.9 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 135.4805 | 0.02 | 1.02 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 135.5781 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:53 | 135.6797 | 0.05 | 1.05 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 135.7891 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 135.918 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 136.0195 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:53 | 136.1094 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 136.1875 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:53 | 136.3203 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 136.418 | 0.06 | 1.06 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 136.5195 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 136.6172 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 136.707 | -0.12 | 0.88 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 136.8086 | -0.13 | 0.87 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 136.9492 | 0 | 1 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 137.0273 | 0.04 | 1.04 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 137.1289 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:53 | 137.2305 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 137.3281 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 137.4297 | 0.06 | 1.06 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 137.5273 | 0.05 | 1.05 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 137.6289 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:53 | 137.7383 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 137.8398 | 0.06 | 1.06 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 137.9688 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 138.0703 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 138.1797 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 138.2695 | -0.12 | 0.88 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 138.3594 | -0.13 | 0.87 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 138.457 | 0.02 | 1.02 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 138.5703 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 138.6602 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 138.7695 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 138.8672 | 0.04 | 1.04 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 138.9688 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 139.0703 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 9:53 | 139.1797 | 0.05 | 1.05 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 139.2773 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 139.3789 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 74.22 | 28.32
2019-09-04 | 9:53 | 139.4883 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 139.5898 | -0.05 | 0.95 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 29.3
2019-09-04 | 9:53 | 139.707 | -0.11 | 0.89 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 139.7969 | -0.13 | 0.87 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 139.9102 | 0.01 | 1.01 | -0.83 | 0.17 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 140.0078 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 140.1094 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 140.207 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 140.3086 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 140.4102 | 0.03 | 1.03 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 140.5078 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 140.6172 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 140.7188 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 140.8281 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:53 | 140.9375 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 9:53 | 141.0391 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 141.1289 | -0.07 | 0.93 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 9:53 | 141.2383 | -0.13 | 0.87 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 141.3594 | -0.13 | 0.87 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 141.4805 | 0.02 | 1.02 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 141.5703 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 141.6484 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 141.75 | 0.03 | 1.03 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 141.8477 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 141.957 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 142.0586 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 142.1602 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:53 | 142.2578 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 142.3594 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 142.4688 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 142.5703 | -0.03 | 0.97 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 142.668 | -0.1 | 0.9 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 142.7773 | -0.11 | 0.89 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 142.8789 | -0.12 | 0.88 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:53 | 142.9805 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 143.0898 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 143.1875 | 0.03 | 1.03 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 143.2773 | 0.05 | 1.05 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 143.418 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 143.5195 | 0.06 | 1.06 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 143.6094 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 143.6992 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 143.8086 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:53 | 143.8984 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 76.17 | 28.32
2019-09-04 | 9:53 | 144 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 144.1094 | -0.06 | 0.94 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 144.2188 | -0.12 | 0.88 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 144.3203 | -0.12 | 0.88 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 144.418 | 0.03 | 1.03 | -0.88 | 0.12 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 144.5195 | 0.03 | 1.03 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 144.6172 | 0.03 | 1.03 | -0.87 | 0.13 | -0.67 | 0.33 | 76.17 | 27.34
2019-09-04 | 9:53 | 144.7188 | 0.05 | 1.05 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 144.8477 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 144.9375 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:53 | 145.0469 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 9:53 | 145.1406 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:53 | 145.2383 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:53 | 145.3398 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 9:53 | 145.4492 | 0.04 | 1.04 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:53 | 145.5703 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 145.6797 | -0.08 | 0.92 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 145.7695 | -0.11 | 0.89 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 145.8594 | -0.09 | 0.91 | -0.73 | 0.27 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:53 | 145.957 | 0.01 | 1.01 | -0.86 | 0.14 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 146.0586 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 146.1797 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 146.2891 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 146.3789 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 25.39
2019-09-04 | 9:53 | 146.4805 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 146.5781 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 146.6797 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 146.7773 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:53 | 146.8906 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 74.22 | 26.37
2019-09-04 | 9:53 | 146.9883 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 147.0898 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 147.1992 | -0.11 | 0.89 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 147.3281 | -0.11 | 0.89 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 147.4297 | 0 | 1 | -0.82 | 0.18 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:53 | 147.5195 | 0.03 | 1.03 | -0.86 | 0.14 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 147.6289 | 0.02 | 1.02 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 147.7188 | 0.05 | 1.05 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 147.8203 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 147.9102 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:53 | 148.0078 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 148.1172 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 9:53 | 148.2188 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 148.3203 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 148.418 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 148.5273 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 148.6289 | -0.07 | 0.93 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 148.7383 | -0.14 | 0.86 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 148.8398 | -0.13 | 0.87 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 148.9375 | 0.01 | 1.01 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 149.0391 | 0.05 | 1.05 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 149.1406 | 0.04 | 1.04 | -0.84 | 0.16 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 149.25 | 0.06 | 1.06 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 149.3477 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 9:53 | 149.457 | 0.03 | 1.03 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 149.5469 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 149.6602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:53 | 149.7578 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:53 | 149.8672 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 75.2 | 28.32
2019-09-04 | 9:53 | 149.9688 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 150.0781 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 150.1797 | -0.08 | 0.92 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 150.2695 | -0.13 | 0.87 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 150.3789 | -0.13 | 0.87 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:53 | 150.4805 | 0.02 | 1.02 | -0.88 | 0.12 | -0.67 | 0.33 | 75.2 | 25.39
2019-09-04 | 9:53 | 150.5781 | 0.02 | 1.02 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 150.6875 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 150.7891 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 150.8906 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:53 | 150.9883 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 9:53 | 151.0977 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 151.1992 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 151.3086 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 151.3984 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 151.5078 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 151.6094 | -0.04 | 0.96 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 151.707 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 151.8203 | -0.14 | 0.86 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:53 | 151.918 | 0 | 1 | -0.88 | 0.12 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:53 | 152.0273 | 0.03 | 1.03 | -0.9 | 0.1 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:53 | 152.1289 | 0.03 | 1.03 | -0.88 | 0.12 | -0.66 | 0.34 | 76.17 | 27.34
2019-09-04 | 9:53 | 152.25 | 0.03 | 1.03 | -0.86 | 0.14 | -0.67 | 0.33 | 75.2 | 25.39
2019-09-04 | 9:53 | 152.3594 | 0.05 | 1.05 | -0.85 | 0.15 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:53 | 152.457 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 152.5469 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 152.6484 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 152.7383 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 152.8398 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:53 | 152.9492 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:53 | 153.0469 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 153.1484 | -0.06 | 0.94 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 153.25 | -0.13 | 0.87 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 153.3594 | -0.14 | 0.86 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:53 | 153.5 | 0.02 | 1.02 | -0.9 | 0.1 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 153.5586 | 0.01 | 1.01 | -0.89 | 0.11 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 153.668 | 0.03 | 1.03 | -0.87 | 0.13 | -0.65 | 0.35 | 74.22 | 26.37
2019-09-04 | 9:53 | 153.7891 | 0.03 | 1.03 | -0.88 | 0.12 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 153.8789 | 0.03 | 1.03 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 153.9805 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 154.0781 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 154.1797 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 154.2773 | 0.05 | 1.05 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 154.3906 | 0.05 | 1.05 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 154.4883 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 154.5898 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 154.6992 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 154.8086 | -0.15 | 0.85 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 154.918 | -0.06 | 0.94 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 155.0195 | 0.02 | 1.02 | -0.89 | 0.11 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:53 | 155.0977 | 0.03 | 1.03 | -0.88 | 0.12 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 155.2188 | 0.02 | 1.02 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 155.3398 | 0.04 | 1.04 | -0.88 | 0.12 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 155.4102 | 0.03 | 1.03 | -0.87 | 0.13 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:53 | 155.5391 | 0.03 | 1.03 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 155.6406 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:53 | 155.7305 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 155.8398 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 155.9375 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 156.0469 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 76.17 | 28.32
2019-09-04 | 9:53 | 156.1406 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 156.2383 | -0.13 | 0.87 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 27.34
2019-09-04 | 9:53 | 156.3398 | -0.13 | 0.87 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 156.4375 | 0 | 1 | -0.9 | 0.1 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 156.5391 | 0 | 1 | -0.9 | 0.1 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 156.6406 | 0.02 | 1.02 | -0.89 | 0.11 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 156.75 | 0.03 | 1.03 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 156.8477 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 156.9492 | 0.05 | 1.05 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 157.0469 | 0.04 | 1.04 | -0.88 | 0.12 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 157.1602 | 0.04 | 1.04 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 157.2578 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:53 | 157.3672 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 9:53 | 157.4805 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:53 | 157.5781 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:53 | 157.668 | -0.1 | 0.9 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 157.7773 | -0.14 | 0.86 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 157.8789 | -0.14 | 0.86 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:53 | 157.9805 | 0.02 | 1.02 | -0.9 | 0.1 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:53 | 158.0781 | 0.04 | 1.04 | -0.87 | 0.13 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:53 | 158.1797 | 0.01 | 1.01 | -0.88 | 0.12 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 158.2891 | 0.02 | 1.02 | -0.88 | 0.12 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 158.3906 | 0.04 | 1.04 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 158.5 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 158.5977 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 158.6992 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:53 | 158.8086 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 158.9102 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:53 | 159.0195 | 0.03 | 1.03 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 159.1289 | -0.08 | 0.92 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 159.2188 | -0.13 | 0.87 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:53 | 159.3281 | -0.15 | 0.85 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:53 | 159.4375 | -0.01 | 0.99 | -0.88 | 0.12 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 159.5273 | 0.01 | 1.01 | -0.89 | 0.11 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:53 | 159.6289 | 0.02 | 1.02 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 159.7305 | 0.03 | 1.03 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 159.8281 | 0.05 | 1.05 | -0.86 | 0.14 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:53 | 159.9375 | 0.03 | 1.03 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 160.0391 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 160.1406 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 160.2383 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:53 | 160.3398 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:53 | 160.4492 | 0.05 | 1.05 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 160.5469 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:53 | 160.6797 | -0.09 | 0.91 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:53 | 160.7891 | -0.14 | 0.86 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:53 | 160.8672 | -0.15 | 0.85 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:53 | 160.9688 | -0.02 | 0.98 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:53 | 161.0586 | 0.02 | 1.02 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 161.168 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:53 | 161.2695 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 161.3672 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 161.4805 | 0.02 | 1.02 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 161.5781 | 0.02 | 1.02 | -0.86 | 0.14 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:53 | 161.6797 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:53 | 161.7773 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 161.8789 | 0.03 | 1.03 | -0.85 | 0.15 | -0.68 | 0.32 | 76.17 | 27.34
2019-09-04 | 9:53 | 162 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:53 | 162.0898 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 162.1875 | -0.13 | 0.87 | -0.73 | 0.27 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:53 | 162.2969 | -0.12 | 0.88 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:53 | 162.3984 | -0.09 | 0.91 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-09-04 | 9:53 | 162.5 | 0 | 1 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:53 | 162.6094 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:53 | 162.707 | 0.03 | 1.03 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:53 | 162.7969 | 0.02 | 1.02 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 9:53 | 162.9102 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 163.0195 | 0.01 | 1.01 | -0.85 | 0.15 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:53 | 163.1172 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:53 | 163.2305 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:53 | 163.3203 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:53 | 163.4297 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:53 | 163.5469 | 0.03 | 1.03 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 163.6484 | -0.09 | 0.91 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 163.75 | -0.14 | 0.86 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 163.8398 | -0.16 | 0.84 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:54 | 163.9688 | -0.01 | 0.99 | -0.84 | 0.16 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:54 | 164.0703 | 0 | 1 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 164.1406 | 0.02 | 1.02 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 164.2695 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 164.3984 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:54 | 164.4883 | 0.03 | 1.03 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 164.5781 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 164.6602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 164.7695 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 164.8789 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 164.9805 | 0.02 | 1.02 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 165.0898 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 165.1875 | -0.12 | 0.88 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 165.2773 | -0.13 | 0.87 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:54 | 165.3789 | -0.15 | 0.85 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 165.4805 | -0.01 | 0.99 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 165.5898 | 0.02 | 1.02 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 165.6875 | 0.02 | 1.02 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 165.7891 | 0.02 | 1.02 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 165.8984 | 0.02 | 1.02 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 166.0078 | 0.02 | 1.02 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 166.1289 | 0.02 | 1.02 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 166.2383 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 166.3281 | 0.03 | 1.03 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 166.4297 | 0.01 | 1.01 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 166.5195 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 166.6094 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 166.7188 | -0.12 | 0.88 | -0.72 | 0.28 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 166.8281 | -0.15 | 0.85 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 166.957 | -0.02 | 0.98 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 167.0391 | 0 | 1 | -0.83 | 0.17 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 167.1172 | 0 | 1 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 167.2578 | 0.02 | 1.02 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 167.3672 | 0.03 | 1.03 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 167.457 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 167.5469 | 0.03 | 1.03 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 167.6406 | 0.03 | 1.03 | -0.82 | 0.18 | -0.69 | 0.31 | 75.2 | 25.39
2019-09-04 | 9:54 | 167.7383 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 167.8398 | 0.03 | 1.03 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 167.9492 | 0.03 | 1.03 | -0.83 | 0.17 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 168.0469 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 168.1602 | -0.11 | 0.89 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 168.2578 | -0.15 | 0.85 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 168.3672 | -0.17 | 0.83 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 168.4883 | -0.02 | 0.98 | -0.82 | 0.18 | -0.66 | 0.34 | 75.2 | 25.39
2019-09-04 | 9:54 | 168.5781 | 0 | 1 | -0.83 | 0.17 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 168.6797 | 0.01 | 1.01 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 168.7891 | 0.01 | 1.01 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 168.8984 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 168.9883 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 169.0977 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 169.1797 | 0.03 | 1.03 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 169.2891 | 0.01 | 1.01 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 169.3906 | 0.03 | 1.03 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 169.4883 | 0.01 | 1.01 | -0.83 | 0.17 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 9:54 | 169.5898 | -0.05 | 0.95 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 169.6992 | -0.12 | 0.88 | -0.7 | 0.3 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 169.7969 | -0.16 | 0.84 | -0.68 | 0.32 | -0.65 | 0.35 | 74.22 | 26.37
2019-09-04 | 9:54 | 169.8984 | -0.15 | 0.85 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 170.0195 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 170.1172 | 0 | 1 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:54 | 170.2188 | 0.02 | 1.02 | -0.83 | 0.17 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 170.3281 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 170.4297 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 170.5195 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 170.6484 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 170.7383 | 0.03 | 1.03 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 170.8477 | 0.03 | 1.03 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 170.9492 | 0.03 | 1.03 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 171.0391 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 171.1406 | -0.09 | 0.91 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 171.2383 | -0.16 | 0.84 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 171.3398 | -0.17 | 0.83 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 171.4492 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 171.5469 | 0 | 1 | -0.81 | 0.19 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:54 | 171.6484 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 171.75 | 0.01 | 1.01 | -0.83 | 0.17 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 171.8477 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 28.32
2019-09-04 | 9:54 | 171.9805 | 0.03 | 1.03 | -0.82 | 0.18 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 172.0781 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 172.168 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 172.2773 | 0.01 | 1.01 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 172.3789 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 172.4688 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 172.5781 | -0.03 | 0.97 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 172.6797 | -0.12 | 0.88 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 172.7891 | -0.16 | 0.84 | -0.68 | 0.32 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 172.8789 | -0.15 | 0.85 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 28.32
2019-09-04 | 9:54 | 173.0078 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 173.0898 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 173.1992 | 0.02 | 1.02 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 173.2969 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 173.418 | 0.03 | 1.03 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 173.5078 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 173.5977 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 173.6992 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 173.8086 | 0.02 | 1.02 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 173.918 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 174.0078 | 0.02 | 1.02 | -0.83 | 0.17 | -0.68 | 0.32 | 76.17 | 28.32
2019-09-04 | 9:54 | 174.1172 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:54 | 174.2188 | -0.15 | 0.85 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 174.3203 | -0.15 | 0.85 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 174.4297 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 174.5391 | -0.01 | 0.99 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 174.6289 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 174.7305 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 174.8281 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 174.957 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 175.0703 | 0.02 | 1.02 | -0.83 | 0.17 | -0.68 | 0.32 | 75.2 | 26.37 | Pressure equilibirum
2019-09-04 | 9:54 | 175.1602 | 0.03 | 1.03 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 175.25 | 0.03 | 1.03 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 175.3672 | 0.01 | 1.01 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 175.457 | 0.03 | 1.03 | -0.82 | 0.18 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:54 | 175.5781 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 175.6602 | -0.11 | 0.89 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:54 | 175.75 | -0.15 | 0.85 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 175.8594 | -0.17 | 0.83 | -0.65 | 0.35 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 175.9688 | 0 | 1 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:54 | 176.0703 | 0.01 | 1.01 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:54 | 176.168 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 176.2695 | 0.01 | 1.01 | -0.82 | 0.18 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 176.3906 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 176.5 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 176.5977 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 176.6992 | 0.02 | 1.02 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:54 | 176.7891 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 176.8906 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:54 | 176.9883 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 177.1094 | -0.04 | 0.96 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 177.2188 | -0.13 | 0.87 | -0.69 | 0.31 | -0.68 | 0.32 | 73.24 | 24.41
2019-09-04 | 9:54 | 177.3203 | -0.15 | 0.85 | -0.66 | 0.34 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 177.418 | -0.17 | 0.83 | -0.65 | 0.35 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 177.5195 | -0.03 | 0.97 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 177.6172 | -0.01 | 0.99 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 177.7188 | 0.01 | 1.01 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 177.8203 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 177.918 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 178.0195 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 178.1289 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 178.2305 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 178.3281 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 178.4297 | -0.01 | 0.99 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 178.5391 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 178.6406 | -0.1 | 0.9 | -0.73 | 0.27 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 178.7383 | -0.15 | 0.85 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 178.8398 | -0.17 | 0.83 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 178.9492 | -0.04 | 0.96 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 179.0469 | -0.01 | 0.99 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 179.1484 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 179.2578 | -0.02 | 0.98 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 179.3789 | 0 | 1 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 179.4805 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 179.5703 | 0.02 | 1.02 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 179.6875 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 179.7773 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 179.8672 | 0.02 | 1.02 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:54 | 179.9805 | -0.01 | 0.99 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 180.0898 | -0.03 | 0.97 | -0.77 | 0.23 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 180.1797 | -0.11 | 0.89 | -0.7 | 0.3 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 180.2773 | -0.16 | 0.84 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:54 | 180.3984 | -0.18 | 0.82 | -0.65 | 0.35 | -0.66 | 0.34 | 76.17 | 26.37
2019-09-04 | 9:54 | 180.5078 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 180.5977 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 180.6875 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 76.17 | 27.34
2019-09-04 | 9:54 | 180.7969 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 180.8984 | 0.02 | 1.02 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 181 | 0.01 | 1.01 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 181.1094 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 181.207 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 181.3398 | 0.02 | 1.02 | -0.81 | 0.19 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:54 | 181.4375 | 0.01 | 1.01 | -0.8 | 0.2 | -0.7 | 0.3 | 74.22 | 27.34
2019-09-04 | 9:54 | 181.5391 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 181.6289 | -0.07 | 0.93 | -0.75 | 0.25 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:54 | 181.7305 | -0.13 | 0.87 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 181.8281 | -0.17 | 0.83 | -0.66 | 0.34 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 181.9297 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:54 | 182.0391 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 28.32
2019-09-04 | 9:54 | 182.1289 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:54 | 182.25 | -0.01 | 0.99 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 182.3594 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 182.4492 | 0 | 1 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 182.5391 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 182.6406 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 182.75 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 182.8477 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 182.957 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 183.0703 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 183.168 | -0.13 | 0.87 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 183.2578 | -0.17 | 0.83 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:54 | 183.3672 | -0.18 | 0.82 | -0.66 | 0.34 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 183.4688 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 183.5977 | -0.03 | 0.97 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 183.6992 | -0.02 | 0.98 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 183.8086 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 183.8906 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 183.9883 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 184.0781 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 76.17 | 27.34
2019-09-04 | 9:54 | 184.1875 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 184.2891 | 0.01 | 1.01 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 184.3906 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 184.5 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 184.5977 | -0.07 | 0.93 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 184.707 | -0.14 | 0.86 | -0.68 | 0.32 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:54 | 184.8203 | -0.19 | 0.81 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:54 | 184.918 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 185.0195 | -0.03 | 0.97 | -0.79 | 0.21 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:54 | 185.1172 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 185.2305 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 185.3203 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 185.418 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 185.5273 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 185.6602 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:54 | 185.75 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 185.8477 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 185.9492 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 186.0469 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:54 | 186.1484 | -0.08 | 0.92 | -0.73 | 0.27 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 186.25 | -0.13 | 0.87 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 186.3477 | -0.17 | 0.83 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:54 | 186.457 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 25.39
2019-09-04 | 9:54 | 186.5469 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 186.6602 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 186.7695 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 186.8594 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 186.9688 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 187.0781 | 0.02 | 1.02 | -0.8 | 0.2 | -0.68 | 0.32 | 76.17 | 26.37
2019-09-04 | 9:54 | 187.1875 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:54 | 187.2773 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 187.3672 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 187.4805 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 187.5977 | -0.02 | 0.98 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 187.707 | -0.13 | 0.87 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 187.8086 | -0.2 | 0.8 | -0.65 | 0.35 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 187.9102 | -0.19 | 0.81 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:54 | 188 | -0.02 | 0.98 | -0.78 | 0.22 | -0.65 | 0.35 | 73.24 | 25.39
2019-09-04 | 9:54 | 188.0977 | -0.01 | 0.99 | -0.78 | 0.22 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:54 | 188.1992 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 188.2969 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 188.3906 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 188.5 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 188.6094 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 188.707 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 188.8086 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 188.918 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 189.0195 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 189.1406 | -0.08 | 0.92 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 189.2383 | -0.15 | 0.85 | -0.68 | 0.32 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:54 | 189.3398 | -0.17 | 0.83 | -0.65 | 0.35 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 189.4375 | -0.09 | 0.91 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:54 | 189.5391 | -0.01 | 0.99 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 189.6289 | -0.03 | 0.97 | -0.79 | 0.21 | -0.66 | 0.34 | 75.2 | 26.37
2019-09-04 | 9:54 | 189.7383 | 0.01 | 1.01 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 189.8672 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 189.9688 | -0.01 | 0.99 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 190.0586 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 76.17 | 27.34
2019-09-04 | 9:54 | 190.1484 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 190.25 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 190.3477 | 0.01 | 1.01 | -0.8 | 0.2 | -0.7 | 0.3 | 74.22 | 26.37
2019-09-04 | 9:54 | 190.457 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 190.5703 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 190.668 | -0.12 | 0.88 | -0.71 | 0.29 | -0.67 | 0.33 | 76.17 | 25.39
2019-09-04 | 9:54 | 190.7578 | -0.17 | 0.83 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 190.8672 | -0.17 | 0.83 | -0.65 | 0.35 | -0.65 | 0.35 | 75.2 | 27.34
2019-09-04 | 9:54 | 190.9688 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:54 | 191.0703 | -0.02 | 0.98 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 191.1797 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 191.2773 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 191.3984 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 191.4883 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 191.5898 | 0.02 | 1.02 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 191.707 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 191.8203 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 191.8906 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 76.17 | 26.37
2019-09-04 | 9:54 | 192 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:54 | 192.0977 | -0.06 | 0.94 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 192.207 | -0.15 | 0.85 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 192.3086 | -0.17 | 0.83 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:54 | 192.4102 | -0.19 | 0.81 | -0.64 | 0.36 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 9:54 | 192.5078 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 192.6172 | -0.01 | 0.99 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 192.7383 | -0.01 | 0.99 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 192.8281 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 192.9297 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 193.0195 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 193.1289 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 193.2305 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 25.39
2019-09-04 | 9:54 | 193.3281 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 193.4375 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 193.5586 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 193.6406 | -0.09 | 0.91 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 193.75 | -0.16 | 0.84 | -0.68 | 0.32 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 193.8594 | -0.18 | 0.82 | -0.64 | 0.36 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 193.9492 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 194.0469 | -0.02 | 0.98 | -0.79 | 0.21 | -0.65 | 0.35 | 75.2 | 26.37
2019-09-04 | 9:54 | 194.1602 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 194.2578 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 194.3594 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 194.4805 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 194.5898 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 194.6797 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 194.7891 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 194.8789 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 194.9805 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 195.0781 | -0.04 | 0.96 | -0.77 | 0.23 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:54 | 195.1797 | -0.15 | 0.85 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 195.2969 | -0.17 | 0.83 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 195.3906 | -0.19 | 0.81 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 25.39
2019-09-04 | 9:54 | 195.4883 | -0.03 | 0.97 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 195.5898 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 195.707 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 195.8203 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 195.918 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 196 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 76.17 | 27.34
2019-09-04 | 9:54 | 196.1094 | -0.02 | 0.98 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 196.2305 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 196.3203 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 196.418 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 196.5195 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 196.6172 | -0.09 | 0.91 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 196.7188 | -0.14 | 0.86 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 196.8281 | -0.18 | 0.82 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 196.9297 | -0.1 | 0.9 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 197.0273 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 197.1406 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 197.25 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 197.3477 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 197.457 | 0.01 | 1.01 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 197.5469 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 197.6484 | -0.02 | 0.98 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 197.75 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 197.8594 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 197.9492 | -0.01 | 0.99 | -0.81 | 0.19 | -0.7 | 0.3 | 74.22 | 26.37
2019-09-04 | 9:54 | 198.0703 | -0.01 | 0.99 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 198.168 | -0.13 | 0.87 | -0.7 | 0.3 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 198.2695 | -0.15 | 0.85 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 198.3984 | -0.17 | 0.83 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 198.4805 | -0.03 | 0.97 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:54 | 198.5703 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:54 | 198.6797 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 198.7773 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 198.8789 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 198.9805 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 199.0898 | -0.01 | 0.99 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 199.1875 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 199.2969 | 0.02 | 1.02 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 199.3984 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 199.5078 | 0.02 | 1.02 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:54 | 199.6289 | -0.04 | 0.96 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 199.707 | -0.15 | 0.85 | -0.71 | 0.29 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 199.8086 | -0.18 | 0.82 | -0.66 | 0.34 | -0.66 | 0.34 | 76.17 | 27.34
2019-09-04 | 9:54 | 199.9102 | -0.19 | 0.81 | -0.64 | 0.36 | -0.66 | 0.34 | 75.2 | 26.37
2019-09-04 | 9:54 | 200.0078 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 200.1094 | -0.01 | 0.99 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 200.2305 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 200.3281 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 200.4297 | 0 | 1 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 25.39
2019-09-04 | 9:54 | 200.5469 | -0.04 | 0.96 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 200.6289 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 200.7305 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 200.8398 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 200.9375 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 201.0391 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 201.1406 | -0.09 | 0.91 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 201.2383 | -0.16 | 0.84 | -0.69 | 0.31 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 201.3594 | -0.18 | 0.82 | -0.65 | 0.35 | -0.66 | 0.34 | 76.17 | 25.39
2019-09-04 | 9:54 | 201.4805 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 201.5703 | -0.05 | 0.95 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 201.6797 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 201.7891 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 201.8789 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 201.9805 | -0.03 | 0.97 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 202.0703 | 0.01 | 1.01 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 202.168 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:54 | 202.2695 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 202.3789 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 25.39
2019-09-04 | 9:54 | 202.4805 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 202.5898 | -0.03 | 0.97 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 202.6875 | -0.1 | 0.9 | -0.73 | 0.27 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 202.7891 | -0.19 | 0.81 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 202.8984 | -0.2 | 0.8 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 202.9883 | -0.04 | 0.96 | -0.79 | 0.21 | -0.66 | 0.34 | 75.2 | 25.39
2019-09-04 | 9:54 | 203.0977 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 203.207 | -0.03 | 0.97 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 203.3203 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 203.4102 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 203.5273 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 203.6289 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 203.7188 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 74.22 | 25.39
2019-09-04 | 9:54 | 203.8203 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 203.918 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 76.17 | 26.37
2019-09-04 | 9:54 | 204.0195 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 204.1406 | -0.05 | 0.95 | -0.76 | 0.24 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 204.25 | -0.13 | 0.87 | -0.7 | 0.3 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 204.3477 | -0.2 | 0.8 | -0.65 | 0.35 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:54 | 204.4375 | -0.14 | 0.86 | -0.67 | 0.33 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 204.5391 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 204.6406 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 204.75 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 204.8477 | -0.02 | 0.98 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:54 | 204.9805 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 205.0469 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 205.1797 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 25.39
2019-09-04 | 9:54 | 205.2695 | -0.04 | 0.96 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 205.3789 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 74.22 | 28.32
2019-09-04 | 9:54 | 205.4805 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 205.5703 | 0.03 | 1.03 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 205.668 | -0.1 | 0.9 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 205.7695 | -0.16 | 0.84 | -0.68 | 0.32 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 205.8672 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 205.9805 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 206.0781 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 206.1797 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 206.2773 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 206.3789 | -0.03 | 0.97 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 206.4883 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 206.5898 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 206.6875 | -0.02 | 0.98 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 206.7969 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 206.8984 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 207.0078 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 207.1289 | -0.04 | 0.96 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 207.2188 | -0.11 | 0.89 | -0.71 | 0.29 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 207.3398 | -0.18 | 0.82 | -0.65 | 0.35 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 207.4297 | -0.19 | 0.81 | -0.65 | 0.35 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 207.5195 | -0.04 | 0.96 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 25.39
2019-09-04 | 9:54 | 207.6289 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 207.7578 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 207.8906 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 207.9883 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:54 | 208.0898 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 208.1875 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 208.2969 | -0.03 | 0.97 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 208.3906 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 208.457 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 73.24 | 25.39
2019-09-04 | 9:54 | 208.5469 | 0.01 | 1.01 | -0.8 | 0.2 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:54 | 208.6602 | -0.1 | 0.9 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 208.7695 | -0.19 | 0.81 | -0.66 | 0.34 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 208.8672 | -0.19 | 0.81 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:54 | 208.9492 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 209.0586 | -0.05 | 0.95 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 209.1602 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 209.2578 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 209.3672 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:54 | 209.4688 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 209.5703 | -0.02 | 0.98 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 209.6875 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 209.7891 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 73.24 | 26.37
2019-09-04 | 9:54 | 209.9102 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 210 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 76.17 | 26.37
2019-09-04 | 9:54 | 210.0898 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 210.1875 | -0.12 | 0.88 | -0.73 | 0.27 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 9:54 | 210.2891 | -0.17 | 0.83 | -0.68 | 0.32 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 210.3906 | -0.2 | 0.8 | -0.64 | 0.36 | -0.65 | 0.35 | 74.22 | 26.37
2019-09-04 | 9:54 | 210.4883 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 210.5977 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 210.6992 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 210.8203 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 210.918 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 211.0195 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 211.1094 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 211.2188 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 211.3398 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 211.4375 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 211.5273 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 211.6172 | -0.06 | 0.94 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 211.7305 | -0.17 | 0.83 | -0.68 | 0.32 | -0.68 | 0.32 | 76.17 | 27.34
2019-09-04 | 9:54 | 211.8281 | -0.18 | 0.82 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 211.9297 | -0.18 | 0.82 | -0.65 | 0.35 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:54 | 212.0391 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 25.39
2019-09-04 | 9:54 | 212.1289 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 9:54 | 212.2383 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 212.3477 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:54 | 212.457 | 0 | 1 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 212.5469 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 212.6602 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 212.7773 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 212.8789 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 212.9688 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 213.0781 | -0.02 | 0.98 | -0.82 | 0.18 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 213.168 | -0.11 | 0.89 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 213.2773 | -0.17 | 0.83 | -0.68 | 0.32 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 213.3789 | -0.18 | 0.82 | -0.65 | 0.35 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:54 | 213.4805 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 213.5781 | -0.03 | 0.97 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 213.6992 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 213.7969 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 213.8906 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 213.9883 | 0.01 | 1.01 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 214.0977 | -0.02 | 0.98 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 214.1875 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 9:54 | 214.2969 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 214.3984 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 214.5078 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 214.6094 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 214.707 | -0.13 | 0.87 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 214.8086 | -0.18 | 0.82 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 214.918 | -0.21 | 0.79 | -0.69 | 0.31 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 215.0273 | -0.04 | 0.96 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 215.1406 | -0.02 | 0.98 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 215.2383 | -0.03 | 0.97 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 215.3281 | 0 | 1 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 215.4375 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 215.5273 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 215.6484 | -0.01 | 0.99 | -0.8 | 0.2 | -0.7 | 0.3 | 75.2 | 25.39
2019-09-04 | 9:54 | 215.7383 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 215.8398 | -0.02 | 0.98 | -0.81 | 0.19 | -0.68 | 0.32 | 76.17 | 27.34
2019-09-04 | 9:54 | 215.9492 | -0.01 | 0.99 | -0.81 | 0.19 | -0.7 | 0.3 | 75.2 | 28.32
2019-09-04 | 9:54 | 216.0391 | -0.02 | 0.98 | -0.81 | 0.19 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:54 | 216.1484 | -0.1 | 0.9 | -0.74 | 0.26 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 216.25 | -0.17 | 0.83 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 216.3672 | -0.21 | 0.79 | -0.65 | 0.35 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:54 | 216.4688 | -0.07 | 0.93 | -0.75 | 0.25 | -0.67 | 0.33 | 76.17 | 27.34
2019-09-04 | 9:54 | 216.5703 | -0.04 | 0.96 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:54 | 216.6797 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 216.7578 | -0.05 | 0.95 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:54 | 216.8672 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 216.9805 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 217.0703 | -0.05 | 0.95 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 217.1797 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 217.2969 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 217.3984 | -0.03 | 0.97 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 217.5 | -0.03 | 0.97 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 217.5781 | -0.05 | 0.95 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 25.39
2019-09-04 | 9:54 | 217.6875 | -0.15 | 0.85 | -0.71 | 0.29 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 217.7891 | -0.22 | 0.78 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 217.8984 | -0.22 | 0.78 | -0.64 | 0.36 | -0.65 | 0.35 | 74.22 | 26.37
2019-09-04 | 9:54 | 218.0078 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 218.0977 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 218.1992 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 218.2969 | -0.03 | 0.97 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:54 | 218.4102 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 218.5078 | -0.04 | 0.96 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 25.39
2019-09-04 | 9:54 | 218.6094 | -0.06 | 0.94 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 218.7188 | -0.07 | 0.93 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 218.8203 | -0.06 | 0.94 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 218.9492 | -0.08 | 0.92 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 219.0273 | -0.07 | 0.93 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 219.1289 | -0.14 | 0.86 | -0.75 | 0.25 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 219.2305 | -0.19 | 0.81 | -0.69 | 0.31 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 219.3281 | -0.23 | 0.77 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 219.4492 | -0.23 | 0.77 | -0.63 | 0.37 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 219.5391 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 219.6484 | -0.06 | 0.94 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 28.32
2019-09-04 | 9:54 | 219.75 | -0.07 | 0.93 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 25.39
2019-09-04 | 9:54 | 219.8477 | -0.06 | 0.94 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 219.9492 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 220.0586 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 220.1484 | -0.02 | 0.98 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 25.39
2019-09-04 | 9:54 | 220.2578 | -0.03 | 0.97 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 220.3594 | -0.03 | 0.97 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:54 | 220.4688 | -0.04 | 0.96 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:54 | 220.5703 | -0.01 | 0.99 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 220.668 | -0.16 | 0.84 | -0.71 | 0.29 | -0.67 | 0.33 | 76.17 | 27.34
2019-09-04 | 9:54 | 220.7695 | -0.21 | 0.79 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:54 | 220.8789 | -0.19 | 0.81 | -0.63 | 0.37 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:54 | 221 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 221.1172 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 221.1992 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 221.2969 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 24.41
2019-09-04 | 9:54 | 221.3906 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 221.5 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:54 | 221.5898 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 221.6992 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 221.8086 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 221.9102 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 222.0078 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:54 | 222.1172 | -0.08 | 0.92 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 222.207 | -0.16 | 0.84 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 222.3086 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 222.418 | -0.19 | 0.81 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 26.37
2019-09-04 | 9:54 | 222.5391 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:54 | 222.6406 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:54 | 222.7383 | 0 | 1 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:54 | 222.8281 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:54 | 222.9375 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:54 | 223.0391 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:54 | 223.1602 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:54 | 223.25 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 9:54 | 223.3398 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 223.4492 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:54 | 223.5391 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 223.6484 | -0.12 | 0.88 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:54 | 223.7578 | -0.18 | 0.82 | -0.68 | 0.32 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 223.8906 | -0.18 | 0.82 | -0.64 | 0.36 | -0.66 | 0.34 | 75.2 | 28.32
2019-09-04 | 9:54 | 223.9805 | -0.07 | 0.93 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:54 | 224.0586 | -0.04 | 0.96 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:54 | 224.1797 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:54 | 224.2695 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:54 | 224.3672 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:54 | 224.4688 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 224.5703 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 224.6797 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 224.7773 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 28.32
2019-09-04 | 9:55 | 224.8984 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:55 | 225 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:55 | 225.0781 | -0.04 | 0.96 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:55 | 225.1875 | -0.13 | 0.87 | -0.7 | 0.3 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 225.3203 | -0.19 | 0.81 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:55 | 225.4102 | -0.19 | 0.81 | -0.64 | 0.36 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:55 | 225.5 | -0.05 | 0.95 | -0.77 | 0.23 | -0.65 | 0.35 | 75.2 | 26.37
2019-09-04 | 9:55 | 225.6094 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:55 | 225.6992 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:55 | 225.7969 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:55 | 225.9102 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:55 | 226.0078 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:55 | 226.1172 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 226.2188 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:55 | 226.3203 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 226.4492 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 226.5469 | -0.01 | 0.99 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:55 | 226.6406 | -0.07 | 0.93 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:55 | 226.7578 | -0.13 | 0.87 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 226.8477 | -0.17 | 0.83 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:55 | 226.957 | -0.2 | 0.8 | -0.63 | 0.37 | -0.63 | 0.37 | 73.24 | 25.39
2019-09-04 | 9:55 | 227.0586 | -0.02 | 0.98 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:55 | 227.1602 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 227.25 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 227.3477 | 0 | 1 | -0.79 | 0.21 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:55 | 227.457 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 227.5469 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:55 | 227.6602 | 0 | 1 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 27.34
2019-09-04 | 9:55 | 227.7578 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:55 | 227.8789 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:55 | 227.9805 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:55 | 228.0781 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 27.34
2019-09-04 | 9:55 | 228.1875 | -0.09 | 0.91 | -0.73 | 0.27 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:55 | 228.2891 | -0.17 | 0.83 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:55 | 228.3906 | -0.18 | 0.82 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:55 | 228.4805 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:55 | 228.5898 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 228.6875 | -0.04 | 0.96 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 228.7773 | -0.03 | 0.97 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:55 | 228.9102 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 229.0195 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:55 | 229.1172 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:55 | 229.207 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:55 | 229.3086 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:55 | 229.3984 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 229.5078 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:55 | 229.6094 | -0.06 | 0.94 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 229.7188 | -0.14 | 0.86 | -0.69 | 0.31 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:55 | 229.8203 | -0.18 | 0.82 | -0.65 | 0.35 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:55 | 229.918 | -0.2 | 0.8 | -0.64 | 0.36 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:55 | 230.0195 | -0.04 | 0.96 | -0.78 | 0.22 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:55 | 230.1172 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 230.2188 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 230.3281 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:55 | 230.4688 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 230.5703 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:55 | 230.6406 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 230.7695 | -0.04 | 0.96 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:55 | 230.8789 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:55 | 230.9805 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 25.39
2019-09-04 | 9:55 | 231.0703 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:55 | 231.168 | -0.09 | 0.91 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 231.2578 | -0.16 | 0.84 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:55 | 231.3594 | -0.18 | 0.82 | -0.66 | 0.34 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:55 | 231.4688 | -0.11 | 0.89 | -0.72 | 0.28 | -0.66 | 0.34 | 75.2 | 25.39
2019-09-04 | 9:55 | 231.5703 | -0.05 | 0.95 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 231.668 | -0.05 | 0.95 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:55 | 231.7695 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:55 | 231.8984 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 27.34
2019-09-04 | 9:55 | 231.9805 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:55 | 232.0898 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:55 | 232.1797 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 232.2891 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:55 | 232.3789 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:55 | 232.4883 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 75.2 | 27.34
2019-09-04 | 9:55 | 232.5898 | -0.05 | 0.95 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 232.6914 | -0.14 | 0.86 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:55 | 232.8008 | -0.17 | 0.83 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 232.9297 | -0.17 | 0.83 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 233.0313 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-09-04 | 9:55 | 233.1406 | -0.03 | 0.97 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 233.2383 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 233.3086 | -0.02 | 0.98 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 233.4102 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:55 | 233.5195 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 233.6406 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:55 | 233.75 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 233.8398 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 28.32
2019-09-04 | 9:55 | 233.9297 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 234.0313 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 76.17 | 26.37
2019-09-04 | 9:55 | 234.1289 | -0.07 | 0.93 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:55 | 234.2383 | -0.16 | 0.84 | -0.68 | 0.32 | -0.68 | 0.32 | 74.22 | 25.39
2019-09-04 | 9:55 | 234.3398 | -0.18 | 0.82 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:55 | 234.4609 | -0.17 | 0.83 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:55 | 234.5586 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 9:55 | 234.6484 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-09-04 | 9:55 | 234.7617 | -0.02 | 0.98 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 234.8594 | -0.01 | 0.99 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 26.37
2019-09-04 | 9:55 | 234.9609 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 25.39
2019-09-04 | 9:55 | 235.0508 | -0.01 | 0.99 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 235.1602 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:55 | 235.2617 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 235.3711 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:55 | 235.4688 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 25.39
2019-09-04 | 9:55 | 235.5898 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:55 | 235.6914 | -0.09 | 0.91 | -0.72 | 0.28 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 235.7891 | -0.17 | 0.83 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 27.34
2019-09-04 | 9:55 | 235.8789 | -0.17 | 0.83 | -0.65 | 0.35 | -0.66 | 0.34 | 75.2 | 27.34
2019-09-04 | 9:55 | 235.9805 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 26.37
2019-09-04 | 9:55 | 236.0781 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 236.1914 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 25.39
2019-09-04 | 9:55 | 236.3203 | -0.02 | 0.98 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 25.39
2019-09-04 | 9:55 | 236.3984 | -0.02 | 0.98 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 27.34
2019-09-04 | 9:55 | 236.5117 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:55 | 236.6211 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 236.7383 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 236.8281 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 236.918 | -0.03 | 0.97 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 25.39
2019-09-04 | 9:55 | 237.0117 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:55 | 237.1211 | 0 | 1 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 237.2188 | -0.12 | 0.88 | -0.71 | 0.29 | -0.69 | 0.31 | 74.22 | 26.37
2019-09-04 | 9:55 | 237.3203 | -0.18 | 0.82 | -0.66 | 0.34 | -0.66 | 0.34 | 75.2 | 26.37
2019-09-04 | 9:55 | 237.4414 | -0.17 | 0.83 | -0.64 | 0.36 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 237.5391 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-09-04 | 9:55 | 237.6289 | -0.02 | 0.98 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-09-04 | 9:55 | 237.75 | -0.02 | 0.98 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 25.39
2019-09-04 | 9:55 | 237.8516 | -0.01 | 0.99 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-09-04 | 9:55 | 237.9414 | 0 | 1 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 26.37
2019-09-04 | 9:55 | 238.0508 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 76.17 | 26.37
2019-09-04 | 9:55 | 238.1484 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 28.32
2019-09-04 | 9:55 | 238.25 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:55 | 238.3711 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 9:55 | 238.4609 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 238.5508 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:55 | 238.6484 | -0.1 | 0.9 | -0.73 | 0.27 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 238.75 | -0.16 | 0.84 | -0.66 | 0.34 | -0.68 | 0.32 | 74.22 | 26.37
2019-09-04 | 9:55 | 238.8594 | -0.19 | 0.81 | -0.65 | 0.35 | -0.66 | 0.34 | 73.24 | 27.34
2019-09-04 | 9:55 | 238.9609 | -0.15 | 0.85 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 24.41
2019-09-04 | 9:55 | 239.0703 | -0.04 | 0.96 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 26.37
2019-09-04 | 9:55 | 239.1797 | -0.04 | 0.96 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 239.3008 | -0.01 | 0.99 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 9:55 | 239.3984 | 0 | 1 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-09-04 | 9:55 | 239.4883 | -0.01 | 0.99 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 25.39
2019-09-04 | 9:55 | 239.6094 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 25.39
2019-09-04 | 9:55 | 239.7109 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 25.39
2019-09-04 | 9:55 | 239.8008 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 26.37
2019-09-04 | 9:55 | 239.8906 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 26.37
2019-09-04 | 9:55 | 240 | -0.02 | 0.98 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-09-04 | 9:55 | 240.1016 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 28.32
2019-09-04 | 9:55 | 240.1992 | -0.08 | 0.92 | -0.72 | 0.28 | -0.69 | 0.31 | 74.22 | 27.34
2019-09-04 | 9:55 | 240.3008 | -0.16 | 0.84 | -0.66 | 0.34 | -0.66 | 0.34 | 75.2 | 26.37

## 7.2mL s
|  | Timer |  | BoilerPressure |  | HEPressure |  | SCPressure
Date | Clock | raw | linked | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | HETemperature | SCTemperature
2019-09-04 | 10:37 | 0.097656 | 0.097656 | 0.05 | 1.05 | -0.3 | 0.7 | -0.25 | 0.75 | 26.37 | 22.46 | Flow
2019-09-04 | 10:37 | 0.20703 | 0.20703 | 0.06 | 1.06 | -0.3 | 0.7 | -0.25 | 0.75 | 28.32 | 22.46 | mL | seconds
2019-09-04 | 10:37 | 0.30859 | 0.30859 | 0.07 | 1.07 | -0.29 | 0.71 | -0.26 | 0.74 | 27.34 | 23.44 | 100 | 13 | 7.7 | start
2019-09-04 | 10:37 | 0.40625 | 0.40625 | 0.02 | 1.02 | -0.27 | 0.73 | -0.25 | 0.75 | 26.37 | 22.46 | 100 | 13 | 7.7
2019-09-04 | 10:37 | 0.51953 | 0.51953 | 0.01 | 1.01 | -0.26 | 0.74 | -0.24 | 0.76 | 27.34 | 22.46 | 100 | 13 | 7.7
2019-09-04 | 10:37 | 0.61719 | 0.61719 | -0.02 | 0.98 | -0.24 | 0.76 | -0.23 | 0.77 | 26.37 | 21.48
2019-09-04 | 10:37 | 0.71875 | 0.71875 | -0.04 | 0.96 | -0.25 | 0.75 | -0.23 | 0.77 | 27.34 | 23.44 | 100 | 15 | 6.7 | end
2019-09-04 | 10:37 | 0.81641 | 0.81641 | -0.01 | 0.99 | -0.24 | 0.76 | -0.22 | 0.78 | 27.34 | 23.44 | 100 | 15 | 6.7
2019-09-04 | 10:37 | 0.92969 | 0.92969 | 0.04 | 1.04 | -0.27 | 0.73 | -0.22 | 0.78 | 27.34 | 23.44 | 100 | 15 | 6.7
2019-09-04 | 10:37 | 1.0273 | 1.0273 | 0.06 | 1.06 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 1.1289 | 1.1289 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 23.44 |  |  | 7.2 | average
2019-09-04 | 10:37 | 1.2266 | 1.2266 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 21.48
2019-09-04 | 10:37 | 1.3398 | 1.3398 | 0.05 | 1.05 | -0.29 | 0.71 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 1.4375 | 1.4375 | 0.06 | 1.06 | -0.29 | 0.71 | -0.23 | 0.77 | 26.37 | 21.48
2019-09-04 | 10:37 | 1.5391 | 1.5391 | 0.06 | 1.06 | -0.27 | 0.73 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 1.6484 | 1.6484 | 0.07 | 1.07 | -0.3 | 0.7 | -0.25 | 0.75 | 26.37 | 23.44
2019-09-04 | 10:37 | 1.75 | 1.75 | 0.07 | 1.07 | -0.31 | 0.69 | -0.27 | 0.73 | 26.37 | 23.44
2019-09-04 | 10:37 | 1.8477 | 1.8477 | 0.06 | 1.06 | -0.3 | 0.7 | -0.24 | 0.76 | 28.32 | 23.44
2019-09-04 | 10:37 | 1.9492 | 1.9492 | 0.01 | 1.01 | -0.27 | 0.73 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 2.0586 | 2.0586 | 0 | 1 | -0.26 | 0.74 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 2.1562 | 2.1562 | -0.02 | 0.98 | -0.24 | 0.76 | -0.23 | 0.77 | 26.37 | 23.44
2019-09-04 | 10:37 | 2.2578 | 2.2578 | -0.01 | 0.99 | -0.24 | 0.76 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 2.3594 | 2.3594 | 0.02 | 1.02 | -0.26 | 0.74 | -0.22 | 0.78 | 27.34 | 23.44
2019-09-04 | 10:37 | 2.4688 | 2.4688 | 0.04 | 1.04 | -0.27 | 0.73 | -0.22 | 0.78 | 27.34 | 24.41
2019-09-04 | 10:37 | 2.5664 | 2.5664 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 2.668 | 2.668 | 0.04 | 1.04 | -0.29 | 0.71 | -0.24 | 0.76 | 28.32 | 22.46
2019-09-04 | 10:37 | 2.7773 | 2.7773 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 2.8789 | 2.8789 | 0.04 | 1.04 | -0.29 | 0.71 | -0.25 | 0.75 | 26.37 | 22.46
2019-09-04 | 10:37 | 2.9766 | 2.9766 | 0.07 | 1.07 | -0.29 | 0.71 | -0.25 | 0.75 | 27.34 | 23.44
2019-09-04 | 10:37 | 3.0781 | 3.0781 | 0.06 | 1.06 | -0.29 | 0.71 | -0.25 | 0.75 | 27.34 | 21.48
2019-09-04 | 10:37 | 3.1875 | 3.1875 | 0.05 | 1.05 | -0.3 | 0.7 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 3.2891 | 3.2891 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 28.32 | 22.46
2019-09-04 | 10:37 | 3.3867 | 3.3867 | 0.04 | 1.04 | -0.29 | 0.71 | -0.24 | 0.76 | 28.32 | 22.46 | Equilibrium pressures from 175 seconds
2019-09-04 | 10:37 | 3.4883 | 3.4883 | 0 | 1 | -0.25 | 0.75 | -0.22 | 0.78 | 27.34 | 22.46
2019-09-04 | 10:37 | 3.5977 | 3.5977 | -0.02 | 0.98 | -0.26 | 0.74 | -0.23 | 0.77 | 27.34 | 22.46 | minimum boiler pressure from 175 seconds is: |  |  |  | 0.83 |  | average Pb | 0.98064
2019-09-04 | 10:37 | 3.6992 | 3.6992 | -0.01 | 0.99 | -0.25 | 0.75 | -0.23 | 0.77 | 26.37 | 22.46 | maximum boiler pressure from 175 seconds is: |  |  |  | 1.04
2019-09-04 | 10:37 | 3.7969 | 3.7969 | -0.02 | 0.98 | -0.23 | 0.77 | -0.22 | 0.78 | 27.34 | 22.46
2019-09-04 | 10:37 | 3.8984 | 3.8984 | 0.04 | 1.04 | -0.28 | 0.72 | -0.22 | 0.78 | 26.37 | 22.46 | minimum heat exchanger pressure from 175 seconds is: |  |  |  | 0.22 |  | average Phe | 0.30005
2019-09-04 | 10:37 | 4.0078 | 4.0078 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 22.46 | maximum heat exchanger pressure from 175 seconds is |  |  |  | 0.45
2019-09-04 | 10:37 | 4.1094 | 4.1094 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 4.207 | 4.207 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 28.32 | 21.48
2019-09-04 | 10:37 | 4.3164 | 4.3164 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 4.418 | 4.418 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 4.5195 | 4.5195 | 0.04 | 1.04 | -0.29 | 0.71 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 4.6172 | 4.6172 | 0.06 | 1.06 | -0.31 | 0.69 | -0.25 | 0.75 | 27.34 | 22.46
2019-09-04 | 10:37 | 4.7266 | 4.7266 | 0.05 | 1.05 | -0.3 | 0.7 | -0.24 | 0.76 | 26.37 | 22.46
2019-09-04 | 10:37 | 4.8281 | 4.8281 | 0.08 | 1.08 | -0.29 | 0.71 | -0.25 | 0.75 | 27.34 | 22.46
2019-09-04 | 10:37 | 4.9297 | 4.9297 | 0.01 | 1.01 | -0.27 | 0.73 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 5.0391 | 5.0391 | -0.01 | 0.99 | -0.26 | 0.74 | -0.24 | 0.76 | 26.37 | 22.46
2019-09-04 | 10:37 | 5.1367 | 5.1367 | 0.01 | 1.01 | -0.26 | 0.74 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 5.2383 | 5.2383 | 0 | 1 | -0.23 | 0.77 | -0.22 | 0.78 | 27.34 | 22.46
2019-09-04 | 10:37 | 5.3477 | 5.3477 | -0.01 | 0.99 | -0.24 | 0.76 | -0.21 | 0.79 | 26.37 | 24.41
2019-09-04 | 10:37 | 5.4492 | 5.4492 | 0.04 | 1.04 | -0.27 | 0.73 | -0.21 | 0.79 | 26.37 | 22.46
2019-09-04 | 10:37 | 5.5469 | 5.5469 | 0.05 | 1.05 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 5.6484 | 5.6484 | 0.05 | 1.05 | -0.27 | 0.73 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 5.75 | 5.75 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 26.37 | 22.46
2019-09-04 | 10:37 | 5.8594 | 5.8594 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 28.32 | 22.46
2019-09-04 | 10:37 | 5.957 | 5.957 | 0.04 | 1.04 | -0.29 | 0.71 | -0.24 | 0.76 | 28.32 | 24.41
2019-09-04 | 10:37 | 6.0586 | 6.0586 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 6.1562 | 6.1562 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 6.2695 | 6.2695 | 0.04 | 1.04 | -0.3 | 0.7 | -0.24 | 0.76 | 26.37 | 22.46
2019-09-04 | 10:37 | 6.3672 | 6.3672 | 0.05 | 1.05 | -0.29 | 0.71 | -0.25 | 0.75 | 27.34 | 23.44 | temperature equilibrium from 175 seconds as well
2019-09-04 | 10:37 | 6.4766 | 6.4766 | 0 | 1 | -0.27 | 0.73 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 6.5781 | 6.5781 | 0.01 | 1.01 | -0.25 | 0.75 | -0.23 | 0.77 | 28.32 | 23.44 | minimum heat exchanger outlet temperature is: |  |  | 77.15 |  | average SC bath temp |  | 27.9839
2019-09-04 | 10:37 | 6.6797 | 6.6797 | -0.01 | 0.99 | -0.25 | 0.75 | -0.22 | 0.78 | 27.34 | 24.41 | maximum heat exchanger outlet temperature is: |  |  | 81.05
2019-09-04 | 10:37 | 6.7773 | 6.7773 | -0.01 | 0.99 | -0.24 | 0.76 | -0.21 | 0.79 | 26.37 | 24.41
2019-09-04 | 10:37 | 6.8867 | 6.8867 | 0.04 | 1.04 | -0.27 | 0.73 | -0.22 | 0.78 | 26.37 | 22.46 | average HE outlet temperature is: |  |  | 78.6688 |  | STDEV | 0.73734
2019-09-04 | 10:37 | 6.9883 | 6.9883 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 7.0898 | 7.0898 | 0.07 | 1.07 | -0.29 | 0.71 | -0.23 | 0.77 | 26.37 | 22.46 | number of temperature points measured is: |  |  | 650
2019-09-04 | 10:37 | 7.1875 | 7.1875 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 7.2969 | 7.2969 | 0.08 | 1.08 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 7.3984 | 7.3984 | 0.08 | 1.08 | -0.29 | 0.71 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 7.5 | 7.5 | 0.06 | 1.06 | -0.28 | 0.72 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 7.5977 | 7.5977 | 0.06 | 1.06 | -0.29 | 0.71 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 7.6992 | 7.6992 | 0.08 | 1.08 | -0.29 | 0.71 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 7.8086 | 7.8086 | 0.08 | 1.08 | -0.3 | 0.7 | -0.24 | 0.76 | 26.37 | 22.46
2019-09-04 | 10:37 | 7.9062 | 7.9062 | 0.03 | 1.03 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 23.44
2019-09-04 | 10:37 | 8.0195 | 8.0195 | 0.01 | 1.01 | -0.26 | 0.74 | -0.23 | 0.77 | 26.37 | 23.44
2019-09-04 | 10:37 | 8.1172 | 8.1172 | 0.01 | 1.01 | -0.24 | 0.76 | -0.21 | 0.79 | 28.32 | 23.44
2019-09-04 | 10:37 | 8.2188 | 8.2188 | -0.01 | 0.99 | -0.24 | 0.76 | -0.23 | 0.77 | 28.32 | 22.46
2019-09-04 | 10:37 | 8.3164 | 8.3164 | -0.01 | 0.99 | -0.23 | 0.77 | -0.22 | 0.78 | 27.34 | 22.46
2019-09-04 | 10:37 | 8.4297 | 8.4297 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 27.34 | 23.44
2019-09-04 | 10:37 | 8.5273 | 8.5273 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 8.6289 | 8.6289 | 0.05 | 1.05 | -0.27 | 0.73 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 8.7266 | 8.7266 | 0.05 | 1.05 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 21.48
2019-09-04 | 10:37 | 8.8398 | 8.8398 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 8.9375 | 8.9375 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 23.44
2019-09-04 | 10:37 | 9.0391 | 9.0391 | 0.08 | 1.08 | -0.29 | 0.71 | -0.24 | 0.76 | 27.34 | 23.44
2019-09-04 | 10:37 | 9.1484 | 9.1484 | 0.08 | 1.08 | -0.27 | 0.73 | -0.24 | 0.76 | 28.32 | 23.44
2019-09-04 | 10:37 | 9.25 | 9.25 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 9.3477 | 9.3477 | 0.06 | 1.06 | -0.3 | 0.7 | -0.24 | 0.76 | 29.3 | 23.44
2019-09-04 | 10:37 | 9.4492 | 9.4492 | 0 | 1 | -0.26 | 0.74 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 9.5586 | 9.5586 | -0.01 | 0.99 | -0.25 | 0.75 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 9.6562 | 9.6562 | -0.01 | 0.99 | -0.23 | 0.77 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 9.7578 | 9.7578 | -0.01 | 0.99 | -0.25 | 0.75 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 9.8594 | 9.8594 | 0.01 | 1.01 | -0.25 | 0.75 | -0.22 | 0.78 | 27.34 | 23.44
2019-09-04 | 10:37 | 9.9688 | 9.9688 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 10.0664 | 10.0664 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 23.44
2019-09-04 | 10:37 | 10.168 | 10.168 | 0.05 | 1.05 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 10.2773 | 10.2773 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 10.3789 | 10.3789 | 0.06 | 1.06 | -0.29 | 0.71 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 10.4766 | 10.4766 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 27.34 | 23.44
2019-09-04 | 10:37 | 10.5781 | 10.5781 | 0.05 | 1.05 | -0.29 | 0.71 | -0.25 | 0.75 | 27.34 | 22.46
2019-09-04 | 10:37 | 10.6875 | 10.6875 | 0.06 | 1.06 | -0.3 | 0.7 | -0.24 | 0.76 | 27.34 | 23.44
2019-09-04 | 10:37 | 10.7891 | 10.7891 | 0.06 | 1.06 | -0.29 | 0.71 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 10.8867 | 10.8867 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 10.9883 | 10.9883 | 0.03 | 1.03 | -0.25 | 0.75 | -0.22 | 0.78 | 28.32 | 23.44
2019-09-04 | 10:37 | 11.0977 | 11.0977 | 0 | 1 | -0.23 | 0.77 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 11.1992 | 11.1992 | -0.01 | 0.99 | -0.22 | 0.78 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 11.3086 | 11.3086 | -0.01 | 0.99 | -0.24 | 0.76 | -0.21 | 0.79 | 26.37 | 22.46
2019-09-04 | 10:37 | 11.4062 | 11.4062 | 0.03 | 1.03 | -0.26 | 0.74 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 11.5078 | 11.5078 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 11.6094 | 11.6094 | 0.06 | 1.06 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 24.41
2019-09-04 | 10:37 | 11.707 | 11.707 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 28.32 | 22.46
2019-09-04 | 10:37 | 11.8164 | 11.8164 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 23.44
2019-09-04 | 10:37 | 11.918 | 11.918 | 0.05 | 1.05 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 23.44
2019-09-04 | 10:37 | 12.0195 | 12.0195 | 0.06 | 1.06 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 12.1172 | 12.1172 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 12.2266 | 12.2266 | 0.06 | 1.06 | -0.28 | 0.72 | -0.25 | 0.75 | 27.34 | 23.44
2019-09-04 | 10:37 | 12.3281 | 12.3281 | 0.04 | 1.04 | -0.28 | 0.72 | -0.25 | 0.75 | 26.37 | 24.41
2019-09-04 | 10:37 | 12.4297 | 12.4297 | 0.02 | 1.02 | -0.25 | 0.75 | -0.23 | 0.77 | 26.37 | 23.44
2019-09-04 | 10:37 | 12.5391 | 12.5391 | -0.02 | 0.98 | -0.26 | 0.74 | -0.23 | 0.77 | 27.34 | 24.41
2019-09-04 | 10:37 | 12.6367 | 12.6367 | -0.02 | 0.98 | -0.24 | 0.76 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 12.7383 | 12.7383 | -0.01 | 0.99 | -0.22 | 0.78 | -0.2 | 0.8 | 27.34 | 22.46
2019-09-04 | 10:37 | 12.8477 | 12.8477 | 0 | 1 | -0.22 | 0.78 | -0.22 | 0.78 | 27.34 | 24.41
2019-09-04 | 10:37 | 12.9492 | 12.9492 | 0.04 | 1.04 | -0.26 | 0.74 | -0.21 | 0.79 | 26.37 | 24.41
2019-09-04 | 10:37 | 13.0469 | 13.0469 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 28.32 | 22.46
2019-09-04 | 10:37 | 13.1484 | 13.1484 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 27.34 | 24.41
2019-09-04 | 10:37 | 13.25 | 13.25 | 0.05 | 1.05 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 24.41
2019-09-04 | 10:37 | 13.3594 | 13.3594 | 0.06 | 1.06 | -0.29 | 0.71 | -0.23 | 0.77 | 26.37 | 24.41
2019-09-04 | 10:37 | 13.457 | 13.457 | 0.09 | 1.09 | -0.28 | 0.72 | -0.23 | 0.77 | 28.32 | 23.44
2019-09-04 | 10:37 | 13.5586 | 13.5586 | 0.06 | 1.06 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 13.6562 | 13.6562 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 24.41
2019-09-04 | 10:37 | 13.7695 | 13.7695 | 0.04 | 1.04 | -0.29 | 0.71 | -0.24 | 0.76 | 28.32 | 22.46
2019-09-04 | 10:37 | 13.8672 | 13.8672 | 0.06 | 1.06 | -0.3 | 0.7 | -0.25 | 0.75 | 28.32 | 23.44
2019-09-04 | 10:37 | 13.9766 | 13.9766 | 0 | 1 | -0.26 | 0.74 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 14.0781 | 14.0781 | -0.02 | 0.98 | -0.24 | 0.76 | -0.23 | 0.77 | 27.34 | 24.41
2019-09-04 | 10:37 | 14.1797 | 14.1797 | 0 | 1 | -0.22 | 0.78 | -0.21 | 0.79 | 27.34 | 24.41
2019-09-04 | 10:37 | 14.2773 | 14.2773 | -0.01 | 0.99 | -0.25 | 0.75 | -0.21 | 0.79 | 27.34 | 22.46
2019-09-04 | 10:37 | 14.3867 | 14.3867 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 14.4883 | 14.4883 | 0.06 | 1.06 | -0.26 | 0.74 | -0.22 | 0.78 | 28.32 | 23.44
2019-09-04 | 10:37 | 14.5898 | 14.5898 | 0.03 | 1.03 | -0.27 | 0.73 | -0.22 | 0.78 | 27.34 | 22.46
2019-09-04 | 10:37 | 14.6875 | 14.6875 | 0.05 | 1.05 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 22.46
2019-09-04 | 10:37 | 14.7891 | 14.7891 | 0.06 | 1.06 | -0.27 | 0.73 | -0.22 | 0.78 | 26.37 | 22.46
2019-09-04 | 10:37 | 14.8984 | 14.8984 | 0.06 | 1.06 | -0.29 | 0.71 | -0.23 | 0.77 | 26.37 | 23.44
2019-09-04 | 10:37 | 15 | 15 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 27.34 | 22.46
2019-09-04 | 10:37 | 15.1094 | 15.1094 | 0.06 | 1.06 | -0.29 | 0.71 | -0.23 | 0.77 | 28.32 | 23.44
2019-09-04 | 10:37 | 15.207 | 15.207 | 0.08 | 1.08 | -0.29 | 0.71 | -0.25 | 0.75 | 27.34 | 23.44
2019-09-04 | 10:37 | 15.3086 | 15.3086 | 0.06 | 1.06 | -0.3 | 0.7 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 15.4062 | 15.4062 | 0.04 | 1.04 | -0.26 | 0.74 | -0.23 | 0.77 | 28.32 | 24.41
2019-09-04 | 10:37 | 15.5195 | 15.5195 | 0 | 1 | -0.25 | 0.75 | -0.23 | 0.77 | 27.34 | 23.44
2019-09-04 | 10:37 | 15.6172 | 15.6172 | -0.03 | 0.97 | -0.24 | 0.76 | -0.21 | 0.79 | 28.32 | 24.41
2019-09-04 | 10:37 | 15.7188 | 15.7188 | -0.02 | 0.98 | -0.22 | 0.78 | -0.21 | 0.79 | 28.32 | 23.44
2019-09-04 | 10:37 | 15.8164 | 15.8164 | -0.03 | 0.97 | -0.22 | 0.78 | -0.2 | 0.8 | 27.34 | 23.44
2019-09-04 | 10:37 | 15.9297 | 15.9297 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 27.34 | 23.44
2019-09-04 | 10:37 | 16.0273 | 16.0273 | 0.06 | 1.06 | -0.27 | 0.73 | -0.22 | 0.78 | 28.32 | 23.44
2019-09-04 | 10:37 | 16.1289 | 16.1289 | 0.04 | 1.04 | -0.27 | 0.73 | -0.22 | 0.78 | 27.34 | 22.46
2019-09-04 | 10:37 | 16.2266 | 16.2266 | 0.06 | 1.06 | -0.28 | 0.72 | -0.22 | 0.78 | 28.32 | 22.46
2019-09-04 | 10:37 | 16.3398 | 16.3398 | 0.05 | 1.05 | -0.27 | 0.73 | -0.22 | 0.78 | 26.37 | 23.44
2019-09-04 | 10:37 | 16.4375 | 16.4375 | 0.08 | 1.08 | -0.28 | 0.72 | -0.24 | 0.76 | 30.27 | 24.41
2019-09-04 | 10:37 | 16.5391 | 16.5391 | 0.05 | 1.05 | -0.27 | 0.73 | -0.24 | 0.76 | 28.32 | 23.44
2019-09-04 | 10:37 | 16.6484 | 16.6484 | 0.04 | 1.04 | -0.3 | 0.7 | -0.24 | 0.76 | 28.32 | 23.44
2019-09-04 | 10:37 | 16.75 | 16.75 | 0.05 | 1.05 | -0.3 | 0.7 | -0.24 | 0.76 | 27.34 | 23.44
2019-09-04 | 10:37 | 16.8477 | 16.8477 | 0.06 | 1.06 | -0.29 | 0.71 | -0.24 | 0.76 | 27.34 | 22.46
2019-09-04 | 10:37 | 16.9492 | 16.9492 | 0.01 | 1.01 | -0.25 | 0.75 | -0.23 | 0.77 | 28.32 | 23.44
2019-09-04 | 10:37 | 17.0586 | 17.0586 | -0.01 | 0.99 | -0.23 | 0.77 | -0.22 | 0.78 | 27.34 | 24.41
2019-09-04 | 10:37 | 17.1562 | 17.1562 | 0.01 | 1.01 | -0.23 | 0.77 | -0.22 | 0.78 | 27.34 | 24.41
2019-09-04 | 10:37 | 17.2578 | 17.2578 | -0.01 | 0.99 | -0.24 | 0.76 | -0.22 | 0.78 | 27.34 | 23.44
2019-09-04 | 10:37 | 17.3672 | 17.3672 | -0.01 | 0.99 | -0.23 | 0.77 | -0.2 | 0.8 | 28.32 | 23.44
2019-09-04 | 10:37 | 17.4688 | 17.4688 | 0.05 | 1.05 | -0.26 | 0.74 | -0.2 | 0.8 | 28.32 | 23.44
2019-09-04 | 10:37 | 17.5664 | 17.5664 | 0.06 | 1.06 | -0.28 | 0.72 | -0.22 | 0.78 | 26.37 | 24.41
2019-09-04 | 10:37 | 17.668 | 17.668 | 0.06 | 1.06 | -0.27 | 0.73 | -0.22 | 0.78 | 26.37 | 24.41
2019-09-04 | 10:37 | 17.7773 | 17.7773 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 24.41
2019-09-04 | 10:37 | 17.8789 | 17.8789 | 0.05 | 1.05 | -0.27 | 0.73 | -0.22 | 0.78 | 27.34 | 24.41
2019-09-04 | 10:37 | 17.9766 | 17.9766 | 0.05 | 1.05 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 26.37
2019-09-04 | 10:37 | 18.0781 | 18.0781 | 0.06 | 1.06 | -0.28 | 0.72 | -0.22 | 0.78 | 27.34 | 24.41
2019-09-04 | 10:37 | 18.1875 | 18.1875 | 0.06 | 1.06 | -0.28 | 0.72 | -0.23 | 0.77 | 26.37 | 25.39
2019-09-04 | 10:37 | 18.2891 | 18.2891 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 28.32 | 25.39
2019-09-04 | 10:37 | 18.3867 | 18.3867 | 0.06 | 1.06 | -0.29 | 0.71 | -0.24 | 0.76 | 28.32 | 25.39
2019-09-04 | 10:37 | 18.5 | 18.5 | -0.01 | 0.99 | -0.26 | 0.74 | -0.23 | 0.77 | 28.32 | 26.37
2019-09-04 | 10:37 | 18.5977 | 18.5977 | -0.01 | 0.99 | -0.24 | 0.76 | -0.23 | 0.77 | 26.37 | 26.37
2019-09-04 | 10:37 | 18.6992 | 18.6992 | -0.01 | 0.99 | -0.24 | 0.76 | -0.22 | 0.78 | 26.37 | 26.37
2019-09-04 | 10:37 | 18.8086 | 18.8086 | -0.01 | 0.99 | -0.24 | 0.76 | -0.21 | 0.79 | 27.34 | 26.37
2019-09-04 | 10:37 | 18.9062 | 18.9062 | 0.04 | 1.04 | -0.26 | 0.74 | -0.21 | 0.79 | 27.34 | 26.37
2019-09-04 | 10:37 | 19.0078 | 19.0078 | 0.06 | 1.06 | -0.26 | 0.74 | -0.23 | 0.77 | 27.34 | 26.37
2019-09-04 | 10:37 | 19.1094 | 19.1094 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 26.37 | 26.37
2019-09-04 | 10:37 | 19.207 | 19.207 | 0.06 | 1.06 | -0.28 | 0.72 | -0.22 | 0.78 | 27.34 | 26.37
2019-09-04 | 10:37 | 19.3164 | 19.3164 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 26.37 | 28.32
2019-09-04 | 10:37 | 19.418 | 19.418 | 0.06 | 1.06 | -0.28 | 0.72 | -0.22 | 0.78 | 28.32 | 27.34
2019-09-04 | 10:37 | 19.5195 | 19.5195 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 27.34 | 28.32
2019-09-04 | 10:37 | 19.6172 | 19.6172 | 0.08 | 1.08 | -0.28 | 0.72 | -0.23 | 0.77 | 28.32 | 28.32
2019-09-04 | 10:37 | 19.7266 | 19.7266 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 27.34 | 27.34
2019-09-04 | 10:37 | 19.8281 | 19.8281 | 0.05 | 1.05 | -0.29 | 0.71 | -0.23 | 0.77 | 27.34 | 29.3
2019-09-04 | 10:37 | 19.9297 | 19.9297 | 0.02 | 1.02 | -0.26 | 0.74 | -0.23 | 0.77 | 27.34 | 28.32
2019-09-04 | 10:37 | 20.0391 | 20.0391 | 0 | 1 | -0.25 | 0.75 | -0.22 | 0.78 | 26.37 | 29.3
2019-09-04 | 10:37 | 20.1367 | 20.1367 | -0.02 | 0.98 | -0.24 | 0.76 | -0.22 | 0.78 | 27.34 | 28.32
2019-09-04 | 10:37 | 20.2383 | 20.2383 | -0.01 | 0.99 | -0.23 | 0.77 | -0.22 | 0.78 | 27.34 | 29.3
2019-09-04 | 10:37 | 20.3477 | 20.3477 | -0.01 | 0.99 | -0.24 | 0.76 | -0.21 | 0.79 | 26.37 | 29.3
2019-09-04 | 10:37 | 20.4492 | 20.4492 | 0.04 | 1.04 | -0.28 | 0.72 | -0.24 | 0.76 | 26.37 | 29.3
2019-09-04 | 10:37 | 20.5469 | 20.5469 | 0.06 | 1.06 | -0.27 | 0.73 | -0.24 | 0.76 | 28.32 | 30.27
2019-09-04 | 10:37 | 20.6484 | 20.6484 | 0.08 | 1.08 | -0.29 | 0.71 | -0.25 | 0.75 | 28.32 | 30.27
2019-09-04 | 10:37 | 20.75 | 20.75 | 0.05 | 1.05 | -0.3 | 0.7 | -0.25 | 0.75 | 28.32 | 30.27
2019-09-04 | 10:37 | 20.8594 | 20.8594 | 0.06 | 1.06 | -0.31 | 0.69 | -0.28 | 0.72 | 27.34 | 29.3
2019-09-04 | 10:37 | 20.957 | 20.957 | 0.05 | 1.05 | -0.33 | 0.67 | -0.29 | 0.71 | 29.3 | 30.27
2019-09-04 | 10:37 | 21.0586 | 21.0586 | 0.06 | 1.06 | -0.33 | 0.67 | -0.29 | 0.71 | 31.25 | 30.27
2019-09-04 | 10:37 | 21.1562 | 21.1562 | 0.04 | 1.04 | -0.35 | 0.65 | -0.3 | 0.7 | 33.2 | 30.27
2019-09-04 | 10:37 | 21.2695 | 21.2695 | 0.07 | 1.07 | -0.37 | 0.63 | -0.31 | 0.69 | 35.16 | 30.27
2019-09-04 | 10:37 | 21.3672 | 21.3672 | 0.08 | 1.08 | -0.37 | 0.63 | -0.32 | 0.68 | 37.11 | 31.25
2019-09-04 | 10:37 | 21.4766 | 21.4766 | -0.01 | 0.99 | -0.33 | 0.67 | -0.32 | 0.68 | 39.06 | 30.27
2019-09-04 | 10:37 | 21.5781 | 21.5781 | -0.02 | 0.98 | -0.33 | 0.67 | -0.31 | 0.69 | 41.02 | 30.27
2019-09-04 | 10:37 | 21.6797 | 21.6797 | -0.04 | 0.96 | -0.31 | 0.69 | -0.3 | 0.7 | 43.95 | 30.27
2019-09-04 | 10:37 | 21.7773 | 21.7773 | -0.04 | 0.96 | -0.31 | 0.69 | -0.31 | 0.69 | 46.88 | 31.25
2019-09-04 | 10:37 | 21.8867 | 21.8867 | 0.03 | 1.03 | -0.37 | 0.63 | -0.32 | 0.68 | 48.83 | 32.23
2019-09-04 | 10:37 | 21.9883 | 21.9883 | 0.06 | 1.06 | -0.37 | 0.63 | -0.35 | 0.65 | 49.8 | 31.25
2019-09-04 | 10:37 | 22.0898 | 22.0898 | 0.07 | 1.07 | -0.39 | 0.61 | -0.36 | 0.64 | 52.73 | 31.25
2019-09-04 | 10:37 | 22.1992 | 22.1992 | 0.06 | 1.06 | -0.41 | 0.59 | -0.36 | 0.64 | 54.69 | 31.25
2019-09-04 | 10:37 | 22.2969 | 22.2969 | 0.06 | 1.06 | -0.42 | 0.58 | -0.37 | 0.63 | 55.66 | 32.23
2019-09-04 | 10:37 | 22.3984 | 22.3984 | 0.06 | 1.06 | -0.43 | 0.57 | -0.38 | 0.62 | 57.62 | 32.23
2019-09-04 | 10:37 | 22.5 | 22.5 | 0.06 | 1.06 | -0.44 | 0.56 | -0.39 | 0.61 | 60.55 | 33.2
2019-09-04 | 10:37 | 22.6094 | 22.6094 | 0.06 | 1.06 | -0.45 | 0.55 | -0.4 | 0.6 | 61.52 | 32.23
2019-09-04 | 10:37 | 22.707 | 22.707 | 0.06 | 1.06 | -0.44 | 0.56 | -0.38 | 0.62 | 62.5 | 32.23
2019-09-04 | 10:37 | 22.8086 | 22.8086 | 0.06 | 1.06 | -0.45 | 0.55 | -0.42 | 0.58 | 64.45 | 32.23
2019-09-04 | 10:37 | 22.9062 | 22.9062 | 0.05 | 1.05 | -0.46 | 0.54 | -0.41 | 0.59 | 65.43 | 33.2
2019-09-04 | 10:37 | 23.0195 | 23.0195 | -0.01 | 0.99 | -0.38 | 0.62 | -0.39 | 0.61 | 65.43 | 32.23
2019-09-04 | 10:37 | 23.1172 | 23.1172 | -0.04 | 0.96 | -0.37 | 0.63 | -0.38 | 0.62 | 66.41 | 32.23
2019-09-04 | 10:37 | 23.2188 | 23.2188 | -0.03 | 0.97 | -0.37 | 0.63 | -0.38 | 0.62 | 67.38 | 33.2
2019-09-04 | 10:37 | 23.3164 | 23.3164 | -0.05 | 0.95 | -0.36 | 0.64 | -0.39 | 0.61 | 67.38 | 32.23
2019-09-04 | 10:37 | 23.4297 | 23.4297 | 0.04 | 1.04 | -0.46 | 0.54 | -0.4 | 0.6 | 67.38 | 33.2
2019-09-04 | 10:37 | 23.5273 | 23.5273 | 0.04 | 1.04 | -0.48 | 0.52 | -0.42 | 0.58 | 69.34 | 33.2
2019-09-04 | 10:37 | 23.6289 | 23.6289 | 0.06 | 1.06 | -0.48 | 0.52 | -0.44 | 0.56 | 68.36 | 32.23
2019-09-04 | 10:37 | 23.7383 | 23.7383 | 0.06 | 1.06 | -0.49 | 0.51 | -0.45 | 0.55 | 69.34 | 34.18
2019-09-04 | 10:37 | 23.8398 | 23.8398 | 0.07 | 1.07 | -0.49 | 0.51 | -0.44 | 0.56 | 68.36 | 34.18
2019-09-04 | 10:37 | 23.9375 | 23.9375 | 0.06 | 1.06 | -0.49 | 0.51 | -0.45 | 0.55 | 69.34 | 34.18
2019-09-04 | 10:37 | 24.0391 | 24.0391 | 0.08 | 1.08 | -0.51 | 0.49 | -0.44 | 0.56 | 68.36 | 34.18
2019-09-04 | 10:37 | 24.1484 | 24.1484 | 0.07 | 1.07 | -0.51 | 0.49 | -0.46 | 0.54 | 68.36 | 33.2
2019-09-04 | 10:37 | 24.25 | 24.25 | 0.05 | 1.05 | -0.51 | 0.49 | -0.47 | 0.53 | 70.31 | 34.18
2019-09-04 | 10:37 | 24.3477 | 24.3477 | 0.05 | 1.05 | -0.5 | 0.5 | -0.46 | 0.54 | 68.36 | 34.18
2019-09-04 | 10:37 | 24.4492 | 24.4492 | 0.04 | 1.04 | -0.47 | 0.53 | -0.46 | 0.54 | 70.31 | 35.16
2019-09-04 | 10:37 | 24.5586 | 24.5586 | -0.02 | 0.98 | -0.4 | 0.6 | -0.44 | 0.56 | 70.31 | 34.18
2019-09-04 | 10:37 | 24.6562 | 24.6562 | -0.06 | 0.94 | -0.41 | 0.59 | -0.43 | 0.57 | 68.36 | 34.18
2019-09-04 | 10:37 | 24.7578 | 24.7578 | -0.06 | 0.94 | -0.4 | 0.6 | -0.42 | 0.58 | 68.36 | 33.2
2019-09-04 | 10:37 | 24.8672 | 24.8672 | -0.08 | 0.92 | -0.4 | 0.6 | -0.43 | 0.57 | 68.36 | 34.18
2019-09-04 | 10:37 | 24.9688 | 24.9688 | 0.04 | 1.04 | -0.51 | 0.49 | -0.46 | 0.54 | 68.36 | 34.18
2019-09-04 | 10:37 | 25.0664 | 25.0664 | 0.07 | 1.07 | -0.52 | 0.48 | -0.46 | 0.54 | 68.36 | 36.13
2019-09-04 | 10:37 | 25.168 | 25.168 | 0.05 | 1.05 | -0.51 | 0.49 | -0.47 | 0.53 | 68.36 | 35.16
2019-09-04 | 10:37 | 25.2773 | 25.2773 | 0.04 | 1.04 | -0.54 | 0.46 | -0.47 | 0.53 | 68.36 | 35.16
2019-09-04 | 10:37 | 25.3789 | 25.3789 | 0.07 | 1.07 | -0.53 | 0.47 | -0.48 | 0.52 | 68.36 | 35.16
2019-09-04 | 10:37 | 25.4766 | 25.4766 | 0.06 | 1.06 | -0.54 | 0.46 | -0.48 | 0.52 | 69.34 | 35.16
2019-09-04 | 10:37 | 25.5781 | 25.5781 | 0.05 | 1.05 | -0.53 | 0.47 | -0.48 | 0.52 | 67.38 | 34.18
2019-09-04 | 10:37 | 25.6875 | 25.6875 | 0.06 | 1.06 | -0.54 | 0.46 | -0.48 | 0.52 | 69.34 | 36.13
2019-09-04 | 10:37 | 25.7891 | 25.7891 | 0.04 | 1.04 | -0.53 | 0.47 | -0.48 | 0.52 | 67.38 | 36.13
2019-09-04 | 10:37 | 25.8867 | 25.8867 | 0.06 | 1.06 | -0.53 | 0.47 | -0.49 | 0.51 | 68.36 | 35.16
2019-09-04 | 10:37 | 26 | 26 | -0.01 | 0.99 | -0.47 | 0.53 | -0.47 | 0.53 | 67.38 | 36.13
2019-09-04 | 10:37 | 26.0977 | 26.0977 | -0.03 | 0.97 | -0.44 | 0.56 | -0.46 | 0.54 | 67.38 | 36.13
2019-09-04 | 10:37 | 26.1992 | 26.1992 | -0.07 | 0.93 | -0.42 | 0.58 | -0.45 | 0.55 | 67.38 | 35.16
2019-09-04 | 10:37 | 26.3086 | 26.3086 | -0.08 | 0.92 | -0.41 | 0.59 | -0.45 | 0.55 | 67.38 | 35.16
2019-09-04 | 10:37 | 26.4062 | 26.4062 | 0.02 | 1.02 | -0.51 | 0.49 | -0.46 | 0.54 | 68.36 | 37.11
2019-09-04 | 10:37 | 26.5078 | 26.5078 | 0.04 | 1.04 | -0.53 | 0.47 | -0.49 | 0.51 | 67.38 | 36.13
2019-09-04 | 10:37 | 26.6094 | 26.6094 | 0.04 | 1.04 | -0.55 | 0.45 | -0.5 | 0.5 | 67.38 | 36.13
2019-09-04 | 10:37 | 26.707 | 26.707 | 0.05 | 1.05 | -0.54 | 0.46 | -0.49 | 0.51 | 68.36 | 37.11
2019-09-04 | 10:37 | 26.8164 | 26.8164 | 0.06 | 1.06 | -0.54 | 0.46 | -0.5 | 0.5 | 68.36 | 36.13
2019-09-04 | 10:37 | 26.918 | 26.918 | 0.06 | 1.06 | -0.55 | 0.45 | -0.51 | 0.49 | 69.34 | 36.13
2019-09-04 | 10:37 | 27.0195 | 27.0195 | 0.07 | 1.07 | -0.54 | 0.46 | -0.5 | 0.5 | 67.38 | 36.13
2019-09-04 | 10:37 | 27.1172 | 27.1172 | 0.08 | 1.08 | -0.55 | 0.45 | -0.52 | 0.48 | 68.36 | 36.13
2019-09-04 | 10:37 | 27.2266 | 27.2266 | 0.06 | 1.06 | -0.56 | 0.44 | -0.51 | 0.49 | 67.38 | 35.16
2019-09-04 | 10:37 | 27.3281 | 27.3281 | 0.06 | 1.06 | -0.56 | 0.44 | -0.52 | 0.48 | 67.38 | 37.11
2019-09-04 | 10:37 | 27.4375 | 27.4375 | 0.06 | 1.06 | -0.57 | 0.43 | -0.51 | 0.49 | 67.38 | 36.13
2019-09-04 | 10:37 | 27.5391 | 27.5391 | -0.04 | 0.96 | -0.47 | 0.53 | -0.49 | 0.51 | 67.38 | 37.11
2019-09-04 | 10:37 | 27.6367 | 27.6367 | -0.07 | 0.93 | -0.44 | 0.56 | -0.48 | 0.52 | 68.36 | 37.11
2019-09-04 | 10:37 | 27.7383 | 27.7383 | -0.09 | 0.91 | -0.43 | 0.57 | -0.48 | 0.52 | 67.38 | 36.13
2019-09-04 | 10:37 | 27.8477 | 27.8477 | -0.05 | 0.95 | -0.44 | 0.56 | -0.48 | 0.52 | 67.38 | 36.13
2019-09-04 | 10:37 | 27.9492 | 27.9492 | 0.04 | 1.04 | -0.55 | 0.45 | -0.51 | 0.49 | 67.38 | 36.13
2019-09-04 | 10:37 | 28.0469 | 28.0469 | 0.04 | 1.04 | -0.56 | 0.44 | -0.51 | 0.49 | 68.36 | 37.11
2019-09-04 | 10:37 | 28.1484 | 28.1484 | 0.04 | 1.04 | -0.56 | 0.44 | -0.53 | 0.47 | 68.36 | 38.09
2019-09-04 | 10:37 | 28.2578 | 28.2578 | 0.07 | 1.07 | -0.56 | 0.44 | -0.53 | 0.47 | 67.38 | 37.11
2019-09-04 | 10:37 | 28.3594 | 28.3594 | 0.06 | 1.06 | -0.57 | 0.43 | -0.53 | 0.47 | 69.34 | 38.09
2019-09-04 | 10:37 | 28.457 | 28.457 | 0.06 | 1.06 | -0.58 | 0.42 | -0.52 | 0.48 | 68.36 | 37.11
2019-09-04 | 10:37 | 28.5664 | 28.5664 | 0.06 | 1.06 | -0.58 | 0.42 | -0.53 | 0.47 | 68.36 | 37.11
2019-09-04 | 10:37 | 28.668 | 28.668 | 0.07 | 1.07 | -0.58 | 0.42 | -0.52 | 0.48 | 67.38 | 37.11
2019-09-04 | 10:37 | 28.7695 | 28.7695 | 0.07 | 1.07 | -0.59 | 0.41 | -0.53 | 0.47 | 68.36 | 37.11
2019-09-04 | 10:37 | 28.8672 | 28.8672 | 0.05 | 1.05 | -0.6 | 0.4 | -0.53 | 0.47 | 68.36 | 37.11
2019-09-04 | 10:37 | 28.9766 | 28.9766 | 0.04 | 1.04 | -0.56 | 0.44 | -0.53 | 0.47 | 67.38 | 37.11
2019-09-04 | 10:37 | 29.0781 | 29.0781 | -0.04 | 0.96 | -0.49 | 0.51 | -0.52 | 0.48 | 68.36 | 37.11
2019-09-04 | 10:37 | 29.1797 | 29.1797 | -0.07 | 0.93 | -0.47 | 0.53 | -0.52 | 0.48 | 68.36 | 38.09
2019-09-04 | 10:37 | 29.2773 | 29.2773 | -0.09 | 0.91 | -0.47 | 0.53 | -0.51 | 0.49 | 68.36 | 38.09
2019-09-04 | 10:37 | 29.3867 | 29.3867 | -0.01 | 0.99 | -0.51 | 0.49 | -0.52 | 0.48 | 68.36 | 37.11
2019-09-04 | 10:37 | 29.4883 | 29.4883 | 0.04 | 1.04 | -0.58 | 0.42 | -0.54 | 0.46 | 68.36 | 37.11
2019-09-04 | 10:37 | 29.5898 | 29.5898 | 0.05 | 1.05 | -0.58 | 0.42 | -0.54 | 0.46 | 68.36 | 38.09
2019-09-04 | 10:37 | 29.6875 | 29.6875 | 0.04 | 1.04 | -0.6 | 0.4 | -0.55 | 0.45 | 67.38 | 38.09
2019-09-04 | 10:37 | 29.7969 | 29.7969 | 0.05 | 1.05 | -0.6 | 0.4 | -0.55 | 0.45 | 67.38 | 38.09
2019-09-04 | 10:37 | 29.8984 | 29.8984 | 0.05 | 1.05 | -0.6 | 0.4 | -0.55 | 0.45 | 67.38 | 37.11
2019-09-04 | 10:37 | 30 | 30 | 0.06 | 1.06 | -0.61 | 0.39 | -0.56 | 0.44 | 67.38 | 38.09
2019-09-04 | 10:38 | 30.1094 | 30.1094 | 0.06 | 1.06 | -0.61 | 0.39 | -0.56 | 0.44 | 68.36 | 38.09
2019-09-04 | 10:38 | 30.207 | 30.207 | 0.05 | 1.05 | -0.61 | 0.39 | -0.56 | 0.44 | 67.38 | 39.06
2019-09-04 | 10:38 | 30.3086 | 30.3086 | 0.05 | 1.05 | -0.61 | 0.39 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 30.4062 | 30.4062 | 0.05 | 1.05 | -0.61 | 0.39 | -0.55 | 0.45 | 69.34 | 39.06
2019-09-04 | 10:38 | 30.5195 | 30.5195 | -0.02 | 0.98 | -0.52 | 0.48 | -0.54 | 0.46 | 68.36 | 40.04
2019-09-04 | 10:38 | 30.6172 | 30.6172 | -0.07 | 0.93 | -0.48 | 0.52 | -0.54 | 0.46 | 67.38 | 38.09
2019-09-04 | 10:38 | 30.7188 | 30.7188 | -0.09 | 0.91 | -0.47 | 0.53 | -0.53 | 0.47 | 68.36 | 38.09
2019-09-04 | 10:38 | 30.8281 | 30.8281 | -0.09 | 0.91 | -0.45 | 0.55 | -0.53 | 0.47 | 68.36 | 38.09
2019-09-04 | 10:38 | 30.9297 | 30.9297 | 0.03 | 1.03 | -0.59 | 0.41 | -0.54 | 0.46 | 67.38 | 38.09
2019-09-04 | 10:38 | 31.0273 | 31.0273 | 0.04 | 1.04 | -0.6 | 0.4 | -0.56 | 0.44 | 67.38 | 38.09
2019-09-04 | 10:38 | 31.1289 | 31.1289 | 0.05 | 1.05 | -0.62 | 0.38 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 31.2383 | 31.2383 | 0.05 | 1.05 | -0.62 | 0.38 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 10:38 | 31.3398 | 31.3398 | 0.05 | 1.05 | -0.62 | 0.38 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 10:38 | 31.4375 | 31.4375 | 0.06 | 1.06 | -0.63 | 0.37 | -0.58 | 0.42 | 68.36 | 39.06
2019-09-04 | 10:38 | 31.5391 | 31.5391 | 0.04 | 1.04 | -0.62 | 0.38 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 10:38 | 31.6484 | 31.6484 | 0.07 | 1.07 | -0.63 | 0.37 | -0.57 | 0.43 | 66.41 | 37.11
2019-09-04 | 10:38 | 31.75 | 31.75 | 0.05 | 1.05 | -0.64 | 0.36 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 31.8477 | 31.8477 | 0.06 | 1.06 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 10:38 | 31.9492 | 31.9492 | 0.04 | 1.04 | -0.62 | 0.38 | -0.58 | 0.42 | 67.38 | 37.11
2019-09-04 | 10:38 | 32.0586 | 32.0586 | -0.05 | 0.95 | -0.51 | 0.49 | -0.55 | 0.45 | 67.38 | 38.09
2019-09-04 | 10:38 | 32.1562 | 32.1562 | -0.08 | 0.92 | -0.49 | 0.51 | -0.55 | 0.45 | 67.38 | 38.09
2019-09-04 | 10:38 | 32.2695 | 32.2695 | -0.09 | 0.91 | -0.49 | 0.51 | -0.54 | 0.46 | 67.38 | 38.09
2019-09-04 | 10:38 | 32.3672 | 32.3672 | -0.1 | 0.9 | -0.45 | 0.55 | -0.54 | 0.46 | 68.36 | 39.06
2019-09-04 | 10:38 | 32.4688 | 32.4688 | 0.04 | 1.04 | -0.61 | 0.39 | -0.57 | 0.43 | 67.38 | 40.04
2019-09-04 | 10:38 | 32.5664 | 32.5664 | 0.04 | 1.04 | -0.62 | 0.38 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 32.6797 | 32.6797 | 0.06 | 1.06 | -0.63 | 0.37 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 32.7773 | 32.7773 | 0.04 | 1.04 | -0.63 | 0.37 | -0.58 | 0.42 | 67.38 | 38.09
2019-09-04 | 10:38 | 32.8789 | 32.8789 | 0.05 | 1.05 | -0.63 | 0.37 | -0.6 | 0.4 | 67.38 | 39.06
2019-09-04 | 10:38 | 32.9766 | 32.9766 | 0.04 | 1.04 | -0.64 | 0.36 | -0.59 | 0.41 | 68.36 | 37.11
2019-09-04 | 10:38 | 33.0781 | 33.0781 | 0.05 | 1.05 | -0.62 | 0.38 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 10:38 | 33.1875 | 33.1875 | 0.04 | 1.04 | -0.65 | 0.35 | -0.6 | 0.4 | 67.38 | 39.06
2019-09-04 | 10:38 | 33.2891 | 33.2891 | 0.06 | 1.06 | -0.65 | 0.35 | -0.59 | 0.41 | 66.41 | 37.11
2019-09-04 | 10:38 | 33.3867 | 33.3867 | 0.05 | 1.05 | -0.64 | 0.36 | -0.6 | 0.4 | 67.38 | 38.09
2019-09-04 | 10:38 | 33.5 | 33.5 | 0 | 1 | -0.59 | 0.41 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 10:38 | 33.5977 | 33.5977 | -0.06 | 0.94 | -0.51 | 0.49 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 33.6992 | 33.6992 | -0.08 | 0.92 | -0.48 | 0.52 | -0.55 | 0.45 | 68.36 | 39.06
2019-09-04 | 10:38 | 33.8086 | 33.8086 | -0.09 | 0.91 | -0.48 | 0.52 | -0.54 | 0.46 | 67.38 | 40.04
2019-09-04 | 10:38 | 33.9062 | 33.9062 | 0.03 | 1.03 | -0.59 | 0.41 | -0.57 | 0.43 | 66.41 | 38.09
2019-09-04 | 10:38 | 34.0078 | 34.0078 | 0.04 | 1.04 | -0.62 | 0.38 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 34.1094 | 34.1094 | 0.06 | 1.06 | -0.62 | 0.38 | -0.58 | 0.42 | 67.38 | 37.11
2019-09-04 | 10:38 | 34.207 | 34.207 | 0.06 | 1.06 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 10:38 | 34.3164 | 34.3164 | 0.04 | 1.04 | -0.62 | 0.38 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 10:38 | 34.418 | 34.418 | 0.06 | 1.06 | -0.63 | 0.37 | -0.57 | 0.43 | 67.38 | 37.11
2019-09-04 | 10:38 | 34.5195 | 34.5195 | 0.06 | 1.06 | -0.63 | 0.37 | -0.58 | 0.42 | 68.36 | 37.11
2019-09-04 | 10:38 | 34.6172 | 34.6172 | 0.05 | 1.05 | -0.64 | 0.36 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 10:38 | 34.7266 | 34.7266 | 0.07 | 1.07 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 37.11
2019-09-04 | 10:38 | 34.8281 | 34.8281 | 0.06 | 1.06 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 10:38 | 34.9375 | 34.9375 | 0.04 | 1.04 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 37.11
2019-09-04 | 10:38 | 35.0391 | 35.0391 | -0.05 | 0.95 | -0.52 | 0.48 | -0.57 | 0.43 | 68.36 | 36.13
2019-09-04 | 10:38 | 35.1367 | 35.1367 | -0.09 | 0.91 | -0.48 | 0.52 | -0.56 | 0.44 | 66.41 | 36.13
2019-09-04 | 10:38 | 35.2383 | 35.2383 | -0.09 | 0.91 | -0.48 | 0.52 | -0.57 | 0.43 | 67.38 | 37.11
2019-09-04 | 10:38 | 35.3477 | 35.3477 | -0.12 | 0.88 | -0.46 | 0.54 | -0.56 | 0.44 | 68.36 | 36.13
2019-09-04 | 10:38 | 35.4492 | 35.4492 | 0.04 | 1.04 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 36.13
2019-09-04 | 10:38 | 35.5469 | 35.5469 | 0.04 | 1.04 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 35.16
2019-09-04 | 10:38 | 35.6484 | 35.6484 | 0.05 | 1.05 | -0.64 | 0.36 | -0.6 | 0.4 | 67.38 | 36.13
2019-09-04 | 10:38 | 35.7578 | 35.7578 | 0.05 | 1.05 | -0.65 | 0.35 | -0.61 | 0.39 | 67.38 | 35.16
2019-09-04 | 10:38 | 35.8594 | 35.8594 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 66.41 | 36.13
2019-09-04 | 10:38 | 35.957 | 35.957 | 0.06 | 1.06 | -0.67 | 0.33 | -0.62 | 0.38 | 67.38 | 37.11
2019-09-04 | 10:38 | 36.0664 | 36.0664 | 0.06 | 1.06 | -0.66 | 0.34 | -0.62 | 0.38 | 68.36 | 36.13
2019-09-04 | 10:38 | 36.168 | 36.168 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 66.41 | 35.16
2019-09-04 | 10:38 | 36.2695 | 36.2695 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 67.38 | 36.13
2019-09-04 | 10:38 | 36.3672 | 36.3672 | 0.07 | 1.07 | -0.67 | 0.33 | -0.62 | 0.38 | 69.34 | 36.13
2019-09-04 | 10:38 | 36.4766 | 36.4766 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 67.38 | 36.13
2019-09-04 | 10:38 | 36.5781 | 36.5781 | -0.06 | 0.94 | -0.55 | 0.45 | -0.61 | 0.39 | 68.36 | 36.13
2019-09-04 | 10:38 | 36.6797 | 36.6797 | -0.07 | 0.93 | -0.52 | 0.48 | -0.6 | 0.4 | 67.38 | 35.16
2019-09-04 | 10:38 | 36.7891 | 36.7891 | -0.11 | 0.89 | -0.52 | 0.48 | -0.6 | 0.4 | 67.38 | 36.13
2019-09-04 | 10:38 | 36.8867 | 36.8867 | -0.04 | 0.96 | -0.55 | 0.45 | -0.59 | 0.41 | 67.38 | 34.18
2019-09-04 | 10:38 | 36.9883 | 36.9883 | 0.02 | 1.02 | -0.66 | 0.34 | -0.61 | 0.39 | 66.41 | 34.18
2019-09-04 | 10:38 | 37.0898 | 37.0898 | 0.04 | 1.04 | -0.66 | 0.34 | -0.62 | 0.38 | 66.41 | 35.16
2019-09-04 | 10:38 | 37.1992 | 37.1992 | 0.05 | 1.05 | -0.67 | 0.33 | -0.63 | 0.37 | 67.38 | 36.13
2019-09-04 | 10:38 | 37.2969 | 37.2969 | 0.05 | 1.05 | -0.66 | 0.34 | -0.62 | 0.38 | 67.38 | 33.2
2019-09-04 | 10:38 | 37.3984 | 37.3984 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 67.38 | 34.18
2019-09-04 | 10:38 | 37.5 | 37.5 | 0.07 | 1.07 | -0.67 | 0.33 | -0.64 | 0.36 | 67.38 | 34.18
2019-09-04 | 10:38 | 37.6094 | 37.6094 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 66.41 | 36.13
2019-09-04 | 10:38 | 37.707 | 37.707 | 0.07 | 1.07 | -0.68 | 0.32 | -0.64 | 0.36 | 67.38 | 34.18
2019-09-04 | 10:38 | 37.8086 | 37.8086 | 0.06 | 1.06 | -0.69 | 0.31 | -0.64 | 0.36 | 66.41 | 34.18
2019-09-04 | 10:38 | 37.9062 | 37.9062 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 33.2
2019-09-04 | 10:38 | 38.0195 | 38.0195 | 0.02 | 1.02 | -0.63 | 0.37 | -0.64 | 0.36 | 67.38 | 34.18
2019-09-04 | 10:38 | 38.1172 | 38.1172 | -0.08 | 0.92 | -0.54 | 0.46 | -0.62 | 0.38 | 67.38 | 36.13
2019-09-04 | 10:38 | 38.2266 | 38.2266 | -0.08 | 0.92 | -0.53 | 0.47 | -0.61 | 0.39 | 67.38 | 34.18
2019-09-04 | 10:38 | 38.3281 | 38.3281 | -0.11 | 0.89 | -0.52 | 0.48 | -0.6 | 0.4 | 67.38 | 34.18
2019-09-04 | 10:38 | 38.4297 | 38.4297 | 0.03 | 1.03 | -0.64 | 0.36 | -0.62 | 0.38 | 67.38 | 35.16
2019-09-04 | 10:38 | 38.5273 | 38.5273 | 0.04 | 1.04 | -0.66 | 0.34 | -0.62 | 0.38 | 68.36 | 34.18
2019-09-04 | 10:38 | 38.6367 | 38.6367 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 67.38 | 33.2
2019-09-04 | 10:38 | 38.7383 | 38.7383 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 68.36 | 35.16
2019-09-04 | 10:38 | 38.8398 | 38.8398 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 67.38 | 34.18
2019-09-04 | 10:38 | 38.9375 | 38.9375 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 67.38 | 35.16
2019-09-04 | 10:38 | 39.0391 | 39.0391 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 33.2
2019-09-04 | 10:38 | 39.1484 | 39.1484 | 0.06 | 1.06 | -0.69 | 0.31 | -0.64 | 0.36 | 67.38 | 33.2
2019-09-04 | 10:38 | 39.25 | 39.25 | 0.07 | 1.07 | -0.69 | 0.31 | -0.64 | 0.36 | 67.38 | 32.23
2019-09-04 | 10:38 | 39.3477 | 39.3477 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 67.38 | 32.23
2019-09-04 | 10:38 | 39.4492 | 39.4492 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 67.38 | 33.2
2019-09-04 | 10:38 | 39.5586 | 39.5586 | -0.05 | 0.95 | -0.58 | 0.42 | -0.63 | 0.37 | 67.38 | 33.2
2019-09-04 | 10:38 | 39.6562 | 39.6562 | -0.07 | 0.93 | -0.55 | 0.45 | -0.62 | 0.38 | 67.38 | 34.18
2019-09-04 | 10:38 | 39.7695 | 39.7695 | -0.11 | 0.89 | -0.53 | 0.47 | -0.62 | 0.38 | 67.38 | 33.2
2019-09-04 | 10:38 | 39.8672 | 39.8672 | -0.11 | 0.89 | -0.49 | 0.51 | -0.6 | 0.4 | 68.36 | 32.23
2019-09-04 | 10:38 | 39.9688 | 39.9688 | 0.06 | 1.06 | -0.66 | 0.34 | -0.61 | 0.39 | 67.38 | 33.2
2019-09-04 | 10:38 | 40.0664 | 40.0664 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 67.38 | 33.2
2019-09-04 | 10:38 | 40.1797 | 40.1797 | 0.05 | 1.05 | -0.66 | 0.34 | -0.63 | 0.37 | 68.36 | 32.23
2019-09-04 | 10:38 | 40.2773 | 40.2773 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 68.36 | 32.23
2019-09-04 | 10:38 | 40.3789 | 40.3789 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 68.36 | 33.2
2019-09-04 | 10:38 | 40.4766 | 40.4766 | 0.06 | 1.06 | -0.67 | 0.33 | -0.64 | 0.36 | 69.34 | 32.23
2019-09-04 | 10:38 | 40.5781 | 40.5781 | 0.07 | 1.07 | -0.68 | 0.32 | -0.63 | 0.37 | 69.34 | 34.18
2019-09-04 | 10:38 | 40.6875 | 40.6875 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 67.38 | 33.2
2019-09-04 | 10:38 | 40.7891 | 40.7891 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 67.38 | 33.2
2019-09-04 | 10:38 | 40.8984 | 40.8984 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 68.36 | 32.23
2019-09-04 | 10:38 | 41 | 41 | 0.07 | 1.07 | -0.68 | 0.32 | -0.63 | 0.37 | 69.34 | 34.18
2019-09-04 | 10:38 | 41.0977 | 41.0977 | -0.06 | 0.94 | -0.56 | 0.44 | -0.63 | 0.37 | 68.36 | 35.16
2019-09-04 | 10:38 | 41.1992 | 41.1992 | -0.08 | 0.92 | -0.54 | 0.46 | -0.63 | 0.37 | 68.36 | 32.23
2019-09-04 | 10:38 | 41.3086 | 41.3086 | -0.1 | 0.9 | -0.51 | 0.49 | -0.61 | 0.39 | 70.31 | 33.2
2019-09-04 | 10:38 | 41.4062 | 41.4062 | 0.02 | 1.02 | -0.64 | 0.36 | -0.61 | 0.39 | 69.34 | 32.23
2019-09-04 | 10:38 | 41.5078 | 41.5078 | 0.03 | 1.03 | -0.67 | 0.33 | -0.63 | 0.37 | 68.36 | 32.23
2019-09-04 | 10:38 | 41.6094 | 41.6094 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 69.34 | 32.23
2019-09-04 | 10:38 | 41.7188 | 41.7188 | 0.07 | 1.07 | -0.67 | 0.33 | -0.64 | 0.36 | 68.36 | 32.23
2019-09-04 | 10:38 | 41.8164 | 41.8164 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 68.36 | 33.2
2019-09-04 | 10:38 | 41.918 | 41.918 | 0.06 | 1.06 | -0.68 | 0.32 | -0.65 | 0.35 | 69.34 | 32.23
2019-09-04 | 10:38 | 42.0273 | 42.0273 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 33.2
2019-09-04 | 10:38 | 42.1289 | 42.1289 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 68.36 | 32.23
2019-09-04 | 10:38 | 42.2266 | 42.2266 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 68.36 | 33.2
2019-09-04 | 10:38 | 42.3281 | 42.3281 | 0.05 | 1.05 | -0.7 | 0.3 | -0.66 | 0.34 | 68.36 | 32.23
2019-09-04 | 10:38 | 42.4375 | 42.4375 | 0.07 | 1.07 | -0.7 | 0.3 | -0.65 | 0.35 | 69.34 | 32.23
2019-09-04 | 10:38 | 42.5391 | 42.5391 | -0.02 | 0.98 | -0.6 | 0.4 | -0.64 | 0.36 | 69.34 | 33.2
2019-09-04 | 10:38 | 42.6367 | 42.6367 | -0.07 | 0.93 | -0.55 | 0.45 | -0.63 | 0.37 | 69.34 | 32.23
2019-09-04 | 10:38 | 42.7383 | 42.7383 | -0.12 | 0.88 | -0.52 | 0.48 | -0.62 | 0.38 | 68.36 | 33.2
2019-09-04 | 10:38 | 42.8477 | 42.8477 | -0.11 | 0.89 | -0.51 | 0.49 | -0.6 | 0.4 | 69.34 | 32.23
2019-09-04 | 10:38 | 42.9492 | 42.9492 | 0.03 | 1.03 | -0.67 | 0.33 | -0.62 | 0.38 | 69.34 | 32.23
2019-09-04 | 10:38 | 43.0469 | 43.0469 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 69.34 | 32.23
2019-09-04 | 10:38 | 43.1562 | 43.1562 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 69.34 | 34.18
2019-09-04 | 10:38 | 43.2578 | 43.2578 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 69.34 | 32.23
2019-09-04 | 10:38 | 43.3594 | 43.3594 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 31.25
2019-09-04 | 10:38 | 43.457 | 43.457 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 69.34 | 33.2
2019-09-04 | 10:38 | 43.5664 | 43.5664 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 33.2
2019-09-04 | 10:38 | 43.668 | 43.668 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 69.34 | 31.25
2019-09-04 | 10:38 | 43.7695 | 43.7695 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 32.23
2019-09-04 | 10:38 | 43.8672 | 43.8672 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 33.2
2019-09-04 | 10:38 | 43.9766 | 43.9766 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 70.31 | 31.25
2019-09-04 | 10:38 | 44.0781 | 44.0781 | -0.04 | 0.96 | -0.57 | 0.43 | -0.63 | 0.37 | 69.34 | 32.23
2019-09-04 | 10:38 | 44.1875 | 44.1875 | -0.09 | 0.91 | -0.54 | 0.46 | -0.61 | 0.39 | 70.31 | 32.23
2019-09-04 | 10:38 | 44.2891 | 44.2891 | -0.11 | 0.89 | -0.53 | 0.47 | -0.61 | 0.39 | 69.34 | 32.23
2019-09-04 | 10:38 | 44.3867 | 44.3867 | -0.11 | 0.89 | -0.53 | 0.47 | -0.61 | 0.39 | 69.34 | 31.25
2019-09-04 | 10:38 | 44.4883 | 44.4883 | 0.05 | 1.05 | -0.66 | 0.34 | -0.62 | 0.38 | 70.31 | 33.2
2019-09-04 | 10:38 | 44.5898 | 44.5898 | 0.07 | 1.07 | -0.66 | 0.34 | -0.62 | 0.38 | 70.31 | 31.25
2019-09-04 | 10:38 | 44.6992 | 44.6992 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 69.34 | 31.25
2019-09-04 | 10:38 | 44.7969 | 44.7969 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 69.34 | 31.25
2019-09-04 | 10:38 | 44.8984 | 44.8984 | 0.08 | 1.08 | -0.67 | 0.33 | -0.64 | 0.36 | 70.31 | 31.25
2019-09-04 | 10:38 | 45 | 45 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 69.34 | 31.25
2019-09-04 | 10:38 | 45.1094 | 45.1094 | 0.05 | 1.05 | -0.68 | 0.32 | -0.66 | 0.34 | 71.29 | 32.23
2019-09-04 | 10:38 | 45.207 | 45.207 | 0.04 | 1.04 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 31.25
2019-09-04 | 10:38 | 45.3086 | 45.3086 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 32.23
2019-09-04 | 10:38 | 45.4062 | 45.4062 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 71.29 | 32.23
2019-09-04 | 10:38 | 45.5195 | 45.5195 | 0.01 | 1.01 | -0.65 | 0.35 | -0.64 | 0.36 | 71.29 | 31.25
2019-09-04 | 10:38 | 45.6172 | 45.6172 | -0.08 | 0.92 | -0.56 | 0.44 | -0.61 | 0.39 | 72.27 | 31.25
2019-09-04 | 10:38 | 45.7266 | 45.7266 | -0.08 | 0.92 | -0.54 | 0.46 | -0.61 | 0.39 | 70.31 | 31.25
2019-09-04 | 10:38 | 45.8281 | 45.8281 | -0.11 | 0.89 | -0.52 | 0.48 | -0.61 | 0.39 | 71.29 | 31.25
2019-09-04 | 10:38 | 45.9297 | 45.9297 | 0.04 | 1.04 | -0.64 | 0.36 | -0.61 | 0.39 | 70.31 | 31.25
2019-09-04 | 10:38 | 46.0273 | 46.0273 | 0.03 | 1.03 | -0.67 | 0.33 | -0.63 | 0.37 | 69.34 | 31.25
2019-09-04 | 10:38 | 46.1367 | 46.1367 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 70.31 | 30.27
2019-09-04 | 10:38 | 46.2383 | 46.2383 | 0.06 | 1.06 | -0.67 | 0.33 | -0.64 | 0.36 | 70.31 | 31.25
2019-09-04 | 10:38 | 46.3398 | 46.3398 | 0.07 | 1.07 | -0.68 | 0.32 | -0.63 | 0.37 | 71.29 | 31.25
2019-09-04 | 10:38 | 46.4375 | 46.4375 | 0.07 | 1.07 | -0.67 | 0.33 | -0.63 | 0.37 | 70.31 | 32.23
2019-09-04 | 10:38 | 46.5391 | 46.5391 | 0.06 | 1.06 | -0.67 | 0.33 | -0.64 | 0.36 | 70.31 | 31.25
2019-09-04 | 10:38 | 46.6484 | 46.6484 | 0.05 | 1.05 | -0.69 | 0.31 | -0.64 | 0.36 | 70.31 | 32.23
2019-09-04 | 10:38 | 46.75 | 46.75 | 0.04 | 1.04 | -0.68 | 0.32 | -0.64 | 0.36 | 71.29 | 31.25
2019-09-04 | 10:38 | 46.8594 | 46.8594 | 0.04 | 1.04 | -0.69 | 0.31 | -0.65 | 0.35 | 71.29 | 31.25
2019-09-04 | 10:38 | 46.957 | 46.957 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 70.31 | 31.25
2019-09-04 | 10:38 | 47.0586 | 47.0586 | -0.03 | 0.97 | -0.6 | 0.4 | -0.63 | 0.37 | 70.31 | 30.27
2019-09-04 | 10:38 | 47.1562 | 47.1562 | -0.09 | 0.91 | -0.55 | 0.45 | -0.62 | 0.38 | 72.27 | 31.25
2019-09-04 | 10:38 | 47.2695 | 47.2695 | -0.09 | 0.91 | -0.53 | 0.47 | -0.61 | 0.39 | 71.29 | 31.25
2019-09-04 | 10:38 | 47.3672 | 47.3672 | -0.11 | 0.89 | -0.51 | 0.49 | -0.6 | 0.4 | 71.29 | 32.23
2019-09-04 | 10:38 | 47.4688 | 47.4688 | 0.04 | 1.04 | -0.65 | 0.35 | -0.6 | 0.4 | 71.29 | 30.27
2019-09-04 | 10:38 | 47.5664 | 47.5664 | 0.03 | 1.03 | -0.67 | 0.33 | -0.63 | 0.37 | 70.31 | 30.27
2019-09-04 | 10:38 | 47.6797 | 47.6797 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 72.27 | 31.25
2019-09-04 | 10:38 | 47.7773 | 47.7773 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 71.29 | 31.25
2019-09-04 | 10:38 | 47.8789 | 47.8789 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 71.29 | 32.23
2019-09-04 | 10:38 | 47.9883 | 47.9883 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 71.29 | 31.25
2019-09-04 | 10:38 | 48.0898 | 48.0898 | 0.07 | 1.07 | -0.67 | 0.33 | -0.63 | 0.37 | 71.29 | 30.27
2019-09-04 | 10:38 | 48.1875 | 48.1875 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 71.29 | 31.25
2019-09-04 | 10:38 | 48.2891 | 48.2891 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 70.31 | 30.27
2019-09-04 | 10:38 | 48.3984 | 48.3984 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 31.25
2019-09-04 | 10:38 | 48.5 | 48.5 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 72.27 | 30.27
2019-09-04 | 10:38 | 48.5977 | 48.5977 | -0.08 | 0.92 | -0.58 | 0.42 | -0.62 | 0.38 | 72.27 | 32.23
2019-09-04 | 10:38 | 48.707 | 48.707 | -0.09 | 0.91 | -0.55 | 0.45 | -0.62 | 0.38 | 71.29 | 31.25
2019-09-04 | 10:38 | 48.8086 | 48.8086 | -0.12 | 0.88 | -0.53 | 0.47 | -0.6 | 0.4 | 72.27 | 30.27
2019-09-04 | 10:38 | 48.9062 | 48.9062 | 0 | 1 | -0.62 | 0.38 | -0.59 | 0.41 | 70.31 | 30.27
2019-09-04 | 10:38 | 49.0078 | 49.0078 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 71.29 | 31.25
2019-09-04 | 10:38 | 49.1172 | 49.1172 | 0.04 | 1.04 | -0.67 | 0.33 | -0.61 | 0.39 | 72.27 | 31.25
2019-09-04 | 10:38 | 49.2188 | 49.2188 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 72.27 | 31.25
2019-09-04 | 10:38 | 49.3164 | 49.3164 | 0.07 | 1.07 | -0.66 | 0.34 | -0.62 | 0.38 | 72.27 | 32.23
2019-09-04 | 10:38 | 49.418 | 49.418 | 0.05 | 1.05 | -0.67 | 0.33 | -0.63 | 0.37 | 71.29 | 32.23
2019-09-04 | 10:38 | 49.5273 | 49.5273 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 72.27 | 31.25
2019-09-04 | 10:38 | 49.6289 | 49.6289 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 71.29 | 31.25
2019-09-04 | 10:38 | 49.7266 | 49.7266 | 0.05 | 1.05 | -0.67 | 0.33 | -0.64 | 0.36 | 71.29 | 32.23
2019-09-04 | 10:38 | 49.8281 | 49.8281 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 32.23
2019-09-04 | 10:38 | 49.9375 | 49.9375 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 71.29 | 30.27
2019-09-04 | 10:38 | 50.0391 | 50.0391 | 0.01 | 1.01 | -0.63 | 0.37 | -0.63 | 0.37 | 72.27 | 31.25
2019-09-04 | 10:38 | 50.1484 | 50.1484 | -0.08 | 0.92 | -0.56 | 0.44 | -0.62 | 0.38 | 72.27 | 30.27
2019-09-04 | 10:38 | 50.25 | 50.25 | -0.08 | 0.92 | -0.54 | 0.46 | -0.61 | 0.39 | 72.27 | 30.27
2019-09-04 | 10:38 | 50.3477 | 50.3477 | -0.12 | 0.88 | -0.51 | 0.49 | -0.6 | 0.4 | 72.27 | 32.23
2019-09-04 | 10:38 | 50.4492 | 50.4492 | 0.03 | 1.03 | -0.65 | 0.35 | -0.61 | 0.39 | 72.27 | 30.27
2019-09-04 | 10:38 | 50.5469 | 50.5469 | 0.04 | 1.04 | -0.68 | 0.32 | -0.61 | 0.39 | 72.27 | 31.25
2019-09-04 | 10:38 | 50.6562 | 50.6562 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 72.27 | 29.3
2019-09-04 | 10:38 | 50.7578 | 50.7578 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 72.27 | 30.27
2019-09-04 | 10:38 | 50.8594 | 50.8594 | 0.06 | 1.06 | -0.67 | 0.33 | -0.63 | 0.37 | 72.27 | 31.25
2019-09-04 | 10:38 | 50.957 | 50.957 | 0.08 | 1.08 | -0.66 | 0.34 | -0.63 | 0.37 | 72.27 | 30.27
2019-09-04 | 10:38 | 51.0664 | 51.0664 | 0.05 | 1.05 | -0.69 | 0.31 | -0.64 | 0.36 | 72.27 | 30.27
2019-09-04 | 10:38 | 51.168 | 51.168 | 0.08 | 1.08 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 31.25
2019-09-04 | 10:38 | 51.2695 | 51.2695 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 73.24 | 31.25
2019-09-04 | 10:38 | 51.3789 | 51.3789 | 0.03 | 1.03 | -0.68 | 0.32 | -0.63 | 0.37 | 73.24 | 32.23
2019-09-04 | 10:38 | 51.4766 | 51.4766 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 72.27 | 31.25
2019-09-04 | 10:38 | 51.5781 | 51.5781 | -0.03 | 0.97 | -0.58 | 0.42 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 51.6797 | 51.6797 | -0.07 | 0.93 | -0.56 | 0.44 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 51.7891 | 51.7891 | -0.1 | 0.9 | -0.55 | 0.45 | -0.61 | 0.39 | 72.27 | 30.27
2019-09-04 | 10:38 | 51.8867 | 51.8867 | -0.11 | 0.89 | -0.52 | 0.48 | -0.61 | 0.39 | 73.24 | 31.25
2019-09-04 | 10:38 | 51.9883 | 51.9883 | 0.03 | 1.03 | -0.67 | 0.33 | -0.62 | 0.38 | 72.27 | 30.27
2019-09-04 | 10:38 | 52.0898 | 52.0898 | 0.04 | 1.04 | -0.66 | 0.34 | -0.62 | 0.38 | 74.22 | 31.25
2019-09-04 | 10:38 | 52.1992 | 52.1992 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 74.22 | 29.3
2019-09-04 | 10:38 | 52.2969 | 52.2969 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 72.27 | 29.3
2019-09-04 | 10:38 | 52.3984 | 52.3984 | 0.06 | 1.06 | -0.67 | 0.33 | -0.63 | 0.37 | 73.24 | 31.25
2019-09-04 | 10:38 | 52.5 | 52.5 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 52.6094 | 52.6094 | 0.05 | 1.05 | -0.69 | 0.31 | -0.64 | 0.36 | 73.24 | 30.27
2019-09-04 | 10:38 | 52.707 | 52.707 | 0.07 | 1.07 | -0.67 | 0.33 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 52.8164 | 52.8164 | 0.07 | 1.07 | -0.69 | 0.31 | -0.64 | 0.36 | 73.24 | 30.27
2019-09-04 | 10:38 | 52.918 | 52.918 | 0.05 | 1.05 | -0.67 | 0.33 | -0.63 | 0.37 | 72.27 | 29.3
2019-09-04 | 10:38 | 53.0195 | 53.0195 | 0.01 | 1.01 | -0.64 | 0.36 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 10:38 | 53.1172 | 53.1172 | -0.06 | 0.94 | -0.56 | 0.44 | -0.62 | 0.38 | 73.24 | 31.25
2019-09-04 | 10:38 | 53.2266 | 53.2266 | -0.09 | 0.91 | -0.52 | 0.48 | -0.62 | 0.38 | 73.24 | 29.3
2019-09-04 | 10:38 | 53.3281 | 53.3281 | -0.12 | 0.88 | -0.52 | 0.48 | -0.61 | 0.39 | 74.22 | 29.3
2019-09-04 | 10:38 | 53.4297 | 53.4297 | 0.02 | 1.02 | -0.65 | 0.35 | -0.61 | 0.39 | 72.27 | 29.3
2019-09-04 | 10:38 | 53.5273 | 53.5273 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 74.22 | 30.27
2019-09-04 | 10:38 | 53.6367 | 53.6367 | 0.05 | 1.05 | -0.66 | 0.34 | -0.61 | 0.39 | 74.22 | 29.3
2019-09-04 | 10:38 | 53.7383 | 53.7383 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 53.8398 | 53.8398 | 0.05 | 1.05 | -0.66 | 0.34 | -0.63 | 0.37 | 73.24 | 31.25
2019-09-04 | 10:38 | 53.9492 | 53.9492 | 0.06 | 1.06 | -0.67 | 0.33 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 54.0469 | 54.0469 | 0.05 | 1.05 | -0.68 | 0.32 | -0.62 | 0.38 | 74.22 | 31.25
2019-09-04 | 10:38 | 54.1484 | 54.1484 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 54.25 | 54.25 | 0.04 | 1.04 | -0.67 | 0.33 | -0.64 | 0.36 | 73.24 | 31.25
2019-09-04 | 10:38 | 54.3594 | 54.3594 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 54.457 | 54.457 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 73.24 | 31.25
2019-09-04 | 10:38 | 54.5586 | 54.5586 | -0.01 | 0.99 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 31.25
2019-09-04 | 10:38 | 54.668 | 54.668 | -0.1 | 0.9 | -0.57 | 0.43 | -0.61 | 0.39 | 73.24 | 29.3
2019-09-04 | 10:38 | 54.7695 | 54.7695 | -0.08 | 0.92 | -0.55 | 0.45 | -0.63 | 0.37 | 73.24 | 31.25
2019-09-04 | 10:38 | 54.8672 | 54.8672 | -0.1 | 0.9 | -0.52 | 0.48 | -0.6 | 0.4 | 73.24 | 29.3
2019-09-04 | 10:38 | 54.9688 | 54.9688 | 0.04 | 1.04 | -0.65 | 0.35 | -0.61 | 0.39 | 73.24 | 29.3
2019-09-04 | 10:38 | 55.0781 | 55.0781 | 0.03 | 1.03 | -0.67 | 0.33 | -0.61 | 0.39 | 73.24 | 30.27
2019-09-04 | 10:38 | 55.1797 | 55.1797 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 74.22 | 30.27
2019-09-04 | 10:38 | 55.2773 | 55.2773 | 0.06 | 1.06 | -0.66 | 0.34 | -0.61 | 0.39 | 75.2 | 29.3
2019-09-04 | 10:38 | 55.3789 | 55.3789 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 73.24 | 29.3
2019-09-04 | 10:38 | 55.4883 | 55.4883 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 74.22 | 30.27
2019-09-04 | 10:38 | 55.5898 | 55.5898 | 0.07 | 1.07 | -0.68 | 0.32 | -0.63 | 0.37 | 73.24 | 30.27
2019-09-04 | 10:38 | 55.6875 | 55.6875 | 0.04 | 1.04 | -0.67 | 0.33 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 10:38 | 55.7891 | 55.7891 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 55.8984 | 55.8984 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 73.24 | 29.3
2019-09-04 | 10:38 | 56 | 56 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 75.2 | 30.27
2019-09-04 | 10:38 | 56.0977 | 56.0977 | -0.06 | 0.94 | -0.58 | 0.42 | -0.62 | 0.38 | 74.22 | 30.27
2019-09-04 | 10:38 | 56.207 | 56.207 | -0.09 | 0.91 | -0.54 | 0.46 | -0.6 | 0.4 | 73.24 | 29.3
2019-09-04 | 10:38 | 56.3086 | 56.3086 | -0.11 | 0.89 | -0.54 | 0.46 | -0.61 | 0.39 | 73.24 | 29.3
2019-09-04 | 10:38 | 56.4062 | 56.4062 | -0.03 | 0.97 | -0.63 | 0.37 | -0.6 | 0.4 | 74.22 | 30.27
2019-09-04 | 10:38 | 56.5078 | 56.5078 | 0.03 | 1.03 | -0.66 | 0.34 | -0.62 | 0.38 | 73.24 | 29.3
2019-09-04 | 10:38 | 56.6172 | 56.6172 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 73.24 | 30.27
2019-09-04 | 10:38 | 56.7188 | 56.7188 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 74.22 | 30.27
2019-09-04 | 10:38 | 56.8164 | 56.8164 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 74.22 | 28.32
2019-09-04 | 10:38 | 56.918 | 56.918 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 73.24 | 29.3
2019-09-04 | 10:38 | 57.0273 | 57.0273 | 0.06 | 1.06 | -0.67 | 0.33 | -0.63 | 0.37 | 73.24 | 29.3
2019-09-04 | 10:38 | 57.1289 | 57.1289 | 0.06 | 1.06 | -0.69 | 0.31 | -0.63 | 0.37 | 74.22 | 30.27
2019-09-04 | 10:38 | 57.2266 | 57.2266 | 0.06 | 1.06 | -0.67 | 0.33 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 57.3281 | 57.3281 | 0.07 | 1.07 | -0.69 | 0.31 | -0.65 | 0.35 | 74.22 | 29.3
2019-09-04 | 10:38 | 57.4375 | 57.4375 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 74.22 | 29.3
2019-09-04 | 10:38 | 57.5391 | 57.5391 | 0.01 | 1.01 | -0.64 | 0.36 | -0.63 | 0.37 | 74.22 | 30.27
2019-09-04 | 10:38 | 57.6367 | 57.6367 | -0.05 | 0.95 | -0.56 | 0.44 | -0.62 | 0.38 | 74.22 | 30.27
2019-09-04 | 10:38 | 57.75 | 57.75 | -0.1 | 0.9 | -0.53 | 0.47 | -0.62 | 0.38 | 74.22 | 29.3
2019-09-04 | 10:38 | 57.8477 | 57.8477 | -0.11 | 0.89 | -0.53 | 0.47 | -0.6 | 0.4 | 74.22 | 28.32
2019-09-04 | 10:38 | 57.9492 | 57.9492 | 0.02 | 1.02 | -0.65 | 0.35 | -0.62 | 0.38 | 73.24 | 29.3
2019-09-04 | 10:38 | 58.0586 | 58.0586 | 0.03 | 1.03 | -0.66 | 0.34 | -0.61 | 0.39 | 73.24 | 27.34
2019-09-04 | 10:38 | 58.1562 | 58.1562 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 73.24 | 29.3
2019-09-04 | 10:38 | 58.2578 | 58.2578 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 58.3672 | 58.3672 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 29.3
2019-09-04 | 10:38 | 58.457 | 58.457 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 58.5664 | 58.5664 | 0.05 | 1.05 | -0.67 | 0.33 | -0.63 | 0.37 | 73.24 | 29.3
2019-09-04 | 10:38 | 58.668 | 58.668 | 0.06 | 1.06 | -0.69 | 0.31 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 58.7773 | 58.7773 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 58.8789 | 58.8789 | 0.04 | 1.04 | -0.7 | 0.3 | -0.65 | 0.35 | 74.22 | 29.3
2019-09-04 | 10:38 | 58.9766 | 58.9766 | 0.09 | 1.09 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 59.0781 | 59.0781 | -0.06 | 0.94 | -0.58 | 0.42 | -0.62 | 0.38 | 74.22 | 29.3
2019-09-04 | 10:38 | 59.1875 | 59.1875 | -0.08 | 0.92 | -0.57 | 0.43 | -0.62 | 0.38 | 74.22 | 29.3
2019-09-04 | 10:38 | 59.2891 | 59.2891 | -0.12 | 0.88 | -0.53 | 0.47 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 59.3867 | 59.3867 | -0.14 | 0.86 | -0.51 | 0.49 | -0.6 | 0.4 | 74.22 | 30.27
2019-09-04 | 10:38 | 59.4883 | 59.4883 | 0.04 | 1.04 | -0.65 | 0.35 | -0.61 | 0.39 | 74.22 | 28.32
2019-09-04 | 10:38 | 59.5898 | 59.5898 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 74.22 | 28.32
2019-09-04 | 10:38 | 59.6992 | 59.6992 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 59.7969 | 59.7969 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 59.9062 | 59.9062 | 0.06 | 1.06 | -0.66 | 0.34 | -0.62 | 0.38 | 74.22 | 29.3
2019-09-04 | 10:38 | 60.0078 | 60.0078 | 0.06 | 1.06 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 60.1094 | 60.1094 | 0.05 | 1.05 | -0.67 | 0.33 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 60.207 | 60.207 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 60.3164 | 60.3164 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 60.418 | 60.418 | 0.06 | 1.06 | -0.69 | 0.31 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 60.5195 | 60.5195 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 76.17 | 29.3
2019-09-04 | 10:38 | 60.6172 | 60.6172 | -0.06 | 0.94 | -0.58 | 0.42 | -0.61 | 0.39 | 74.22 | 28.32
2019-09-04 | 10:38 | 60.7266 | 60.7266 | -0.1 | 0.9 | -0.54 | 0.46 | -0.61 | 0.39 | 73.24 | 28.32
2019-09-04 | 10:38 | 60.8281 | 60.8281 | -0.12 | 0.88 | -0.54 | 0.46 | -0.62 | 0.38 | 73.24 | 28.32
2019-09-04 | 10:38 | 60.9297 | 60.9297 | 0.01 | 1.01 | -0.64 | 0.36 | -0.61 | 0.39 | 74.22 | 29.3
2019-09-04 | 10:38 | 61.0391 | 61.0391 | 0.06 | 1.06 | -0.66 | 0.34 | -0.62 | 0.38 | 74.22 | 28.32
2019-09-04 | 10:38 | 61.1367 | 61.1367 | 0.05 | 1.05 | -0.67 | 0.33 | -0.61 | 0.39 | 75.2 | 29.3
2019-09-04 | 10:38 | 61.2383 | 61.2383 | 0.04 | 1.04 | -0.66 | 0.34 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 61.3398 | 61.3398 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 74.22 | 27.34
2019-09-04 | 10:38 | 61.4492 | 61.4492 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 61.5469 | 61.5469 | 0.07 | 1.07 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 61.6484 | 61.6484 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 61.75 | 61.75 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 61.8594 | 61.8594 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 61.957 | 61.957 | 0.04 | 1.04 | -0.7 | 0.3 | -0.64 | 0.36 | 74.22 | 28.32
2019-09-04 | 10:38 | 62.0586 | 62.0586 | -0.02 | 0.98 | -0.63 | 0.37 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 62.168 | 62.168 | -0.07 | 0.93 | -0.57 | 0.43 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 62.2695 | 62.2695 | -0.1 | 0.9 | -0.54 | 0.46 | -0.6 | 0.4 | 75.2 | 30.27
2019-09-04 | 10:38 | 62.3672 | 62.3672 | -0.13 | 0.87 | -0.52 | 0.48 | -0.59 | 0.41 | 75.2 | 28.32
2019-09-04 | 10:38 | 62.4688 | 62.4688 | 0.03 | 1.03 | -0.66 | 0.34 | -0.61 | 0.39 | 74.22 | 28.32
2019-09-04 | 10:38 | 62.5781 | 62.5781 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 62.6797 | 62.6797 | 0.04 | 1.04 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 62.7773 | 62.7773 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 29.3
2019-09-04 | 10:38 | 62.8789 | 62.8789 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 74.22 | 27.34
2019-09-04 | 10:38 | 62.9883 | 62.9883 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 74.22 | 28.32
2019-09-04 | 10:38 | 63.0898 | 63.0898 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 29.3
2019-09-04 | 10:38 | 63.1875 | 63.1875 | 0.06 | 1.06 | -0.68 | 0.32 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 63.2891 | 63.2891 | 0.05 | 1.05 | -0.7 | 0.3 | -0.64 | 0.36 | 74.22 | 28.32
2019-09-04 | 10:38 | 63.3984 | 63.3984 | 0.06 | 1.06 | -0.69 | 0.31 | -0.71 | 0.29 | 74.22 | 28.32
2019-09-04 | 10:38 | 63.5 | 63.5 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 74.22 | 29.3
2019-09-04 | 10:38 | 63.5977 | 63.5977 | -0.08 | 0.92 | -0.6 | 0.4 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 63.707 | 63.707 | -0.1 | 0.9 | -0.57 | 0.43 | -0.61 | 0.39 | 74.22 | 28.32
2019-09-04 | 10:38 | 63.8086 | 63.8086 | -0.1 | 0.9 | -0.54 | 0.46 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:38 | 63.9062 | 63.9062 | -0.03 | 0.97 | -0.59 | 0.41 | -0.61 | 0.39 | 73.24 | 27.34
2019-09-04 | 10:38 | 64.0078 | 64.0078 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 64.1172 | 64.1172 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 64.2188 | 64.2188 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 64.3164 | 64.3164 | 0.05 | 1.05 | -0.66 | 0.34 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 64.418 | 64.418 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 64.5273 | 64.5273 | 0.06 | 1.06 | -0.68 | 0.32 | -0.62 | 0.38 | 76.17 | 29.3
2019-09-04 | 10:38 | 64.6289 | 64.6289 | 0.06 | 1.06 | -0.68 | 0.32 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 64.7383 | 64.7383 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 64.8398 | 64.8398 | 0.06 | 1.06 | -0.69 | 0.31 | -0.64 | 0.36 | 76.17 | 29.3
2019-09-04 | 10:38 | 64.9375 | 64.9375 | 0.07 | 1.07 | -0.69 | 0.31 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 65.0391 | 65.0391 | 0 | 1 | -0.63 | 0.37 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 65.1484 | 65.1484 | -0.08 | 0.92 | -0.56 | 0.44 | -0.63 | 0.37 | 74.22 | 29.3
2019-09-04 | 10:38 | 65.25 | 65.25 | -0.09 | 0.91 | -0.57 | 0.43 | -0.61 | 0.39 | 74.22 | 27.34
2019-09-04 | 10:38 | 65.3477 | 65.3477 | -0.11 | 0.89 | -0.54 | 0.46 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 65.4492 | 65.4492 | 0.03 | 1.03 | -0.66 | 0.34 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 65.5586 | 65.5586 | 0.05 | 1.05 | -0.67 | 0.33 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 65.6562 | 65.6562 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 65.7578 | 65.7578 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 74.22 | 27.34
2019-09-04 | 10:38 | 65.8672 | 65.8672 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 65.9688 | 65.9688 | 0.06 | 1.06 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 66.0664 | 66.0664 | 0.06 | 1.06 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 66.168 | 66.168 | 0.07 | 1.07 | -0.69 | 0.31 | -0.64 | 0.36 | 74.22 | 27.34
2019-09-04 | 10:38 | 66.2773 | 66.2773 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 66.3789 | 66.3789 | 0.06 | 1.06 | -0.69 | 0.31 | -0.63 | 0.37 | 76.17 | 29.3
2019-09-04 | 10:38 | 66.4766 | 66.4766 | 0.05 | 1.05 | -0.7 | 0.3 | -0.65 | 0.35 | 76.17 | 27.34
2019-09-04 | 10:38 | 66.5781 | 66.5781 | -0.05 | 0.95 | -0.61 | 0.39 | -0.62 | 0.38 | 76.17 | 29.3
2019-09-04 | 10:38 | 66.6875 | 66.6875 | -0.08 | 0.92 | -0.56 | 0.44 | -0.6 | 0.4 | 76.17 | 28.32
2019-09-04 | 10:38 | 66.7891 | 66.7891 | -0.09 | 0.91 | -0.56 | 0.44 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 66.8867 | 66.8867 | -0.14 | 0.86 | -0.52 | 0.48 | -0.59 | 0.41 | 76.17 | 29.3
2019-09-04 | 10:38 | 67 | 67 | 0.03 | 1.03 | -0.66 | 0.34 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:38 | 67.0977 | 67.0977 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 67.1992 | 67.1992 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 67.2969 | 67.2969 | 0.02 | 1.02 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 67.4062 | 67.4062 | 0.06 | 1.06 | -0.69 | 0.31 | -0.62 | 0.38 | 76.17 | 29.3
2019-09-04 | 10:38 | 67.5078 | 67.5078 | 0.04 | 1.04 | -0.68 | 0.32 | -0.64 | 0.36 | 74.22 | 26.37
2019-09-04 | 10:38 | 67.6094 | 67.6094 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:38 | 67.707 | 67.707 | 0.06 | 1.06 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 67.8164 | 67.8164 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 67.918 | 67.918 | 0.07 | 1.07 | -0.7 | 0.3 | -0.64 | 0.36 | 74.22 | 28.32
2019-09-04 | 10:38 | 68.0273 | 68.0273 | 0 | 1 | -0.65 | 0.35 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 68.1289 | 68.1289 | -0.07 | 0.93 | -0.59 | 0.41 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:38 | 68.2266 | 68.2266 | -0.12 | 0.88 | -0.55 | 0.45 | -0.6 | 0.4 | 74.22 | 28.32
2019-09-04 | 10:38 | 68.3281 | 68.3281 | -0.13 | 0.87 | -0.54 | 0.46 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 68.4297 | 68.4297 | 0.01 | 1.01 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 68.5391 | 68.5391 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 76.17 | 29.3
2019-09-04 | 10:38 | 68.6367 | 68.6367 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 68.7383 | 68.7383 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 68.8398 | 68.8398 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 68.9492 | 68.9492 | 0.05 | 1.05 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 69.0469 | 69.0469 | 0.07 | 1.07 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 69.1484 | 69.1484 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 74.22 | 27.34
2019-09-04 | 10:38 | 69.25 | 69.25 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 69.3594 | 69.3594 | 0.07 | 1.07 | -0.69 | 0.31 | -0.63 | 0.37 | 74.22 | 26.37
2019-09-04 | 10:38 | 69.457 | 69.457 | 0.06 | 1.06 | -0.71 | 0.29 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 69.5664 | 69.5664 | -0.03 | 0.97 | -0.62 | 0.38 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 69.668 | 69.668 | -0.07 | 0.93 | -0.58 | 0.42 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:38 | 69.7695 | 69.7695 | -0.08 | 0.92 | -0.56 | 0.44 | -0.6 | 0.4 | 74.22 | 27.34
2019-09-04 | 10:38 | 69.8672 | 69.8672 | -0.09 | 0.91 | -0.55 | 0.45 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:38 | 69.9688 | 69.9688 | 0.01 | 1.01 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 70.0781 | 70.0781 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 70.1797 | 70.1797 | 0.04 | 1.04 | -0.69 | 0.31 | -0.62 | 0.38 | 74.22 | 27.34
2019-09-04 | 10:38 | 70.2773 | 70.2773 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 70.3789 | 70.3789 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 70.4883 | 70.4883 | 0.06 | 1.06 | -0.7 | 0.3 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 70.5898 | 70.5898 | 0.06 | 1.06 | -0.69 | 0.31 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 70.6992 | 70.6992 | 0.06 | 1.06 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:38 | 70.7969 | 70.7969 | 0.05 | 1.05 | -0.69 | 0.31 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 70.8984 | 70.8984 | 0.06 | 1.06 | -0.69 | 0.31 | -0.64 | 0.36 | 74.22 | 28.32
2019-09-04 | 10:38 | 71 | 71 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 71.1094 | 71.1094 | -0.06 | 0.94 | -0.6 | 0.4 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 71.207 | 71.207 | -0.08 | 0.92 | -0.56 | 0.44 | -0.62 | 0.38 | 74.22 | 27.34
2019-09-04 | 10:38 | 71.3086 | 71.3086 | -0.1 | 0.9 | -0.55 | 0.45 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 71.4062 | 71.4062 | -0.07 | 0.93 | -0.59 | 0.41 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 71.5078 | 71.5078 | 0.02 | 1.02 | -0.67 | 0.33 | -0.6 | 0.4 | 74.22 | 26.37
2019-09-04 | 10:38 | 71.6172 | 71.6172 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 71.7188 | 71.7188 | 0.04 | 1.04 | -0.68 | 0.32 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 71.8281 | 71.8281 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 71.9297 | 71.9297 | 0.04 | 1.04 | -0.69 | 0.31 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 72.0273 | 72.0273 | 0.07 | 1.07 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 72.1289 | 72.1289 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 72.2383 | 72.2383 | 0.06 | 1.06 | -0.7 | 0.3 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 72.3398 | 72.3398 | 0.05 | 1.05 | -0.7 | 0.3 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:38 | 72.4375 | 72.4375 | 0.07 | 1.07 | -0.71 | 0.29 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 72.5469 | 72.5469 | -0.02 | 0.98 | -0.63 | 0.37 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 72.6484 | 72.6484 | -0.07 | 0.93 | -0.6 | 0.4 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 72.75 | 72.75 | -0.1 | 0.9 | -0.56 | 0.44 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 72.8477 | 72.8477 | -0.15 | 0.85 | -0.54 | 0.46 | -0.61 | 0.39 | 74.22 | 27.34
2019-09-04 | 10:38 | 72.9492 | 72.9492 | 0.03 | 1.03 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 73.0586 | 73.0586 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 74.22 | 27.34
2019-09-04 | 10:38 | 73.1562 | 73.1562 | 0.05 | 1.05 | -0.68 | 0.32 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 73.2578 | 73.2578 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:38 | 73.3672 | 73.3672 | 0.07 | 1.07 | -0.68 | 0.32 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 73.4688 | 73.4688 | 0.06 | 1.06 | -0.69 | 0.31 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 73.5664 | 73.5664 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 74.22 | 27.34
2019-09-04 | 10:38 | 73.668 | 73.668 | 0.05 | 1.05 | -0.69 | 0.31 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 73.7773 | 73.7773 | 0.05 | 1.05 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 73.8789 | 73.8789 | 0.05 | 1.05 | -0.7 | 0.3 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 73.9766 | 73.9766 | 0.05 | 1.05 | -0.71 | 0.29 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 74.0898 | 74.0898 | -0.04 | 0.96 | -0.62 | 0.38 | -0.63 | 0.37 | 74.22 | 27.34
2019-09-04 | 10:38 | 74.1875 | 74.1875 | -0.08 | 0.92 | -0.57 | 0.43 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 74.2891 | 74.2891 | -0.07 | 0.93 | -0.56 | 0.44 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 74.3867 | 74.3867 | -0.13 | 0.87 | -0.53 | 0.47 | -0.6 | 0.4 | 76.17 | 28.32
2019-09-04 | 10:38 | 74.5 | 74.5 | 0.03 | 1.03 | -0.68 | 0.32 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:38 | 74.5977 | 74.5977 | 0.04 | 1.04 | -0.69 | 0.31 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 74.6992 | 74.6992 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:38 | 74.7969 | 74.7969 | 0.04 | 1.04 | -0.68 | 0.32 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 74.9062 | 74.9062 | 0.06 | 1.06 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 75.0078 | 75.0078 | 0.05 | 1.05 | -0.71 | 0.29 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 75.1094 | 75.1094 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:38 | 75.207 | 75.207 | 0.06 | 1.06 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 75.3164 | 75.3164 | 0.05 | 1.05 | -0.7 | 0.3 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 75.418 | 75.418 | 0.06 | 1.06 | -0.7 | 0.3 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 75.5273 | 75.5273 | 0.02 | 1.02 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 75.6289 | 75.6289 | -0.06 | 0.94 | -0.59 | 0.41 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 75.7266 | 75.7266 | -0.08 | 0.92 | -0.57 | 0.43 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 75.8281 | 75.8281 | -0.12 | 0.88 | -0.54 | 0.46 | -0.6 | 0.4 | 75.2 | 26.37
2019-09-04 | 10:38 | 75.9297 | 75.9297 | -0.01 | 0.99 | -0.65 | 0.35 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:38 | 76.0391 | 76.0391 | 0.05 | 1.05 | -0.68 | 0.32 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 76.1367 | 76.1367 | 0.04 | 1.04 | -0.69 | 0.31 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 76.2383 | 76.2383 | 0.04 | 1.04 | -0.7 | 0.3 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 76.3398 | 76.3398 | 0.04 | 1.04 | -0.69 | 0.31 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:38 | 76.4492 | 76.4492 | 0.04 | 1.04 | -0.69 | 0.31 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 76.5469 | 76.5469 | 0.04 | 1.04 | -0.7 | 0.3 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 76.6562 | 76.6562 | 0.04 | 1.04 | -0.7 | 0.3 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 76.7578 | 76.7578 | 0.04 | 1.04 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 76.8594 | 76.8594 | 0.04 | 1.04 | -0.7 | 0.3 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:38 | 76.957 | 76.957 | 0.04 | 1.04 | -0.71 | 0.29 | -0.64 | 0.36 | 75.2 | 29.3
2019-09-04 | 10:38 | 77.0664 | 77.0664 | -0.04 | 0.96 | -0.63 | 0.37 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 77.168 | 77.168 | -0.06 | 0.94 | -0.59 | 0.41 | -0.6 | 0.4 | 75.2 | 28.32
2019-09-04 | 10:38 | 77.2695 | 77.2695 | -0.11 | 0.89 | -0.56 | 0.44 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:38 | 77.3672 | 77.3672 | -0.15 | 0.85 | -0.54 | 0.46 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:38 | 77.4688 | 77.4688 | 0.03 | 1.03 | -0.68 | 0.32 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 77.5781 | 77.5781 | 0.04 | 1.04 | -0.68 | 0.32 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 77.6797 | 77.6797 | 0.04 | 1.04 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 77.7773 | 77.7773 | 0.02 | 1.02 | -0.71 | 0.29 | -0.62 | 0.38 | 74.22 | 26.37
2019-09-04 | 10:38 | 77.8867 | 77.8867 | 0.04 | 1.04 | -0.7 | 0.3 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 77.9883 | 77.9883 | 0.05 | 1.05 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 78.0898 | 78.0898 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 78.1992 | 78.1992 | 0.04 | 1.04 | -0.71 | 0.29 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:38 | 78.2969 | 78.2969 | 0.07 | 1.07 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 78.3984 | 78.3984 | 0.05 | 1.05 | -0.7 | 0.3 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 78.5 | 78.5 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 78.6094 | 78.6094 | -0.06 | 0.94 | -0.62 | 0.38 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 78.707 | 78.707 | -0.07 | 0.93 | -0.6 | 0.4 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 78.8086 | 78.8086 | -0.12 | 0.88 | -0.56 | 0.44 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 78.918 | 78.918 | -0.13 | 0.87 | -0.55 | 0.45 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:38 | 79.0195 | 79.0195 | 0.04 | 1.04 | -0.69 | 0.31 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 79.1172 | 79.1172 | 0.04 | 1.04 | -0.69 | 0.31 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 79.2188 | 79.2188 | 0.04 | 1.04 | -0.71 | 0.29 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 79.3281 | 79.3281 | 0.06 | 1.06 | -0.7 | 0.3 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:38 | 79.4297 | 79.4297 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 79.5273 | 79.5273 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 79.6289 | 79.6289 | 0.07 | 1.07 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 79.7383 | 79.7383 | 0.05 | 1.05 | -0.71 | 0.29 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:38 | 79.8398 | 79.8398 | 0.05 | 1.05 | -0.72 | 0.28 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 79.9375 | 79.9375 | 0.06 | 1.06 | -0.73 | 0.27 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 80.0469 | 80.0469 | 0 | 1 | -0.68 | 0.32 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 80.1484 | 80.1484 | -0.07 | 0.93 | -0.62 | 0.38 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 80.25 | 80.25 | -0.1 | 0.9 | -0.6 | 0.4 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 80.3477 | 80.3477 | -0.11 | 0.89 | -0.59 | 0.41 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:38 | 80.457 | 80.457 | 0.03 | 1.03 | -0.69 | 0.31 | -0.59 | 0.41 | 76.17 | 27.34
2019-09-04 | 10:38 | 80.5586 | 80.5586 | 0.03 | 1.03 | -0.71 | 0.29 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 80.6562 | 80.6562 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:38 | 80.7578 | 80.7578 | 0.05 | 1.05 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:38 | 80.8672 | 80.8672 | 0.04 | 1.04 | -0.73 | 0.27 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 80.9688 | 80.9688 | 0.05 | 1.05 | -0.73 | 0.27 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 81.0664 | 81.0664 | 0.05 | 1.05 | -0.74 | 0.26 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 81.168 | 81.168 | 0.05 | 1.05 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 81.2773 | 81.2773 | 0.05 | 1.05 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 81.3789 | 81.3789 | 0.06 | 1.06 | -0.73 | 0.27 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 81.4766 | 81.4766 | 0.06 | 1.06 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 81.5898 | 81.5898 | -0.02 | 0.98 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 29.3
2019-09-04 | 10:38 | 81.6875 | 81.6875 | -0.08 | 0.92 | -0.64 | 0.36 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 81.7891 | 81.7891 | -0.09 | 0.91 | -0.62 | 0.38 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 81.8867 | 81.8867 | -0.1 | 0.9 | -0.62 | 0.38 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 82 | 82 | 0.04 | 1.04 | -0.73 | 0.27 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 82.0977 | 82.0977 | 0.04 | 1.04 | -0.73 | 0.27 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 82.1992 | 82.1992 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 82.3086 | 82.3086 | 0.04 | 1.04 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 82.4062 | 82.4062 | 0.04 | 1.04 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 29.3
2019-09-04 | 10:38 | 82.5078 | 82.5078 | 0.05 | 1.05 | -0.74 | 0.26 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 82.6172 | 82.6172 | 0.05 | 1.05 | -0.74 | 0.26 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:38 | 82.7188 | 82.7188 | 0.05 | 1.05 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 82.8164 | 82.8164 | 0.06 | 1.06 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 82.918 | 82.918 | 0.07 | 1.07 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 83.0273 | 83.0273 | 0.03 | 1.03 | -0.73 | 0.27 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 83.1289 | 83.1289 | -0.05 | 0.95 | -0.66 | 0.34 | -0.62 | 0.38 | 77.15 | 29.3
2019-09-04 | 10:38 | 83.2266 | 83.2266 | -0.09 | 0.91 | -0.64 | 0.36 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 83.3281 | 83.3281 | -0.1 | 0.9 | -0.61 | 0.39 | -0.62 | 0.38 | 75.2 | 29.3
2019-09-04 | 10:38 | 83.4297 | 83.4297 | -0.01 | 0.99 | -0.7 | 0.3 | -0.59 | 0.41 | 74.22 | 27.34
2019-09-04 | 10:38 | 83.5391 | 83.5391 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 83.6367 | 83.6367 | 0.03 | 1.03 | -0.74 | 0.26 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:38 | 83.7383 | 83.7383 | 0.04 | 1.04 | -0.74 | 0.26 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 83.8477 | 83.8477 | 0.06 | 1.06 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 83.9492 | 83.9492 | 0.05 | 1.05 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 84.0469 | 84.0469 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 84.1562 | 84.1562 | 0.06 | 1.06 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:38 | 84.2578 | 84.2578 | 0.04 | 1.04 | -0.75 | 0.25 | -0.65 | 0.35 | 76.17 | 27.34
2019-09-04 | 10:38 | 84.3594 | 84.3594 | 0.06 | 1.06 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:38 | 84.457 | 84.457 | 0.06 | 1.06 | -0.75 | 0.25 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:38 | 84.5664 | 84.5664 | -0.03 | 0.97 | -0.69 | 0.31 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:38 | 84.668 | 84.668 | -0.08 | 0.92 | -0.65 | 0.35 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 84.7695 | 84.7695 | -0.11 | 0.89 | -0.62 | 0.38 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:38 | 84.8789 | 84.8789 | -0.11 | 0.89 | -0.61 | 0.39 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:38 | 84.9688 | 84.9688 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 85.0781 | 85.0781 | 0.02 | 1.02 | -0.73 | 0.27 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:38 | 85.1797 | 85.1797 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 85.2891 | 85.2891 | 0.05 | 1.05 | -0.74 | 0.26 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:38 | 85.3867 | 85.3867 | 0.04 | 1.04 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 85.4883 | 85.4883 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 85.5898 | 85.5898 | 0.08 | 1.08 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:38 | 85.6992 | 85.6992 | 0.05 | 1.05 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 85.7969 | 85.7969 | 0.06 | 1.06 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:38 | 85.8984 | 85.8984 | 0.04 | 1.04 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 86.0078 | 86.0078 | 0.05 | 1.05 | -0.76 | 0.24 | -0.64 | 0.36 | 76.17 | 28.32
2019-09-04 | 10:38 | 86.1094 | 86.1094 | -0.07 | 0.93 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 86.207 | 86.207 | -0.07 | 0.93 | -0.64 | 0.36 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:38 | 86.3086 | 86.3086 | -0.12 | 0.88 | -0.63 | 0.37 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:38 | 86.418 | 86.418 | -0.1 | 0.9 | -0.61 | 0.39 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:38 | 86.5195 | 86.5195 | 0.02 | 1.02 | -0.74 | 0.26 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 86.6172 | 86.6172 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 86.7188 | 86.7188 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 86.8281 | 86.8281 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 86.9297 | 86.9297 | 0.04 | 1.04 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:38 | 87.0273 | 87.0273 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:38 | 87.1289 | 87.1289 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 87.2383 | 87.2383 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:38 | 87.3398 | 87.3398 | 0.06 | 1.06 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 87.4375 | 87.4375 | 0.04 | 1.04 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 87.5469 | 87.5469 | 0 | 1 | -0.73 | 0.27 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 87.6484 | 87.6484 | -0.05 | 0.95 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:38 | 87.75 | 87.75 | -0.09 | 0.91 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:38 | 87.8477 | 87.8477 | -0.11 | 0.89 | -0.63 | 0.37 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 87.957 | 87.957 | 0 | 1 | -0.73 | 0.27 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:38 | 88.0586 | 88.0586 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 75.2 | 29.3
2019-09-04 | 10:38 | 88.1562 | 88.1562 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:38 | 88.2578 | 88.2578 | 0.06 | 1.06 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 88.3672 | 88.3672 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 88.4688 | 88.4688 | 0.04 | 1.04 | -0.76 | 0.24 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:38 | 88.5781 | 88.5781 | 0.05 | 1.05 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 88.6797 | 88.6797 | 0.05 | 1.05 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 29.3
2019-09-04 | 10:38 | 88.7773 | 88.7773 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 88.8789 | 88.8789 | 0.04 | 1.04 | -0.77 | 0.23 | -0.65 | 0.35 | 75.2 | 27.34
2019-09-04 | 10:38 | 88.9883 | 88.9883 | 0.07 | 1.07 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:38 | 89.0898 | 89.0898 | -0.03 | 0.97 | -0.7 | 0.3 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:38 | 89.1875 | 89.1875 | -0.08 | 0.92 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 89.2891 | 89.2891 | -0.11 | 0.89 | -0.63 | 0.37 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:38 | 89.3867 | 89.3867 | -0.1 | 0.9 | -0.61 | 0.39 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 89.5 | 89.5 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:38 | 89.5977 | 89.5977 | 0.03 | 1.03 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:38 | 89.6992 | 89.6992 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:38 | 89.8086 | 89.8086 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 89.9062 | 89.9062 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:38 | 90.0078 | 90.0078 | 0.06 | 1.06 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:38 | 90.1172 | 90.1172 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:38 | 90.2188 | 90.2188 | 0.04 | 1.04 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:38 | 90.3281 | 90.3281 | 0.06 | 1.06 | -0.77 | 0.23 | -0.65 | 0.35 | 75.2 | 27.34
2019-09-04 | 10:38 | 90.418 | 90.418 | 0.05 | 1.05 | -0.77 | 0.23 | -0.65 | 0.35 | 76.17 | 28.32
2019-09-04 | 10:38 | 90.5273 | 90.5273 | 0.03 | 1.03 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 28.32
2019-09-04 | 10:38 | 90.6289 | 90.6289 | -0.06 | 0.94 | -0.66 | 0.34 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:38 | 90.7266 | 90.7266 | -0.1 | 0.9 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:38 | 90.8398 | 90.8398 | -0.12 | 0.88 | -0.62 | 0.38 | -0.62 | 0.38 | 77.15 | 29.3
2019-09-04 | 10:38 | 90.9375 | 90.9375 | -0.02 | 0.98 | -0.7 | 0.3 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:38 | 91.0391 | 91.0391 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 91.1484 | 91.1484 | 0.03 | 1.03 | -0.75 | 0.25 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 91.25 | 91.25 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 91.3477 | 91.3477 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 91.4492 | 91.4492 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 91.5469 | 91.5469 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 29.3
2019-09-04 | 10:39 | 91.6562 | 91.6562 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 91.7578 | 91.7578 | 0.05 | 1.05 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 91.8594 | 91.8594 | 0.07 | 1.07 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 29.3
2019-09-04 | 10:39 | 91.957 | 91.957 | 0.04 | 1.04 | -0.79 | 0.21 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:39 | 92.0664 | 92.0664 | -0.01 | 0.99 | -0.71 | 0.29 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 92.168 | 92.168 | -0.08 | 0.92 | -0.67 | 0.33 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 92.2695 | 92.2695 | -0.09 | 0.91 | -0.65 | 0.35 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 92.3789 | 92.3789 | -0.12 | 0.88 | -0.63 | 0.37 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 92.4766 | 92.4766 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 92.5781 | 92.5781 | 0.04 | 1.04 | -0.75 | 0.25 | -0.61 | 0.39 | 75.2 | 29.3
2019-09-04 | 10:39 | 92.6797 | 92.6797 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 92.7891 | 92.7891 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 92.8867 | 92.8867 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 92.9883 | 92.9883 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 93.0898 | 93.0898 | 0.06 | 1.06 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 93.1992 | 93.1992 | 0.05 | 1.05 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 93.2969 | 93.2969 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 76.17 | 29.3
2019-09-04 | 10:39 | 93.3984 | 93.3984 | 0.06 | 1.06 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 93.5078 | 93.5078 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 28.32
2019-09-04 | 10:39 | 93.6094 | 93.6094 | -0.03 | 0.97 | -0.71 | 0.29 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 93.707 | 93.707 | -0.06 | 0.94 | -0.67 | 0.33 | -0.63 | 0.37 | 76.17 | 29.3
2019-09-04 | 10:39 | 93.8086 | 93.8086 | -0.11 | 0.89 | -0.65 | 0.35 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:39 | 93.918 | 93.918 | -0.09 | 0.91 | -0.64 | 0.36 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 94.0195 | 94.0195 | 0.03 | 1.03 | -0.76 | 0.24 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 94.1172 | 94.1172 | 0.05 | 1.05 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 94.2188 | 94.2188 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 94.3281 | 94.3281 | 0.04 | 1.04 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:39 | 94.4297 | 94.4297 | 0.05 | 1.05 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:39 | 94.5391 | 94.5391 | 0.06 | 1.06 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 29.3
2019-09-04 | 10:39 | 94.6367 | 94.6367 | 0.05 | 1.05 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 94.7383 | 94.7383 | 0.04 | 1.04 | -0.78 | 0.22 | -0.65 | 0.35 | 75.2 | 28.32
2019-09-04 | 10:39 | 94.8398 | 94.8398 | 0.06 | 1.06 | -0.78 | 0.22 | -0.65 | 0.35 | 75.2 | 27.34
2019-09-04 | 10:39 | 94.9375 | 94.9375 | 0.05 | 1.05 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 95.0469 | 95.0469 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 95.1484 | 95.1484 | -0.04 | 0.96 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 95.25 | 95.25 | -0.09 | 0.91 | -0.66 | 0.34 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:39 | 95.3594 | 95.3594 | -0.11 | 0.89 | -0.68 | 0.32 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 95.457 | 95.457 | 0.01 | 1.01 | -0.79 | 0.21 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:39 | 95.5586 | 95.5586 | 0.03 | 1.03 | -0.81 | 0.19 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 95.668 | 95.668 | 0.04 | 1.04 | -0.8 | 0.2 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 95.7695 | 95.7695 | 0.04 | 1.04 | -0.81 | 0.19 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 95.8672 | 95.8672 | 0.06 | 1.06 | -0.8 | 0.2 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 95.9688 | 95.9688 | 0.04 | 1.04 | -0.8 | 0.2 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 96.0781 | 96.0781 | 0.05 | 1.05 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 96.1797 | 96.1797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 96.2773 | 96.2773 | 0.06 | 1.06 | -0.8 | 0.2 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 96.3789 | 96.3789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 96.4883 | 96.4883 | 0.05 | 1.05 | -0.79 | 0.21 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:39 | 96.5898 | 96.5898 | -0.03 | 0.97 | -0.7 | 0.3 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 96.6875 | 96.6875 | -0.1 | 0.9 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 96.7969 | 96.7969 | -0.11 | 0.89 | -0.63 | 0.37 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 96.8984 | 96.8984 | -0.12 | 0.88 | -0.62 | 0.38 | -0.61 | 0.39 | 74.22 | 28.32
2019-09-04 | 10:39 | 97 | 97 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 29.3
2019-09-04 | 10:39 | 97.0977 | 97.0977 | 0.04 | 1.04 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 97.207 | 97.207 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:39 | 97.3086 | 97.3086 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 97.4062 | 97.4062 | 0.05 | 1.05 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:39 | 97.5078 | 97.5078 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 97.6172 | 97.6172 | 0.04 | 1.04 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 97.7188 | 97.7188 | 0.05 | 1.05 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 97.8164 | 97.8164 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 29.3
2019-09-04 | 10:39 | 97.918 | 97.918 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 98.0273 | 98.0273 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 27.34
2019-09-04 | 10:39 | 98.1289 | 98.1289 | -0.02 | 0.98 | -0.66 | 0.34 | -0.63 | 0.37 | 79.1 | 27.34
2019-09-04 | 10:39 | 98.2266 | 98.2266 | -0.1 | 0.9 | -0.63 | 0.37 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 98.3398 | 98.3398 | -0.12 | 0.88 | -0.6 | 0.4 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:39 | 98.4375 | 98.4375 | -0.04 | 0.96 | -0.66 | 0.34 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:39 | 98.5391 | 98.5391 | 0.04 | 1.04 | -0.73 | 0.27 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:39 | 98.6484 | 98.6484 | 0.04 | 1.04 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:39 | 98.75 | 98.75 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 98.8477 | 98.8477 | 0.03 | 1.03 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 98.9492 | 98.9492 | 0.06 | 1.06 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 29.3
2019-09-04 | 10:39 | 99.0469 | 99.0469 | 0.05 | 1.05 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 99.1562 | 99.1562 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 99.2578 | 99.2578 | 0.05 | 1.05 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 99.3672 | 99.3672 | 0.05 | 1.05 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 99.4688 | 99.4688 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 27.34
2019-09-04 | 10:39 | 99.5664 | 99.5664 | -0.01 | 0.99 | -0.7 | 0.3 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 99.668 | 99.668 | -0.07 | 0.93 | -0.65 | 0.35 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 99.7695 | 99.7695 | -0.13 | 0.87 | -0.61 | 0.39 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 99.8789 | 99.8789 | -0.13 | 0.87 | -0.6 | 0.4 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 99.9766 | 99.9766 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 75.2 | 26.37
2019-09-04 | 10:39 | 100.0781 | 100.0781 | 0.03 | 1.03 | -0.73 | 0.27 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:39 | 100.1797 | 100.1797 | 0.04 | 1.04 | -0.73 | 0.27 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 100.2891 | 100.2891 | 0.04 | 1.04 | -0.74 | 0.26 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 100.3867 | 100.3867 | 0.06 | 1.06 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:39 | 100.4883 | 100.4883 | 0.05 | 1.05 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 27.34
2019-09-04 | 10:39 | 100.5977 | 100.5977 | 0.05 | 1.05 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 100.6992 | 100.6992 | 0.05 | 1.05 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:39 | 100.7969 | 100.7969 | 0.04 | 1.04 | -0.74 | 0.26 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 100.8984 | 100.8984 | 0.06 | 1.06 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 10:39 | 101.0078 | 101.0078 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 101.1094 | 101.1094 | -0.07 | 0.93 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 101.207 | 101.207 | -0.08 | 0.92 | -0.63 | 0.37 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 101.3164 | 101.3164 | -0.09 | 0.91 | -0.61 | 0.39 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 101.418 | 101.418 | -0.12 | 0.88 | -0.58 | 0.42 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 101.5195 | 101.5195 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 101.6289 | 101.6289 | 0.02 | 1.02 | -0.73 | 0.27 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 101.7266 | 101.7266 | 0.05 | 1.05 | -0.72 | 0.28 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 101.8281 | 101.8281 | 0.04 | 1.04 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 101.9297 | 101.9297 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 102.0391 | 102.0391 | 0.04 | 1.04 | -0.73 | 0.27 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 102.1367 | 102.1367 | 0.05 | 1.05 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 102.2383 | 102.2383 | 0.04 | 1.04 | -0.74 | 0.26 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 102.3398 | 102.3398 | 0.07 | 1.07 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 102.4492 | 102.4492 | 0.06 | 1.06 | -0.74 | 0.26 | -0.64 | 0.36 | 76.17 | 28.32
2019-09-04 | 10:39 | 102.5469 | 102.5469 | 0.03 | 1.03 | -0.72 | 0.28 | -0.64 | 0.36 | 76.17 | 29.3
2019-09-04 | 10:39 | 102.6484 | 102.6484 | -0.07 | 0.93 | -0.65 | 0.35 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 102.7578 | 102.7578 | -0.08 | 0.92 | -0.64 | 0.36 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 102.8594 | 102.8594 | -0.12 | 0.88 | -0.63 | 0.37 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 102.957 | 102.957 | 0 | 1 | -0.75 | 0.25 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 103.0586 | 103.0586 | 0.03 | 1.03 | -0.75 | 0.25 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 103.168 | 103.168 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 103.2695 | 103.2695 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 103.3672 | 103.3672 | 0.04 | 1.04 | -0.74 | 0.26 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 103.4688 | 103.4688 | 0.05 | 1.05 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 103.5781 | 103.5781 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 103.6797 | 103.6797 | 0.05 | 1.05 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 103.7773 | 103.7773 | 0.06 | 1.06 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 103.8789 | 103.8789 | 0.04 | 1.04 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 103.9883 | 103.9883 | 0.04 | 1.04 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 27.34
2019-09-04 | 10:39 | 104.0898 | 104.0898 | -0.04 | 0.96 | -0.69 | 0.31 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 104.1875 | 104.1875 | -0.07 | 0.93 | -0.65 | 0.35 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 104.2969 | 104.2969 | -0.08 | 0.92 | -0.65 | 0.35 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 104.3984 | 104.3984 | -0.13 | 0.87 | -0.65 | 0.35 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:39 | 104.5 | 104.5 | 0.03 | 1.03 | -0.76 | 0.24 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 104.5977 | 104.5977 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 104.707 | 104.707 | 0.03 | 1.03 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 104.8086 | 104.8086 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 104.9063 | 104.9063 | 0.05 | 1.05 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 105.0078 | 105.0078 | 0.05 | 1.05 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 105.1172 | 105.1172 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 105.2188 | 105.2188 | 0.05 | 1.05 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 105.3164 | 105.3164 | 0.05 | 1.05 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 105.4297 | 105.4297 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 105.5273 | 105.5273 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 105.6289 | 105.6289 | -0.04 | 0.96 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 105.7266 | 105.7266 | -0.11 | 0.89 | -0.7 | 0.3 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 105.8398 | 105.8398 | -0.11 | 0.89 | -0.7 | 0.3 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:39 | 105.9375 | 105.9375 | -0.03 | 0.97 | -0.75 | 0.25 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:39 | 106.0391 | 106.0391 | 0.04 | 1.04 | -0.8 | 0.2 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 106.1367 | 106.1367 | 0.03 | 1.03 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 106.25 | 106.25 | 0.04 | 1.04 | -0.79 | 0.21 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:39 | 106.3477 | 106.3477 | 0.04 | 1.04 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 106.457 | 106.457 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 106.5586 | 106.5586 | 0.05 | 1.05 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 106.6563 | 106.6563 | 0.05 | 1.05 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 106.7578 | 106.7578 | 0.04 | 1.04 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 106.8594 | 106.8594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 106.9688 | 106.9688 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 107.0664 | 107.0664 | 0.04 | 1.04 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 107.1797 | 107.1797 | -0.06 | 0.94 | -0.7 | 0.3 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 107.2773 | 107.2773 | -0.1 | 0.9 | -0.71 | 0.29 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 0.078125 | 107.3554 | 0.04 | 1.04 | -0.82 | 0.18 | -0.65 | 0.35 | 74.22 | 26.37
2019-09-04 | 10:39 | 0.17969 | 107.457 | 0.04 | 1.04 | -0.8 | 0.2 | -0.63 | 0.37 | 75.2 | 25.39
2019-09-04 | 10:39 | 0.28906 | 107.5664 | 0.04 | 1.04 | -0.81 | 0.19 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:39 | 0.38672 | 107.664 | 0.05 | 1.05 | -0.79 | 0.21 | -0.63 | 0.37 | 74.22 | 27.34
2019-09-04 | 10:39 | 0.48828 | 107.7656 | 0.06 | 1.06 | -0.8 | 0.2 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 0.59766 | 107.875 | 0 | 1 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 26.37
2019-09-04 | 10:39 | 0.69922 | 107.9765 | -0.08 | 0.92 | -0.71 | 0.29 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 0.79688 | 108.0742 | -0.11 | 0.89 | -0.68 | 0.32 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:39 | 0.89844 | 108.1757 | -0.13 | 0.87 | -0.66 | 0.34 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:39 | 1.0078 | 108.2851 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 1.1094 | 108.3867 | 0.04 | 1.04 | -0.78 | 0.22 | -0.61 | 0.39 | 75.2 | 25.39
2019-09-04 | 10:39 | 1.207 | 108.4843 | 0.04 | 1.04 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 1.3086 | 108.5859 | 0.04 | 1.04 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 25.39
2019-09-04 | 10:39 | 1.418 | 108.6953 | 0.04 | 1.04 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 1.5195 | 108.7968 | 0.05 | 1.05 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 1.6172 | 108.8945 | 0.05 | 1.05 | -0.79 | 0.21 | -0.63 | 0.37 | 74.22 | 26.37
2019-09-04 | 10:39 | 1.7188 | 108.996 | 0.04 | 1.04 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 1.8281 | 109.1054 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 25.39
2019-09-04 | 10:39 | 1.9297 | 109.207 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 2.0273 | 109.3046 | 0.04 | 1.04 | -0.79 | 0.21 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:39 | 2.1367 | 109.414 | -0.04 | 0.96 | -0.69 | 0.31 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:39 | 2.2383 | 109.5156 | -0.09 | 0.91 | -0.7 | 0.3 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 2.3398 | 109.6171 | -0.12 | 0.88 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 2.4375 | 109.7148 | -0.12 | 0.88 | -0.66 | 0.34 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 2.5469 | 109.8242 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 74.22 | 26.37
2019-09-04 | 10:39 | 2.6484 | 109.9257 | 0.03 | 1.03 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 2.75 | 110.0273 | 0.04 | 1.04 | -0.78 | 0.22 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 2.8477 | 110.125 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 2.957 | 110.2343 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 3.0586 | 110.3359 | 0.04 | 1.04 | -0.78 | 0.22 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 3.2578 | 110.5351 | 0.06 | 1.06 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:39 | 3.2773 | 110.5546 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 3.3672 | 110.6445 | 0.06 | 1.06 | -0.79 | 0.21 | -0.65 | 0.35 | 75.2 | 28.32
2019-09-04 | 10:39 | 3.4688 | 110.746 | 0.05 | 1.05 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 3.5664 | 110.8437 | 0.02 | 1.02 | -0.74 | 0.26 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:39 | 3.6797 | 110.957 | -0.06 | 0.94 | -0.68 | 0.32 | -0.64 | 0.36 | 74.22 | 26.37
2019-09-04 | 10:39 | 3.7773 | 111.0546 | -0.1 | 0.9 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 3.8789 | 111.1562 | -0.14 | 0.86 | -0.65 | 0.35 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:39 | 3.9883 | 111.2656 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:39 | 4.0898 | 111.3671 | 0.02 | 1.02 | -0.77 | 0.23 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 4.1875 | 111.4648 | 0.02 | 1.02 | -0.78 | 0.22 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 4.2891 | 111.5664 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 25.39
2019-09-04 | 10:39 | 4.3984 | 111.6757 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 4.5 | 111.7773 | 0.04 | 1.04 | -0.77 | 0.23 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 4.5977 | 111.875 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 4.707 | 111.9843 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 4.8086 | 112.0859 | 0.04 | 1.04 | -0.78 | 0.22 | -0.65 | 0.35 | 76.17 | 26.37
2019-09-04 | 10:39 | 4.9062 | 112.1835 | 0.04 | 1.04 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 26.37
2019-09-04 | 10:39 | 5.0078 | 112.2851 | 0.05 | 1.05 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 5.1172 | 112.3945 | -0.02 | 0.98 | -0.72 | 0.28 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 5.2188 | 112.496 | -0.1 | 0.9 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 5.3164 | 112.5937 | -0.09 | 0.91 | -0.65 | 0.35 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 5.4297 | 112.707 | -0.14 | 0.86 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 28.32
2019-09-04 | 10:39 | 5.5273 | 112.8046 | 0 | 1 | -0.77 | 0.23 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 5.6289 | 112.9062 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 5.7266 | 113.0039 | 0.01 | 1.01 | -0.78 | 0.22 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 5.8398 | 113.1171 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 5.9375 | 113.2148 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 6.0391 | 113.3164 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 6.1367 | 113.414 | 0.03 | 1.03 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 6.25 | 113.5273 | 0.05 | 1.05 | -0.78 | 0.22 | -0.64 | 0.36 | 77.15 | 29.3
2019-09-04 | 10:39 | 6.3477 | 113.625 | 0.04 | 1.04 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 6.4492 | 113.7265 | 0.04 | 1.04 | -0.77 | 0.23 | -0.65 | 0.35 | 76.17 | 27.34
2019-09-04 | 10:39 | 6.5469 | 113.8242 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 6.6562 | 113.9335 | -0.06 | 0.94 | -0.68 | 0.32 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 6.7578 | 114.0351 | -0.11 | 0.89 | -0.65 | 0.35 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 6.8594 | 114.1367 | -0.11 | 0.89 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 6.9688 | 114.246 | -0.03 | 0.97 | -0.7 | 0.3 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 7.0664 | 114.3437 | 0.03 | 1.03 | -0.77 | 0.23 | -0.61 | 0.39 | 74.22 | 26.37
2019-09-04 | 10:39 | 7.168 | 114.4453 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 7.2695 | 114.5468 | 0.04 | 1.04 | -0.78 | 0.22 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:39 | 7.3789 | 114.6562 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 7.4766 | 114.7539 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 7.5781 | 114.8554 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 7.6797 | 114.957 | 0.03 | 1.03 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 7.7891 | 115.0664 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 7.8867 | 115.164 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 28.32
2019-09-04 | 10:39 | 7.9883 | 115.2656 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 74.22 | 27.34
2019-09-04 | 10:39 | 8.0977 | 115.375 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 8.1992 | 115.4765 | -0.07 | 0.93 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 8.2969 | 115.5742 | -0.09 | 0.91 | -0.65 | 0.35 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 8.3984 | 115.6757 | -0.11 | 0.89 | -0.65 | 0.35 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 8.5078 | 115.7851 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 25.39
2019-09-04 | 10:39 | 8.6094 | 115.8867 | 0.02 | 1.02 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 8.707 | 115.9843 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 8.8086 | 116.0859 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 8.918 | 116.1953 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 25.39
2019-09-04 | 10:39 | 9.0195 | 116.2968 | 0.01 | 1.01 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 9.1289 | 116.4062 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:39 | 9.2266 | 116.5039 | 0.06 | 1.06 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 9.3281 | 116.6054 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 9.4297 | 116.707 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 9.5273 | 116.8046 | 0.05 | 1.05 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:39 | 9.6367 | 116.914 | -0.05 | 0.95 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 25.39
2019-09-04 | 10:39 | 9.7383 | 117.0156 | -0.1 | 0.9 | -0.66 | 0.34 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 9.8398 | 117.1171 | -0.11 | 0.89 | -0.65 | 0.35 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 9.9375 | 117.2148 | -0.13 | 0.87 | -0.62 | 0.38 | -0.6 | 0.4 | 75.2 | 26.37
2019-09-04 | 10:39 | 10.0469 | 117.3242 | 0.02 | 1.02 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 10.1484 | 117.4257 | 0.03 | 1.03 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 10.2578 | 117.5351 | 0.02 | 1.02 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 10.3594 | 117.6367 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 10.457 | 117.7343 | 0.03 | 1.03 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 10.5586 | 117.8359 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 10.668 | 117.9453 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 10.7695 | 118.0468 | 0.06 | 1.06 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:39 | 10.8672 | 118.1445 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 74.22 | 27.34
2019-09-04 | 10:39 | 10.9688 | 118.246 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 11.0781 | 118.3554 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 11.1797 | 118.457 | -0.07 | 0.93 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 11.2773 | 118.5546 | -0.11 | 0.89 | -0.65 | 0.35 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 11.3867 | 118.664 | -0.12 | 0.88 | -0.65 | 0.35 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 11.4883 | 118.7656 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 11.5898 | 118.8671 | 0.02 | 1.02 | -0.75 | 0.25 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:39 | 11.6875 | 118.9648 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 11.7969 | 119.0742 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 11.8984 | 119.1757 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 12 | 119.2773 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 12.0977 | 119.375 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 12.207 | 119.4843 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 12.3086 | 119.5859 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 25.39
2019-09-04 | 10:39 | 12.4062 | 119.6835 | 0.05 | 1.05 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 12.5078 | 119.7851 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 74.22 | 26.37
2019-09-04 | 10:39 | 12.6172 | 119.8945 | -0.02 | 0.98 | -0.71 | 0.29 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 12.7188 | 119.996 | -0.07 | 0.93 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 12.8164 | 120.0937 | -0.11 | 0.89 | -0.64 | 0.36 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:39 | 12.9297 | 120.207 | -0.13 | 0.87 | -0.65 | 0.35 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 13.0273 | 120.3046 | 0.03 | 1.03 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 13.1289 | 120.4062 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 13.2266 | 120.5039 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 13.3398 | 120.6171 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:39 | 13.4375 | 120.7148 | 0.03 | 1.03 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 13.5391 | 120.8164 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 13.6367 | 120.914 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 13.75 | 121.0273 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:39 | 13.8477 | 121.125 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 74.22 | 28.32
2019-09-04 | 10:39 | 13.9492 | 121.2265 | 0.04 | 1.04 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 14.0586 | 121.3359 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 76.17 | 28.32
2019-09-04 | 10:39 | 14.1562 | 121.4335 | -0.06 | 0.94 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 14.2578 | 121.5351 | -0.1 | 0.9 | -0.66 | 0.34 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 14.3594 | 121.6367 | -0.14 | 0.86 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 14.4688 | 121.746 | -0.08 | 0.92 | -0.67 | 0.33 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 14.5664 | 121.8437 | 0.02 | 1.02 | -0.76 | 0.24 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 14.668 | 121.9453 | 0.02 | 1.02 | -0.77 | 0.23 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:39 | 14.7695 | 122.0468 | 0.03 | 1.03 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 25.39
2019-09-04 | 10:39 | 14.8789 | 122.1562 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 14.9766 | 122.2539 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 15.0898 | 122.3671 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 15.1875 | 122.4648 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:39 | 15.2891 | 122.5664 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 76.17 | 28.32
2019-09-04 | 10:39 | 15.3867 | 122.664 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 15.5 | 122.7773 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:39 | 15.5977 | 122.875 | 0.02 | 1.02 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 15.6992 | 122.9765 | -0.06 | 0.94 | -0.67 | 0.33 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 15.7969 | 123.0742 | -0.11 | 0.89 | -0.63 | 0.37 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:39 | 15.9062 | 123.1835 | -0.13 | 0.87 | -0.62 | 0.38 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 16.0078 | 123.2851 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:39 | 16.1094 | 123.3867 | 0.01 | 1.01 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:39 | 16.2188 | 123.496 | 0.04 | 1.04 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 16.3164 | 123.5937 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 16.418 | 123.6953 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:39 | 16.5195 | 123.7968 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:39 | 16.6289 | 123.9062 | 0.02 | 1.02 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 16.7266 | 124.0039 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 16.8281 | 124.1054 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 16.9297 | 124.207 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 17.0273 | 124.3046 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 17.1367 | 124.414 | -0.08 | 0.92 | -0.68 | 0.32 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 17.2383 | 124.5156 | -0.09 | 0.91 | -0.65 | 0.35 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 17.3477 | 124.625 | -0.13 | 0.87 | -0.63 | 0.37 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:39 | 17.4492 | 124.7265 | -0.13 | 0.87 | -0.61 | 0.39 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:39 | 17.5469 | 124.8242 | 0.02 | 1.02 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:39 | 17.6484 | 124.9257 | 0.02 | 1.02 | -0.76 | 0.24 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:39 | 17.7578 | 125.0351 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:39 | 17.8594 | 125.1367 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:39 | 17.957 | 125.2343 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:39 | 18.0586 | 125.3359 | 0.04 | 1.04 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 18.168 | 125.4453 | 0.06 | 1.06 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:39 | 18.2695 | 125.5468 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:39 | 18.3672 | 125.6445 | 0.06 | 1.06 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:39 | 18.4688 | 125.746 | 0.01 | 1.01 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 27.34
2019-09-04 | 10:39 | 18.5781 | 125.8554 | 0.03 | 1.03 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:39 | 18.6797 | 125.957 | -0.08 | 0.92 | -0.67 | 0.33 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:39 | 18.7773 | 126.0546 | -0.11 | 0.89 | -0.65 | 0.35 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:39 | 18.8867 | 126.164 | -0.14 | 0.86 | -0.63 | 0.37 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:39 | 18.9883 | 126.2656 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:39 | 19.0898 | 126.3671 | 0.01 | 1.01 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:39 | 19.1875 | 126.4648 | 0.03 | 1.03 | -0.74 | 0.26 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:39 | 19.2969 | 126.5742 | 0.02 | 1.02 | -0.75 | 0.25 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:39 | 19.3984 | 126.6757 | 0.04 | 1.04 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 26.37
2019-09-04 | 10:39 | 19.5 | 126.7773 | 0.05 | 1.05 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 19.5977 | 126.875 | 0.02 | 1.02 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:40 | 19.707 | 126.9843 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 19.8086 | 127.0859 | 0.05 | 1.05 | -0.74 | 0.26 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:40 | 19.9062 | 127.1835 | 0.02 | 1.02 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 20.0391 | 127.3164 | 0.03 | 1.03 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 29.3
2019-09-04 | 10:40 | 20.1172 | 127.3945 | -0.03 | 0.97 | -0.72 | 0.28 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 20.2188 | 127.496 | -0.09 | 0.91 | -0.66 | 0.34 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 20.3164 | 127.5937 | -0.12 | 0.88 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 20.4297 | 127.707 | -0.13 | 0.87 | -0.63 | 0.37 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:40 | 20.5273 | 127.8046 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 25.39
2019-09-04 | 10:40 | 20.6289 | 127.9062 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 20.7266 | 128.0039 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 20.8398 | 128.1171 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 20.9375 | 128.2148 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 21.0391 | 128.3164 | 0.03 | 1.03 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:40 | 21.207 | 128.4843 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 21.25 | 128.5273 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 21.3477 | 128.625 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 21.4492 | 128.7265 | 0.03 | 1.03 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 21.5586 | 128.8359 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 21.6562 | 128.9335 | -0.06 | 0.94 | -0.69 | 0.31 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 21.7695 | 129.0468 | -0.07 | 0.93 | -0.66 | 0.34 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 21.8672 | 129.1445 | -0.12 | 0.88 | -0.64 | 0.36 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 21.9688 | 129.246 | -0.13 | 0.87 | -0.64 | 0.36 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:40 | 22.0664 | 129.3437 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 22.1797 | 129.457 | 0.02 | 1.02 | -0.75 | 0.25 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 22.2773 | 129.5546 | 0.01 | 1.01 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 22.3789 | 129.6562 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 22.4766 | 129.7539 | 0.04 | 1.04 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 22.5781 | 129.8554 | 0.03 | 1.03 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 22.6875 | 129.9648 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 22.7891 | 130.0664 | 0.02 | 1.02 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 22.8867 | 130.164 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 22.9883 | 130.2656 | 0.04 | 1.04 | -0.77 | 0.23 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 23.0977 | 130.375 | -0.02 | 0.98 | -0.72 | 0.28 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 23.1992 | 130.4765 | -0.09 | 0.91 | -0.67 | 0.33 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 23.3086 | 130.5859 | -0.13 | 0.87 | -0.65 | 0.35 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 23.4062 | 130.6835 | -0.13 | 0.87 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:40 | 23.5078 | 130.7851 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 23.6094 | 130.8867 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 23.7188 | 130.996 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 23.8164 | 131.0937 | 0.04 | 1.04 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 23.918 | 131.1953 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 24.0195 | 131.2968 | 0.03 | 1.03 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 24.1289 | 131.4062 | 0.05 | 1.05 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 24.2266 | 131.5039 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 24.3281 | 131.6054 | 0.05 | 1.05 | -0.76 | 0.24 | -0.65 | 0.35 | 77.15 | 27.34
2019-09-04 | 10:40 | 24.4375 | 131.7148 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 24.5391 | 131.8164 | 0.05 | 1.05 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 24.6367 | 131.914 | -0.05 | 0.95 | -0.7 | 0.3 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 24.7383 | 132.0156 | -0.11 | 0.89 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 24.8477 | 132.125 | -0.14 | 0.86 | -0.63 | 0.37 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 24.9492 | 132.2265 | -0.13 | 0.87 | -0.64 | 0.36 | -0.6 | 0.4 | 76.17 | 26.37
2019-09-04 | 10:40 | 25.0469 | 132.3242 | 0.02 | 1.02 | -0.76 | 0.24 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 25.1484 | 132.4257 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:40 | 25.2578 | 132.5351 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 25.3594 | 132.6367 | 0.03 | 1.03 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 25.457 | 132.7343 | 0.02 | 1.02 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 25.5664 | 132.8437 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 25.668 | 132.9453 | 0.03 | 1.03 | -0.77 | 0.23 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 25.7695 | 133.0468 | 0.02 | 1.02 | -0.76 | 0.24 | -0.65 | 0.35 | 76.17 | 28.32
2019-09-04 | 10:40 | 25.8789 | 133.1562 | 0.02 | 1.02 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 26.37
2019-09-04 | 10:40 | 25.9766 | 133.2539 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 29.3
2019-09-04 | 10:40 | 26.0781 | 133.3554 | 0.01 | 1.01 | -0.75 | 0.25 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 26.1797 | 133.457 | -0.08 | 0.92 | -0.67 | 0.33 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 26.2773 | 133.5546 | -0.12 | 0.88 | -0.65 | 0.35 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:40 | 26.3867 | 133.664 | -0.15 | 0.85 | -0.62 | 0.38 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 26.4883 | 133.7656 | -0.04 | 0.96 | -0.72 | 0.28 | -0.6 | 0.4 | 75.2 | 26.37
2019-09-04 | 10:40 | 26.5977 | 133.875 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 26.6992 | 133.9765 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 26.7969 | 134.0742 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 26.8984 | 134.1757 | 0.02 | 1.02 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 27 | 134.2773 | 0.02 | 1.02 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 27.1094 | 134.3867 | 0.04 | 1.04 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 27.207 | 134.4843 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 27.3086 | 134.5859 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:40 | 27.4062 | 134.6835 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 27.5195 | 134.7968 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 27.6172 | 134.8945 | -0.03 | 0.97 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 27.7266 | 135.0039 | -0.1 | 0.9 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 25.39
2019-09-04 | 10:40 | 27.8281 | 135.1054 | -0.12 | 0.88 | -0.65 | 0.35 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 27.9297 | 135.207 | -0.17 | 0.83 | -0.64 | 0.36 | -0.6 | 0.4 | 75.2 | 27.34
2019-09-04 | 10:40 | 28.0273 | 135.3046 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 28.1367 | 135.414 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 28.2383 | 135.5156 | 0.03 | 1.03 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 28.3398 | 135.6171 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 28.4375 | 135.7148 | 0.02 | 1.02 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:40 | 28.5391 | 135.8164 | 0.01 | 1.01 | -0.76 | 0.24 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:40 | 28.6484 | 135.9257 | 0.03 | 1.03 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 28.75 | 136.0273 | 0.02 | 1.02 | -0.77 | 0.23 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 28.8477 | 136.125 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 28.9492 | 136.2265 | 0.04 | 1.04 | -0.77 | 0.23 | -0.65 | 0.35 | 76.17 | 27.34
2019-09-04 | 10:40 | 29.0586 | 136.3359 | 0.03 | 1.03 | -0.77 | 0.23 | -0.65 | 0.35 | 75.2 | 26.37
2019-09-04 | 10:40 | 29.1562 | 136.4335 | -0.04 | 0.96 | -0.69 | 0.31 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 29.2695 | 136.5468 | -0.08 | 0.92 | -0.66 | 0.34 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 29.3672 | 136.6445 | -0.15 | 0.85 | -0.65 | 0.35 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 29.4688 | 136.746 | -0.14 | 0.86 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 29.5664 | 136.8437 | 0.02 | 1.02 | -0.77 | 0.23 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:40 | 29.6797 | 136.957 | 0.01 | 1.01 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 29.7773 | 137.0546 | 0 | 1 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 29.8789 | 137.1562 | 0.04 | 1.04 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 29.9766 | 137.2539 | 0.02 | 1.02 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 30.0898 | 137.3671 | 0.02 | 1.02 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:40 | 30.1875 | 137.4648 | 0.04 | 1.04 | -0.78 | 0.22 | -0.65 | 0.35 | 75.2 | 26.37
2019-09-04 | 10:40 | 30.2891 | 137.5664 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:40 | 30.3984 | 137.6757 | 0.03 | 1.03 | -0.76 | 0.24 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 30.5 | 137.7773 | 0.04 | 1.04 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 30.5977 | 137.875 | 0.02 | 1.02 | -0.75 | 0.25 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 30.6992 | 137.9765 | -0.09 | 0.91 | -0.67 | 0.33 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 30.8086 | 138.0859 | -0.14 | 0.86 | -0.67 | 0.33 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 30.9062 | 138.1835 | -0.14 | 0.86 | -0.65 | 0.35 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 31.0078 | 138.2851 | -0.03 | 0.97 | -0.77 | 0.23 | -0.61 | 0.39 | 75.2 | 25.39
2019-09-04 | 10:40 | 31.1172 | 138.3945 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 31.2188 | 138.496 | 0.01 | 1.01 | -0.77 | 0.23 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:40 | 31.3164 | 138.5937 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 25.39
2019-09-04 | 10:40 | 31.418 | 138.6953 | 0.02 | 1.02 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 31.5273 | 138.8046 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 31.6289 | 138.9062 | 0.02 | 1.02 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 31.7266 | 139.0039 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 31.8281 | 139.1054 | 0.01 | 1.01 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 31.9375 | 139.2148 | 0.02 | 1.02 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 28.32
2019-09-04 | 10:40 | 32.0391 | 139.3164 | 0.02 | 1.02 | -0.77 | 0.23 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 32.1367 | 139.414 | -0.05 | 0.95 | -0.69 | 0.31 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 32.25 | 139.5273 | -0.11 | 0.89 | -0.67 | 0.33 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 32.3477 | 139.625 | -0.15 | 0.85 | -0.64 | 0.36 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 32.4492 | 139.7265 | -0.14 | 0.86 | -0.64 | 0.36 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:40 | 32.5469 | 139.8242 | -0.03 | 0.97 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 32.6562 | 139.9335 | 0.02 | 1.02 | -0.77 | 0.23 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 32.7578 | 140.0351 | 0.01 | 1.01 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 32.8594 | 140.1367 | 0.01 | 1.01 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 32.957 | 140.2343 | 0.02 | 1.02 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 33.0664 | 140.3437 | 0.02 | 1.02 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 33.168 | 140.4453 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 33.2773 | 140.5546 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 33.3672 | 140.6445 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 33.4766 | 140.7539 | 0.02 | 1.02 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 33.5781 | 140.8554 | 0.03 | 1.03 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 33.6875 | 140.9648 | -0.08 | 0.92 | -0.68 | 0.32 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 33.7891 | 141.0664 | -0.13 | 0.87 | -0.65 | 0.35 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 33.8867 | 141.164 | -0.14 | 0.86 | -0.64 | 0.36 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 33.9883 | 141.2656 | -0.05 | 0.95 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:40 | 34.0977 | 141.375 | 0.01 | 1.01 | -0.79 | 0.21 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 34.1992 | 141.4765 | -0.02 | 0.98 | -0.78 | 0.22 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 34.2969 | 141.5742 | -0.01 | 0.99 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 34.3984 | 141.6757 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 34.5078 | 141.7851 | 0.03 | 1.03 | -0.78 | 0.22 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:40 | 34.6094 | 141.8867 | 0 | 1 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 34.707 | 141.9843 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 34.8086 | 142.0859 | 0.02 | 1.02 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 34.918 | 142.1953 | 0.01 | 1.01 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:40 | 35.0195 | 142.2968 | 0.03 | 1.03 | -0.76 | 0.24 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 35.1172 | 142.3945 | -0.03 | 0.97 | -0.73 | 0.27 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 35.2266 | 142.5039 | -0.1 | 0.9 | -0.69 | 0.31 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 35.3281 | 142.6054 | -0.13 | 0.87 | -0.69 | 0.31 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 35.4297 | 142.707 | -0.16 | 0.84 | -0.69 | 0.31 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 35.5273 | 142.8046 | -0.03 | 0.97 | -0.8 | 0.2 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 35.6367 | 142.914 | 0.01 | 1.01 | -0.8 | 0.2 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 35.7383 | 143.0156 | 0.01 | 1.01 | -0.8 | 0.2 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 35.8398 | 143.1171 | 0 | 1 | -0.79 | 0.21 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 35.9492 | 143.2265 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:40 | 36.0391 | 143.3164 | 0.04 | 1.04 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 36.1484 | 143.4257 | 0.02 | 1.02 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 36.25 | 143.5273 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 36.3594 | 143.6367 | 0 | 1 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 36.457 | 143.7343 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 36.5586 | 143.8359 | 0 | 1 | -0.78 | 0.22 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 36.6562 | 143.9335 | -0.08 | 0.92 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 36.7695 | 144.0468 | -0.13 | 0.87 | -0.7 | 0.3 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 36.8672 | 144.1445 | -0.14 | 0.86 | -0.69 | 0.31 | -0.62 | 0.38 | 75.2 | 28.32
2019-09-04 | 10:40 | 36.9688 | 144.246 | -0.14 | 0.86 | -0.68 | 0.32 | -0.6 | 0.4 | 75.2 | 26.37
2019-09-04 | 10:40 | 37.0781 | 144.3554 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 37.1797 | 144.457 | 0.01 | 1.01 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 37.2773 | 144.5546 | -0.01 | 0.99 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 37.3789 | 144.6562 | 0.02 | 1.02 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 37.4883 | 144.7656 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 37.5898 | 144.8671 | 0.04 | 1.04 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 37.6875 | 144.9648 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 37.7891 | 145.0664 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 26.37
2019-09-04 | 10:40 | 37.8984 | 145.1757 | 0.02 | 1.02 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 38 | 145.2773 | 0.02 | 1.02 | -0.79 | 0.21 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 38.0977 | 145.375 | 0.02 | 1.02 | -0.78 | 0.22 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 38.207 | 145.4843 | -0.11 | 0.89 | -0.71 | 0.29 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 38.3086 | 145.5859 | -0.13 | 0.87 | -0.66 | 0.34 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 38.4062 | 145.6835 | -0.17 | 0.83 | -0.66 | 0.34 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 38.5078 | 145.7851 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 38.6172 | 145.8945 | 0 | 1 | -0.78 | 0.22 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 38.7188 | 145.996 | 0 | 1 | -0.78 | 0.22 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:40 | 38.8164 | 146.0937 | 0.03 | 1.03 | -0.78 | 0.22 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 38.918 | 146.1953 | 0.02 | 1.02 | -0.78 | 0.22 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 39.0273 | 146.3046 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 39.1289 | 146.4062 | 0 | 1 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 28.32
2019-09-04 | 10:40 | 39.2266 | 146.5039 | 0 | 1 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 39.3281 | 146.6054 | 0.02 | 1.02 | -0.79 | 0.21 | -0.65 | 0.35 | 75.2 | 26.37
2019-09-04 | 10:40 | 39.4375 | 146.7148 | 0 | 1 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 39.5391 | 146.8164 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 39.6484 | 146.9257 | -0.04 | 0.96 | -0.72 | 0.28 | -0.64 | 0.36 | 75.2 | 28.32
2019-09-04 | 10:40 | 39.75 | 147.0273 | -0.15 | 0.85 | -0.67 | 0.33 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 39.8477 | 147.125 | -0.15 | 0.85 | -0.65 | 0.35 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:40 | 39.9492 | 147.2265 | -0.17 | 0.83 | -0.66 | 0.34 | -0.6 | 0.4 | 75.2 | 26.37
2019-09-04 | 10:40 | 40.0586 | 147.3359 | -0.02 | 0.98 | -0.79 | 0.21 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 40.1562 | 147.4335 | -0.01 | 0.99 | -0.78 | 0.22 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 40.2578 | 147.5351 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 40.3672 | 147.6445 | 0.01 | 1.01 | -0.79 | 0.21 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 40.4688 | 147.746 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 40.5664 | 147.8437 | 0.03 | 1.03 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 40.6797 | 147.957 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 40.7773 | 148.0546 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 40.8789 | 148.1562 | 0.03 | 1.03 | -0.78 | 0.22 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 40.9766 | 148.2539 | 0.03 | 1.03 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 41.0898 | 148.3671 | 0.02 | 1.02 | -0.78 | 0.22 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 41.1875 | 148.4648 | -0.1 | 0.9 | -0.69 | 0.31 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 41.2891 | 148.5664 | -0.14 | 0.86 | -0.66 | 0.34 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 41.3867 | 148.664 | -0.17 | 0.83 | -0.66 | 0.34 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:40 | 41.4883 | 148.7656 | -0.08 | 0.92 | -0.75 | 0.25 | -0.6 | 0.4 | 75.2 | 26.37
2019-09-04 | 10:40 | 41.5977 | 148.875 | -0.01 | 0.99 | -0.79 | 0.21 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 41.6992 | 148.9765 | -0.01 | 0.99 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 41.7969 | 149.0742 | -0.01 | 0.99 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 41.9062 | 149.1835 | 0 | 1 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 42.0078 | 149.2851 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 42.1172 | 149.3945 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 42.207 | 149.4843 | 0 | 1 | -0.78 | 0.22 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 42.3164 | 149.5937 | 0.03 | 1.03 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 42.418 | 149.6953 | 0.02 | 1.02 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 27.34
2019-09-04 | 10:40 | 42.5195 | 149.7968 | 0.02 | 1.02 | -0.79 | 0.21 | -0.65 | 0.35 | 76.17 | 28.32
2019-09-04 | 10:40 | 42.6172 | 149.8945 | -0.05 | 0.95 | -0.73 | 0.27 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 42.7266 | 150.0039 | -0.13 | 0.87 | -0.68 | 0.32 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 42.8281 | 150.1054 | -0.15 | 0.85 | -0.68 | 0.32 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 42.9297 | 150.207 | -0.15 | 0.85 | -0.69 | 0.31 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:40 | 43.0391 | 150.3164 | -0.04 | 0.96 | -0.79 | 0.21 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:40 | 43.1367 | 150.414 | -0.01 | 0.99 | -0.8 | 0.2 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 43.2383 | 150.5156 | -0.01 | 0.99 | -0.8 | 0.2 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 43.3398 | 150.6171 | -0.01 | 0.99 | -0.8 | 0.2 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 43.4492 | 150.7265 | -0.01 | 0.99 | -0.8 | 0.2 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 43.5469 | 150.8242 | 0.02 | 1.02 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 43.6484 | 150.9257 | -0.01 | 0.99 | -0.79 | 0.21 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 43.75 | 151.0273 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 43.8594 | 151.1367 | 0.02 | 1.02 | -0.79 | 0.21 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 43.957 | 151.2343 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 44.0586 | 151.3359 | 0.02 | 1.02 | -0.79 | 0.21 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 44.168 | 151.4453 | -0.11 | 0.89 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 44.2695 | 151.5468 | -0.15 | 0.85 | -0.69 | 0.31 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 44.3672 | 151.6445 | -0.17 | 0.83 | -0.66 | 0.34 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 44.4766 | 151.7539 | -0.17 | 0.83 | -0.67 | 0.33 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 44.5781 | 151.8554 | -0.02 | 0.98 | -0.8 | 0.2 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 44.6797 | 151.957 | -0.02 | 0.98 | -0.79 | 0.21 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 44.7773 | 152.0546 | -0.01 | 0.99 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 44.8867 | 152.164 | 0 | 1 | -0.8 | 0.2 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 44.9883 | 152.2656 | 0.01 | 1.01 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 45.0898 | 152.3671 | 0 | 1 | -0.8 | 0.2 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 45.1992 | 152.4765 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:40 | 45.2891 | 152.5664 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:40 | 45.3984 | 152.6757 | 0.03 | 1.03 | -0.79 | 0.21 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 45.5 | 152.7773 | 0.01 | 1.01 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 45.6094 | 152.8867 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 45.707 | 152.9843 | -0.11 | 0.89 | -0.69 | 0.31 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 45.8086 | 153.0859 | -0.15 | 0.85 | -0.67 | 0.33 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:40 | 45.9062 | 153.1835 | -0.16 | 0.84 | -0.67 | 0.33 | -0.6 | 0.4 | 76.17 | 28.32
2019-09-04 | 10:40 | 46.0195 | 153.2968 | -0.05 | 0.95 | -0.79 | 0.21 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 46.1172 | 153.3945 | -0.01 | 0.99 | -0.79 | 0.21 | -0.6 | 0.4 | 76.17 | 26.37
2019-09-04 | 10:40 | 46.2188 | 153.496 | 0 | 1 | -0.81 | 0.19 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 46.3164 | 153.5937 | 0.02 | 1.02 | -0.8 | 0.2 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 46.4297 | 153.707 | -0.01 | 0.99 | -0.8 | 0.2 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 46.5273 | 153.8046 | 0.02 | 1.02 | -0.8 | 0.2 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 46.6289 | 153.9062 | -0.01 | 0.99 | -0.8 | 0.2 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 46.7383 | 154.0156 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 46.8398 | 154.1171 | 0.01 | 1.01 | -0.8 | 0.2 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 46.9375 | 154.2148 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 47.0391 | 154.3164 | 0.02 | 1.02 | -0.78 | 0.22 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 47.1484 | 154.4257 | -0.05 | 0.95 | -0.75 | 0.25 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 47.25 | 154.5273 | -0.12 | 0.88 | -0.69 | 0.31 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 47.3477 | 154.625 | -0.14 | 0.86 | -0.69 | 0.31 | -0.6 | 0.4 | 75.2 | 28.32
2019-09-04 | 10:40 | 47.457 | 154.7343 | -0.17 | 0.83 | -0.66 | 0.34 | -0.6 | 0.4 | 76.17 | 26.37
2019-09-04 | 10:40 | 47.5586 | 154.8359 | -0.02 | 0.98 | -0.79 | 0.21 | -0.61 | 0.39 | 75.2 | 26.37
2019-09-04 | 10:40 | 47.6562 | 154.9335 | -0.01 | 0.99 | -0.8 | 0.2 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 47.7578 | 155.0351 | -0.01 | 0.99 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 27.34
2019-09-04 | 10:40 | 47.8672 | 155.1445 | 0 | 1 | -0.8 | 0.2 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 47.9688 | 155.246 | 0 | 1 | -0.8 | 0.2 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 48.0664 | 155.3437 | 0.02 | 1.02 | -0.79 | 0.21 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:40 | 48.168 | 155.4453 | 0.01 | 1.01 | -0.8 | 0.2 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 48.2773 | 155.5546 | 0 | 1 | -0.8 | 0.2 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 48.3789 | 155.6562 | 0.01 | 1.01 | -0.8 | 0.2 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 48.4883 | 155.7656 | 0.03 | 1.03 | -0.79 | 0.21 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 48.5781 | 155.8554 | 0 | 1 | -0.79 | 0.21 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 48.6875 | 155.9648 | -0.09 | 0.91 | -0.71 | 0.29 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 48.7891 | 156.0664 | -0.14 | 0.86 | -0.66 | 0.34 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 48.8867 | 156.164 | -0.15 | 0.85 | -0.67 | 0.33 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 49 | 156.2773 | -0.09 | 0.91 | -0.72 | 0.28 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 49.0977 | 156.375 | 0 | 1 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 49.1992 | 156.4765 | -0.02 | 0.98 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 49.2969 | 156.5742 | 0 | 1 | -0.8 | 0.2 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 49.4062 | 156.6835 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 26.37
2019-09-04 | 10:40 | 49.5078 | 156.7851 | 0.01 | 1.01 | -0.8 | 0.2 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 49.6094 | 156.8867 | 0.01 | 1.01 | -0.8 | 0.2 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 49.707 | 156.9843 | 0.01 | 1.01 | -0.79 | 0.21 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 49.8164 | 157.0937 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 49.918 | 157.1953 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 50.0195 | 157.2968 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 50.1289 | 157.4062 | -0.02 | 0.98 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 50.2266 | 157.5039 | -0.09 | 0.91 | -0.71 | 0.29 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 50.3281 | 157.6054 | -0.14 | 0.86 | -0.68 | 0.32 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 50.4297 | 157.707 | -0.18 | 0.82 | -0.66 | 0.34 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 50.5391 | 157.8164 | -0.05 | 0.95 | -0.78 | 0.22 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 50.6367 | 157.914 | -0.02 | 0.98 | -0.79 | 0.21 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 50.7383 | 158.0156 | -0.01 | 0.99 | -0.78 | 0.22 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 50.8398 | 158.1171 | 0 | 1 | -0.79 | 0.21 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 50.9492 | 158.2265 | -0.02 | 0.98 | -0.79 | 0.21 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 51.0469 | 158.3242 | 0 | 1 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 51.1562 | 158.4335 | 0 | 1 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 51.25 | 158.5273 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 51.3594 | 158.6367 | -0.01 | 0.99 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 51.457 | 158.7343 | 0.02 | 1.02 | -0.79 | 0.21 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 51.5664 | 158.8437 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 75.2 | 27.34
2019-09-04 | 10:40 | 51.668 | 158.9453 | -0.08 | 0.92 | -0.72 | 0.28 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 51.7695 | 159.0468 | -0.16 | 0.84 | -0.66 | 0.34 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 51.8672 | 159.1445 | -0.16 | 0.84 | -0.66 | 0.34 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 51.9766 | 159.2539 | -0.17 | 0.83 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 52.0781 | 159.3554 | -0.03 | 0.97 | -0.77 | 0.23 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 52.1797 | 159.457 | -0.03 | 0.97 | -0.78 | 0.22 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:40 | 52.2773 | 159.5546 | 0.02 | 1.02 | -0.79 | 0.21 | -0.62 | 0.38 | 75.2 | 26.37
2019-09-04 | 10:40 | 52.3867 | 159.664 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 52.4883 | 159.7656 | -0.02 | 0.98 | -0.79 | 0.21 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:40 | 52.5898 | 159.8671 | 0.01 | 1.01 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 52.6992 | 159.9765 | -0.02 | 0.98 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 52.7969 | 160.0742 | 0.03 | 1.03 | -0.78 | 0.22 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 52.8984 | 160.1757 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 53 | 160.2773 | -0.01 | 0.99 | -0.79 | 0.21 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 53.1094 | 160.3867 | 0 | 1 | -0.78 | 0.22 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 53.207 | 160.4843 | -0.11 | 0.89 | -0.69 | 0.31 | -0.61 | 0.39 | 75.2 | 27.34
2019-09-04 | 10:40 | 53.3086 | 160.5859 | -0.15 | 0.85 | -0.65 | 0.35 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 53.418 | 160.6953 | -0.16 | 0.84 | -0.65 | 0.35 | -0.6 | 0.4 | 76.17 | 28.32
2019-09-04 | 10:40 | 53.5195 | 160.7968 | -0.05 | 0.95 | -0.76 | 0.24 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:40 | 53.6172 | 160.8945 | 0 | 1 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 53.7188 | 160.996 | -0.01 | 0.99 | -0.78 | 0.22 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 53.8281 | 161.1054 | 0 | 1 | -0.78 | 0.22 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 53.9297 | 161.207 | -0.01 | 0.99 | -0.78 | 0.22 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 54.0273 | 161.3046 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 54.1289 | 161.4062 | 0 | 1 | -0.79 | 0.21 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 54.2383 | 161.5156 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 54.3398 | 161.6171 | -0.01 | 0.99 | -0.78 | 0.22 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 54.4375 | 161.7148 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 54.5391 | 161.8164 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 29.3
2019-09-04 | 10:40 | 54.6484 | 161.9257 | -0.04 | 0.96 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 54.75 | 162.0273 | -0.13 | 0.87 | -0.68 | 0.32 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 54.8477 | 162.125 | -0.17 | 0.83 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 54.957 | 162.2343 | -0.14 | 0.86 | -0.65 | 0.35 | -0.6 | 0.4 | 76.17 | 28.32
2019-09-04 | 10:40 | 55.0586 | 162.3359 | -0.03 | 0.97 | -0.76 | 0.24 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:40 | 55.1562 | 162.4335 | 0 | 1 | -0.76 | 0.24 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 55.2578 | 162.5351 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 55.3672 | 162.6445 | 0.01 | 1.01 | -0.77 | 0.23 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 55.4688 | 162.746 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 55.5664 | 162.8437 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 55.6797 | 162.957 | -0.02 | 0.98 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 55.7773 | 163.0546 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 55.8789 | 163.1562 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 55.9883 | 163.2656 | 0.02 | 1.02 | -0.77 | 0.23 | -0.64 | 0.36 | 78.12 | 28.32
2019-09-04 | 10:40 | 56.0898 | 163.3671 | -0.01 | 0.99 | -0.78 | 0.22 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 56.1875 | 163.4648 | -0.1 | 0.9 | -0.68 | 0.32 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 56.2891 | 163.5664 | -0.12 | 0.88 | -0.65 | 0.35 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 56.3867 | 163.664 | -0.18 | 0.82 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 56.5 | 163.7773 | -0.13 | 0.87 | -0.66 | 0.34 | -0.6 | 0.4 | 77.15 | 28.32
2019-09-04 | 10:40 | 56.5977 | 163.875 | -0.02 | 0.98 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:40 | 56.6992 | 163.9765 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 56.8086 | 164.0859 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 56.9062 | 164.1835 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 57.0078 | 164.2851 | -0.02 | 0.98 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 57.1172 | 164.3945 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 57.2188 | 164.496 | 0 | 1 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 57.3164 | 164.5937 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 57.418 | 164.6953 | 0 | 1 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 57.5273 | 164.8046 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 57.6289 | 164.9062 | -0.06 | 0.94 | -0.72 | 0.28 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 57.7266 | 165.0039 | -0.12 | 0.88 | -0.66 | 0.34 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 57.8281 | 165.1054 | -0.15 | 0.85 | -0.63 | 0.37 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 57.9297 | 165.207 | -0.15 | 0.85 | -0.61 | 0.39 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 58.0391 | 165.3164 | -0.04 | 0.96 | -0.73 | 0.27 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 58.1367 | 165.414 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:40 | 58.25 | 165.5273 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 58.3477 | 165.625 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 58.4492 | 165.7265 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 58.5469 | 165.8242 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 58.6562 | 165.9335 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 58.7578 | 166.0351 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 58.8594 | 166.1367 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 58.957 | 166.2343 | 0 | 1 | -0.75 | 0.25 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 59.0664 | 166.3437 | -0.01 | 0.99 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 59.168 | 166.4453 | -0.07 | 0.93 | -0.69 | 0.31 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 59.2695 | 166.5468 | -0.12 | 0.88 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 59.3789 | 166.6562 | -0.14 | 0.86 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 59.4766 | 166.7539 | -0.17 | 0.83 | -0.61 | 0.39 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 59.5781 | 166.8554 | -0.04 | 0.96 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 28.32
2019-09-04 | 10:40 | 59.6797 | 166.957 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 59.7891 | 167.0664 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:40 | 59.8867 | 167.164 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 59.9883 | 167.2656 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 60.0898 | 167.3671 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 60.1992 | 167.4765 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 60.2969 | 167.5742 | -0.01 | 0.99 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 60.3984 | 167.6757 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 60.5078 | 167.7851 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 60.6094 | 167.8867 | -0.04 | 0.96 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 28.32
2019-09-04 | 10:40 | 60.707 | 167.9843 | -0.11 | 0.89 | -0.67 | 0.33 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 60.8086 | 168.0859 | -0.16 | 0.84 | -0.63 | 0.37 | -0.62 | 0.38 | 76.17 | 27.34
2019-09-04 | 10:40 | 60.918 | 168.1953 | -0.16 | 0.84 | -0.62 | 0.38 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 61.0195 | 168.2968 | -0.06 | 0.94 | -0.71 | 0.29 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:40 | 61.1172 | 168.3945 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 61.2188 | 168.496 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 61.3281 | 168.6054 | -0.02 | 0.98 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 61.4297 | 168.707 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 61.5391 | 168.8164 | -0.02 | 0.98 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 61.6367 | 168.914 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 61.7383 | 169.0156 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 28.32
2019-09-04 | 10:40 | 61.8398 | 169.1171 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 61.9492 | 169.2265 | -0.01 | 0.99 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 62.0469 | 169.3242 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 62.1484 | 169.4257 | -0.05 | 0.95 | -0.72 | 0.28 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 62.25 | 169.5273 | -0.14 | 0.86 | -0.65 | 0.35 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 62.3477 | 169.625 | -0.18 | 0.82 | -0.61 | 0.39 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 62.457 | 169.7343 | -0.19 | 0.81 | -0.62 | 0.38 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 62.5586 | 169.8359 | -0.06 | 0.94 | -0.73 | 0.27 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 62.668 | 169.9453 | -0.03 | 0.97 | -0.75 | 0.25 | -0.6 | 0.4 | 76.17 | 26.37
2019-09-04 | 10:40 | 62.7695 | 170.0468 | -0.03 | 0.97 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 62.8672 | 170.1445 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 62.9688 | 170.246 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 63.0781 | 170.3554 | -0.02 | 0.98 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 63.1797 | 170.457 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 63.2773 | 170.5546 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 63.3789 | 170.6562 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 63.4883 | 170.7656 | -0.01 | 0.99 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 63.5898 | 170.8671 | 0.01 | 1.01 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 63.6875 | 170.9648 | -0.1 | 0.9 | -0.69 | 0.31 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:40 | 63.7969 | 171.0742 | -0.16 | 0.84 | -0.65 | 0.35 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:40 | 63.8984 | 171.1757 | -0.17 | 0.83 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:40 | 64 | 171.2773 | -0.18 | 0.82 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:40 | 64.0977 | 171.375 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 64.207 | 171.4843 | -0.02 | 0.98 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 64.3086 | 171.5859 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:40 | 64.4062 | 171.6835 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:40 | 64.5078 | 171.7851 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:40 | 64.6172 | 171.8945 | 0 | 1 | -0.75 | 0.25 | -0.64 | 0.36 | 76.17 | 26.37
2019-09-04 | 10:40 | 64.7188 | 171.996 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 64.8164 | 172.0937 | -0.04 | 0.96 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:40 | 64.9297 | 172.207 | -0.01 | 0.99 | -0.77 | 0.23 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 65.0273 | 172.3046 | -0.01 | 0.99 | -0.76 | 0.24 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 65.1289 | 172.4062 | -0.05 | 0.95 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 65.2266 | 172.5039 | -0.11 | 0.89 | -0.67 | 0.33 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 65.3398 | 172.6171 | -0.16 | 0.84 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 65.4375 | 172.7148 | -0.19 | 0.81 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 65.5391 | 172.8164 | -0.05 | 0.95 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 65.6367 | 172.914 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 65.75 | 173.0273 | -0.02 | 0.98 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 65.8477 | 173.125 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 65.9492 | 173.2265 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 66.0586 | 173.3359 | -0.03 | 0.97 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 66.1562 | 173.4335 | -0.03 | 0.97 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 66.2578 | 173.5351 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 66.3594 | 173.6367 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:40 | 66.4688 | 173.746 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 66.5664 | 173.8437 | -0.03 | 0.97 | -0.77 | 0.23 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 66.668 | 173.9453 | -0.11 | 0.89 | -0.69 | 0.31 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 66.7695 | 174.0468 | -0.16 | 0.84 | -0.64 | 0.36 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 66.8789 | 174.1562 | -0.18 | 0.82 | -0.62 | 0.38 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:40 | 66.9766 | 174.2539 | -0.21 | 0.79 | -0.61 | 0.39 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:40 | 67.0781 | 174.3554 | -0.03 | 0.97 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 67.1875 | 174.4648 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 67.2891 | 174.5664 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 67.3867 | 174.664 | -0.03 | 0.97 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 67.5 | 174.7773 | -0.03 | 0.97 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 67.5977 | 174.875 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 67.6992 | 174.9765 | 0 | 1 | -0.75 | 0.25 | -0.66 | 0.34 | 77.15 | 27.34
2019-09-04 | 10:40 | 67.7969 | 175.0742 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 67.8984 | 175.1757 | -0.03 | 0.97 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 68.0078 | 175.2851 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 68.1094 | 175.3867 | -0.01 | 0.99 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 68.207 | 175.4843 | -0.11 | 0.89 | -0.67 | 0.33 | -0.61 | 0.39 | 76.17 | 28.32
2019-09-04 | 10:40 | 68.3086 | 175.5859 | -0.18 | 0.82 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:40 | 68.418 | 175.6953 | -0.18 | 0.82 | -0.6 | 0.4 | -0.6 | 0.4 | 76.17 | 26.37
2019-09-04 | 10:40 | 68.5195 | 175.7968 | -0.05 | 0.95 | -0.71 | 0.29 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:40 | 68.6289 | 175.9062 | -0.03 | 0.97 | -0.74 | 0.26 | -0.6 | 0.4 | 76.17 | 27.34
2019-09-04 | 10:40 | 68.7266 | 176.0039 | -0.04 | 0.96 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 68.8281 | 176.1054 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 68.9297 | 176.207 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:40 | 69.0391 | 176.3164 | -0.03 | 0.97 | -0.75 | 0.25 | -0.61 | 0.39 | 76.17 | 26.37
2019-09-04 | 10:40 | 69.1367 | 176.414 | -0.01 | 0.99 | -0.74 | 0.26 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:40 | 69.2383 | 176.5156 | -0.01 | 0.99 | -0.75 | 0.25 | -0.64 | 0.36 | 76.17 | 27.34
2019-09-04 | 10:40 | 69.3398 | 176.6171 | -0.03 | 0.97 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 69.4492 | 176.7265 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:40 | 69.5469 | 176.8242 | -0.02 | 0.98 | -0.76 | 0.24 | -0.63 | 0.37 | 79.1 | 29.3
2019-09-04 | 10:40 | 69.6484 | 176.9257 | -0.07 | 0.93 | -0.71 | 0.29 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 69.7578 | 177.0351 | -0.13 | 0.87 | -0.65 | 0.35 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 69.8594 | 177.1367 | -0.16 | 0.84 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:40 | 69.957 | 177.2343 | -0.18 | 0.82 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:40 | 70.0586 | 177.3359 | -0.06 | 0.94 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 70.168 | 177.4453 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:40 | 70.2695 | 177.5468 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:40 | 70.3672 | 177.6445 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 26.37
2019-09-04 | 10:40 | 70.4688 | 177.746 | -0.01 | 0.99 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 70.5781 | 177.8554 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 70.6797 | 177.957 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 70.7773 | 178.0546 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 70.8867 | 178.164 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 70.9883 | 178.2656 | -0.02 | 0.98 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:40 | 71.0898 | 178.3671 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 71.1875 | 178.4648 | -0.13 | 0.87 | -0.67 | 0.33 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 71.2969 | 178.5742 | -0.16 | 0.84 | -0.62 | 0.38 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:40 | 71.3984 | 178.6757 | -0.18 | 0.82 | -0.6 | 0.4 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 71.5078 | 178.7851 | -0.17 | 0.83 | -0.59 | 0.41 | -0.59 | 0.41 | 77.15 | 27.34
2019-09-04 | 10:40 | 71.5977 | 178.875 | -0.04 | 0.96 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:40 | 71.707 | 178.9843 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 71.8086 | 179.0859 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 71.918 | 179.1953 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:40 | 72.0195 | 179.2968 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:40 | 72.1172 | 179.3945 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 72.2188 | 179.496 | -0.02 | 0.98 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 72.3281 | 179.6054 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 72.4297 | 179.707 | -0.02 | 0.98 | -0.75 | 0.25 | -0.64 | 0.36 | 78.12 | 25.39
2019-09-04 | 10:40 | 72.5273 | 179.8046 | -0.01 | 0.99 | -0.75 | 0.25 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:40 | 72.6289 | 179.9062 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 72.7266 | 180.0039 | -0.11 | 0.89 | -0.65 | 0.35 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 72.8398 | 180.1171 | -0.16 | 0.84 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 72.9375 | 180.2148 | -0.19 | 0.81 | -0.6 | 0.4 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 73.0469 | 180.3242 | -0.04 | 0.96 | -0.72 | 0.28 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 73.1484 | 180.4257 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 73.25 | 180.5273 | -0.02 | 0.98 | -0.72 | 0.28 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 73.3477 | 180.625 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 73.457 | 180.7343 | 0.02 | 1.02 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 73.5586 | 180.8359 | -0.03 | 0.97 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:40 | 73.6562 | 180.9335 | 0.02 | 1.02 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 73.7578 | 181.0351 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 73.8594 | 181.1367 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 73.9688 | 181.246 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 74.0664 | 181.3437 | 0.02 | 1.02 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 74.1797 | 181.457 | -0.09 | 0.91 | -0.67 | 0.33 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 74.2773 | 181.5546 | -0.14 | 0.86 | -0.63 | 0.37 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:40 | 74.3789 | 181.6562 | -0.17 | 0.83 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:40 | 74.4766 | 181.7539 | -0.19 | 0.81 | -0.59 | 0.41 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:40 | 74.5898 | 181.8671 | -0.05 | 0.95 | -0.72 | 0.28 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 74.6875 | 181.9648 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 74.7891 | 182.0664 | -0.02 | 0.98 | -0.73 | 0.27 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:40 | 74.8984 | 182.1757 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 75 | 182.2773 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:40 | 75.0977 | 182.375 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 75.1992 | 182.4765 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 75.3086 | 182.5859 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 76.17 | 26.37
2019-09-04 | 10:40 | 75.4062 | 182.6835 | -0.01 | 0.99 | -0.74 | 0.26 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 75.5078 | 182.7851 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 75.6094 | 182.8867 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 75.7188 | 182.996 | -0.11 | 0.89 | -0.67 | 0.33 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 75.8164 | 183.0937 | -0.16 | 0.84 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:40 | 75.918 | 183.1953 | -0.16 | 0.84 | -0.62 | 0.38 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:40 | 76.0195 | 183.2968 | -0.08 | 0.92 | -0.69 | 0.31 | -0.6 | 0.4 | 76.17 | 26.37
2019-09-04 | 10:40 | 76.1289 | 183.4062 | -0.01 | 0.99 | -0.72 | 0.28 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 76.2266 | 183.5039 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:40 | 76.3281 | 183.6054 | 0 | 1 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 76.4375 | 183.7148 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 76.5391 | 183.8164 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 76.6367 | 183.914 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 76.7383 | 184.0156 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 76.8477 | 184.125 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 29.3
2019-09-04 | 10:40 | 76.9492 | 184.2265 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:40 | 77.0469 | 184.3242 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 77.1484 | 184.4257 | -0.06 | 0.94 | -0.72 | 0.28 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 77.2578 | 184.5351 | -0.12 | 0.88 | -0.64 | 0.36 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 77.3594 | 184.6367 | -0.16 | 0.84 | -0.6 | 0.4 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 77.457 | 184.7343 | -0.18 | 0.82 | -0.6 | 0.4 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:40 | 77.5664 | 184.8437 | -0.03 | 0.97 | -0.72 | 0.28 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 77.668 | 184.9453 | -0.02 | 0.98 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:40 | 77.7695 | 185.0468 | 0 | 1 | -0.73 | 0.27 | -0.63 | 0.37 | 76.17 | 27.34
2019-09-04 | 10:40 | 77.8789 | 185.1562 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:40 | 77.9766 | 185.2539 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:40 | 78.0781 | 185.3554 | 0.02 | 1.02 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 78.1797 | 185.457 | -0.02 | 0.98 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 78.2773 | 185.5546 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:40 | 78.3867 | 185.664 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 78.4883 | 185.7656 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 78.5898 | 185.8671 | 0.02 | 1.02 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:40 | 78.6875 | 185.9648 | -0.1 | 0.9 | -0.67 | 0.33 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:40 | 78.7969 | 186.0742 | -0.13 | 0.87 | -0.64 | 0.36 | -0.6 | 0.4 | 77.15 | 28.32
2019-09-04 | 10:40 | 78.8984 | 186.1757 | -0.15 | 0.85 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:40 | 79.0078 | 186.2851 | -0.17 | 0.83 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:40 | 79.1094 | 186.3867 | -0.03 | 0.97 | -0.73 | 0.27 | -0.61 | 0.39 | 76.17 | 27.34
2019-09-04 | 10:40 | 79.207 | 186.4843 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:40 | 79.3086 | 186.5859 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:40 | 79.418 | 186.6953 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:40 | 79.5195 | 186.7968 | -0.02 | 0.98 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:40 | 79.6172 | 186.8945 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:40 | 79.7188 | 186.996 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:40 | 79.8281 | 187.1054 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 29.3
2019-09-04 | 10:40 | 79.9297 | 187.207 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:40 | 80.0273 | 187.3046 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:40 | 80.1367 | 187.414 | -0.02 | 0.98 | -0.72 | 0.28 | -0.63 | 0.37 | 79.1 | 28.32
2019-09-04 | 10:40 | 80.2383 | 187.5156 | -0.09 | 0.91 | -0.65 | 0.35 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:40 | 80.3398 | 187.6171 | -0.15 | 0.85 | -0.62 | 0.38 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:40 | 80.4375 | 187.7148 | -0.17 | 0.83 | -0.59 | 0.41 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:40 | 80.5469 | 187.8242 | -0.06 | 0.94 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 80.6484 | 187.9257 | -0.03 | 0.97 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 80.75 | 188.0273 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 80.8477 | 188.125 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 80.957 | 188.2343 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 81.0586 | 188.3359 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 81.1562 | 188.4335 | 0 | 1 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 81.2578 | 188.5351 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 81.3672 | 188.6445 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 81.4688 | 188.746 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 81.5664 | 188.8437 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 81.6797 | 188.957 | -0.07 | 0.93 | -0.69 | 0.31 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 81.7773 | 189.0546 | -0.12 | 0.88 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 81.8867 | 189.164 | -0.17 | 0.83 | -0.6 | 0.4 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:41 | 81.9766 | 189.2539 | -0.17 | 0.83 | -0.6 | 0.4 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 82.0898 | 189.3671 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 82.1875 | 189.4648 | 0 | 1 | -0.72 | 0.28 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 82.2969 | 189.5742 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 82.3984 | 189.6757 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 82.5 | 189.7773 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 82.5977 | 189.875 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 82.6992 | 189.9765 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:41 | 82.8086 | 190.0859 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 82.9062 | 190.1835 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 83.0078 | 190.2851 | 0.01 | 1.01 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:41 | 83.1094 | 190.3867 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 83.2188 | 190.496 | -0.1 | 0.9 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 83.3164 | 190.5937 | -0.13 | 0.87 | -0.62 | 0.38 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 83.4297 | 190.707 | -0.16 | 0.84 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 83.5273 | 190.8046 | -0.08 | 0.92 | -0.67 | 0.33 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 83.6289 | 190.9062 | -0.03 | 0.97 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 83.7266 | 191.0039 | -0.03 | 0.97 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 83.8281 | 191.1054 | -0.01 | 0.99 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 83.9375 | 191.2148 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:41 | 84.0391 | 191.3164 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 84.1367 | 191.414 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 84.25 | 191.5273 | 0 | 1 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 26.37
2019-09-04 | 10:41 | 84.3477 | 191.625 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 80.08 | 28.32
2019-09-04 | 10:41 | 84.4492 | 191.7265 | 0.01 | 1.01 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 84.5586 | 191.8359 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:41 | 84.6562 | 191.9335 | -0.05 | 0.95 | -0.71 | 0.29 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 84.7578 | 192.0351 | -0.12 | 0.88 | -0.64 | 0.36 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 84.8672 | 192.1445 | -0.17 | 0.83 | -0.62 | 0.38 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 84.9688 | 192.246 | -0.19 | 0.81 | -0.59 | 0.41 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 85.0664 | 192.3437 | -0.06 | 0.94 | -0.72 | 0.28 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 85.168 | 192.4453 | -0.03 | 0.97 | -0.73 | 0.27 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 85.2695 | 192.5468 | -0.03 | 0.97 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 85.3789 | 192.6562 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 85.4766 | 192.7539 | -0.04 | 0.96 | -0.75 | 0.25 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 85.5781 | 192.8554 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 85.6875 | 192.9648 | -0.03 | 0.97 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 85.7891 | 193.0664 | -0.02 | 0.98 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 85.8867 | 193.164 | -0.03 | 0.97 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 85.9883 | 193.2656 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 86.0977 | 193.375 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 86.1992 | 193.4765 | -0.12 | 0.88 | -0.67 | 0.33 | -0.62 | 0.38 | 80.08 | 27.34
2019-09-04 | 10:41 | 86.2969 | 193.5742 | -0.15 | 0.85 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:41 | 86.3984 | 193.6757 | -0.2 | 0.8 | -0.62 | 0.38 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 86.5078 | 193.7851 | -0.2 | 0.8 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 86.6094 | 193.8867 | -0.06 | 0.94 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:41 | 86.707 | 193.9843 | -0.03 | 0.97 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 86.8086 | 194.0859 | -0.04 | 0.96 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 86.918 | 194.1953 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 87.0195 | 194.2968 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:41 | 87.1172 | 194.3945 | -0.04 | 0.96 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 87.2266 | 194.5039 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 87.3281 | 194.6054 | -0.03 | 0.97 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 87.4297 | 194.707 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 87.5273 | 194.8046 | -0.01 | 0.99 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:41 | 87.6367 | 194.914 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 87.7383 | 195.0156 | -0.11 | 0.89 | -0.66 | 0.34 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 87.8398 | 195.1171 | -0.17 | 0.83 | -0.62 | 0.38 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 87.9375 | 195.2148 | -0.2 | 0.8 | -0.6 | 0.4 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 88.0469 | 195.3242 | -0.06 | 0.94 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 88.1484 | 195.4257 | -0.04 | 0.96 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 88.25 | 195.5273 | -0.04 | 0.96 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 88.3594 | 195.6367 | -0.04 | 0.96 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 88.457 | 195.7343 | -0.02 | 0.98 | -0.74 | 0.26 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 88.5586 | 195.8359 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 88.6562 | 195.9335 | -0.03 | 0.97 | -0.74 | 0.26 | -0.63 | 0.37 | 79.1 | 26.37
2019-09-04 | 10:41 | 88.7695 | 196.0468 | -0.04 | 0.96 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 88.8672 | 196.1445 | -0.03 | 0.97 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:41 | 88.9688 | 196.246 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 89.0664 | 196.3437 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:41 | 89.1797 | 196.457 | -0.08 | 0.92 | -0.7 | 0.3 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 89.2773 | 196.5546 | -0.12 | 0.88 | -0.65 | 0.35 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 89.3867 | 196.664 | -0.17 | 0.83 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 89.4883 | 196.7656 | -0.18 | 0.82 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 89.5898 | 196.8671 | -0.05 | 0.95 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 89.6875 | 196.9648 | -0.04 | 0.96 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 89.7969 | 197.0742 | -0.02 | 0.98 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 89.8984 | 197.1757 | -0.04 | 0.96 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 90 | 197.2773 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 90.0977 | 197.375 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 90.1992 | 197.4765 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 90.3086 | 197.5859 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 90.4062 | 197.6835 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 90.5195 | 197.7968 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 90.6172 | 197.8945 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 90.7188 | 197.996 | -0.07 | 0.93 | -0.67 | 0.33 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 90.8164 | 198.0937 | -0.15 | 0.85 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 90.9297 | 198.207 | -0.18 | 0.82 | -0.6 | 0.4 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 91.0273 | 198.3046 | -0.11 | 0.89 | -0.65 | 0.35 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 91.1289 | 198.4062 | -0.03 | 0.97 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 91.2266 | 198.5039 | -0.04 | 0.96 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 91.3398 | 198.6171 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 91.4375 | 198.7148 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 91.5391 | 198.8164 | -0.01 | 0.99 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 91.6484 | 198.9257 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 91.75 | 199.0273 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 91.8477 | 199.125 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 91.9492 | 199.2265 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 92.0586 | 199.3359 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 92.1562 | 199.4335 | -0.05 | 0.95 | -0.7 | 0.3 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 92.2578 | 199.5351 | -0.12 | 0.88 | -0.64 | 0.36 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 92.3594 | 199.6367 | -0.19 | 0.81 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 92.4688 | 199.746 | -0.17 | 0.83 | -0.59 | 0.41 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 92.5664 | 199.8437 | -0.04 | 0.96 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 92.668 | 199.9453 | -0.02 | 0.98 | -0.73 | 0.27 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 92.7773 | 200.0546 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 92.8789 | 200.1562 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 92.9766 | 200.2539 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 93.0781 | 200.3554 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 93.1875 | 200.4648 | -0.01 | 0.99 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 93.2891 | 200.5664 | 0 | 1 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 93.3867 | 200.664 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 93.4883 | 200.7656 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 93.5977 | 200.875 | -0.04 | 0.96 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 93.6992 | 200.9765 | -0.1 | 0.9 | -0.69 | 0.31 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 93.8086 | 201.0859 | -0.15 | 0.85 | -0.64 | 0.36 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:41 | 93.9062 | 201.1835 | -0.18 | 0.82 | -0.62 | 0.38 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 94.0078 | 201.2851 | -0.17 | 0.83 | -0.61 | 0.39 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:41 | 94.1094 | 201.3867 | -0.04 | 0.96 | -0.73 | 0.27 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 94.207 | 201.4843 | -0.05 | 0.95 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 94.3164 | 201.5937 | -0.05 | 0.95 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 26.37
2019-09-04 | 10:41 | 94.418 | 201.6953 | -0.05 | 0.95 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 94.5195 | 201.7968 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 94.6172 | 201.8945 | -0.04 | 0.96 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 94.7266 | 202.0039 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 94.8281 | 202.1054 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 94.9297 | 202.207 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 95.0391 | 202.3164 | -0.01 | 0.99 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 95.1367 | 202.414 | -0.05 | 0.95 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 29.3
2019-09-04 | 10:41 | 95.2383 | 202.5156 | -0.15 | 0.85 | -0.65 | 0.35 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 95.3477 | 202.625 | -0.18 | 0.82 | -0.62 | 0.38 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 95.4492 | 202.7265 | -0.18 | 0.82 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 95.5469 | 202.8242 | -0.06 | 0.94 | -0.71 | 0.29 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 95.6484 | 202.9257 | -0.05 | 0.95 | -0.73 | 0.27 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 95.75 | 203.0273 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 95.8594 | 203.1367 | -0.04 | 0.96 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 95.957 | 203.2343 | -0.03 | 0.97 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 96.0586 | 203.3359 | -0.03 | 0.97 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 96.168 | 203.4453 | -0.03 | 0.97 | -0.76 | 0.24 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 96.2695 | 203.5468 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 96.3672 | 203.6445 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 96.4766 | 203.7539 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 96.5781 | 203.8554 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 96.6797 | 203.957 | -0.09 | 0.91 | -0.69 | 0.31 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 96.7773 | 204.0546 | -0.17 | 0.83 | -0.63 | 0.37 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 96.8867 | 204.164 | -0.2 | 0.8 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 96.9883 | 204.2656 | -0.21 | 0.79 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 97.0898 | 204.3671 | -0.06 | 0.94 | -0.73 | 0.27 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 97.1875 | 204.4648 | -0.05 | 0.95 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 97.2969 | 204.5742 | -0.04 | 0.96 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 97.3984 | 204.6757 | -0.04 | 0.96 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 97.5 | 204.7773 | -0.04 | 0.96 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 97.6094 | 204.8867 | -0.02 | 0.98 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 97.707 | 204.9843 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 97.8086 | 205.0859 | -0.03 | 0.97 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 97.9062 | 205.1835 | 0 | 1 | -0.76 | 0.24 | -0.64 | 0.36 | 78.12 | 28.32
2019-09-04 | 10:41 | 98.0195 | 205.2968 | -0.02 | 0.98 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 98.1172 | 205.3945 | -0.02 | 0.98 | -0.76 | 0.24 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 98.2188 | 205.496 | -0.11 | 0.89 | -0.67 | 0.33 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 98.3164 | 205.5937 | -0.14 | 0.86 | -0.65 | 0.35 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 98.4297 | 205.707 | -0.16 | 0.84 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 98.5273 | 205.8046 | -0.16 | 0.84 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 98.6289 | 205.9062 | -0.05 | 0.95 | -0.72 | 0.28 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 98.7383 | 206.0156 | -0.03 | 0.97 | -0.74 | 0.26 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 98.8398 | 206.1171 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:41 | 98.9375 | 206.2148 | -0.02 | 0.98 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 99.0391 | 206.3164 | -0.04 | 0.96 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 99.1484 | 206.4257 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 99.25 | 206.5273 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 99.3477 | 206.625 | -0.01 | 0.99 | -0.76 | 0.24 | -0.63 | 0.37 | 79.1 | 26.37
2019-09-04 | 10:41 | 99.4492 | 206.7265 | -0.02 | 0.98 | -0.76 | 0.24 | -0.64 | 0.36 | 78.12 | 27.34
2019-09-04 | 10:41 | 99.5586 | 206.8359 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:41 | 99.6562 | 206.9335 | -0.04 | 0.96 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:41 | 99.7578 | 207.0351 | -0.14 | 0.86 | -0.66 | 0.34 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 99.8672 | 207.1445 | -0.18 | 0.82 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 99.9688 | 207.246 | -0.18 | 0.82 | -0.61 | 0.39 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:41 | 100.0664 | 207.3437 | -0.06 | 0.94 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 100.168 | 207.4453 | -0.03 | 0.97 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 100.2773 | 207.5546 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 100.3789 | 207.6562 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 100.4766 | 207.7539 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 100.5781 | 207.8554 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 100.6875 | 207.9648 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 100.7891 | 208.0664 | 0 | 1 | -0.76 | 0.24 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 100.8984 | 208.1757 | -0.02 | 0.98 | -0.75 | 0.25 | -0.64 | 0.36 | 78.12 | 26.37
2019-09-04 | 10:41 | 101 | 208.2773 | -0.01 | 0.99 | -0.77 | 0.23 | -0.64 | 0.36 | 78.12 | 27.34
2019-09-04 | 10:41 | 101.0977 | 208.375 | 0.01 | 1.01 | -0.75 | 0.25 | -0.64 | 0.36 | 79.1 | 27.34
2019-09-04 | 10:41 | 101.1992 | 208.4765 | -0.09 | 0.91 | -0.69 | 0.31 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 101.3086 | 208.5859 | -0.14 | 0.86 | -0.65 | 0.35 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 101.4063 | 208.6836 | -0.16 | 0.84 | -0.62 | 0.38 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 101.5078 | 208.7851 | -0.18 | 0.82 | -0.6 | 0.4 | -0.58 | 0.42 | 80.08 | 28.32
2019-09-04 | 10:41 | 101.6094 | 208.8867 | -0.03 | 0.97 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 101.707 | 208.9843 | -0.03 | 0.97 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:41 | 101.8164 | 209.0937 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 101.918 | 209.1953 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:41 | 102.0273 | 209.3046 | -0.02 | 0.98 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 29.3
2019-09-04 | 10:41 | 102.1172 | 209.3945 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 102.2266 | 209.5039 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 102.3281 | 209.6054 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 102.4375 | 209.7148 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 102.5391 | 209.8164 | 0 | 1 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 102.6367 | 209.914 | -0.02 | 0.98 | -0.74 | 0.26 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:41 | 102.7383 | 210.0156 | -0.11 | 0.89 | -0.66 | 0.34 | -0.6 | 0.4 | 77.15 | 28.32
2019-09-04 | 10:41 | 102.8477 | 210.125 | -0.16 | 0.84 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:41 | 102.9492 | 210.2265 | -0.16 | 0.84 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 103.0469 | 210.3242 | -0.05 | 0.95 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 103.1563 | 210.4336 | -0.03 | 0.97 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 103.2578 | 210.5351 | -0.02 | 0.98 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 26.37
2019-09-04 | 10:41 | 103.3594 | 210.6367 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 103.457 | 210.7343 | -0.01 | 0.99 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 103.5664 | 210.8437 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 103.668 | 210.9453 | 0.01 | 1.01 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 103.7695 | 211.0468 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 103.8672 | 211.1445 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 103.9766 | 211.2539 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 79.1 | 28.32
2019-09-04 | 10:41 | 104.0781 | 211.3554 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 104.1797 | 211.457 | -0.07 | 0.93 | -0.72 | 0.28 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 104.2891 | 211.5664 | -0.1 | 0.9 | -0.66 | 0.34 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 104.3867 | 211.664 | -0.15 | 0.85 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 104.4883 | 211.7656 | -0.16 | 0.84 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 104.5898 | 211.8671 | -0.04 | 0.96 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 104.6992 | 211.9765 | -0.03 | 0.97 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 104.7969 | 212.0742 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 104.8984 | 212.1757 | -0.03 | 0.97 | -0.76 | 0.24 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 105 | 212.2773 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 105.1094 | 212.3867 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 105.207 | 212.4843 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 105.3086 | 212.5859 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 78.12 | 27.34
2019-09-04 | 10:41 | 105.418 | 212.6953 | -0.01 | 0.99 | -0.77 | 0.23 | -0.63 | 0.37 | 79.1 | 27.34
2019-09-04 | 10:41 | 105.5195 | 212.7968 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 105.6172 | 212.8945 | 0.01 | 1.01 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 105.7188 | 212.9961 | -0.11 | 0.89 | -0.67 | 0.33 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 105.8281 | 213.1054 | -0.14 | 0.86 | -0.65 | 0.35 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 105.9297 | 213.207 | -0.16 | 0.84 | -0.62 | 0.38 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 106.0273 | 213.3046 | -0.17 | 0.83 | -0.6 | 0.4 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 106.1289 | 213.4062 | -0.02 | 0.98 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 106.2383 | 213.5156 | -0.02 | 0.98 | -0.73 | 0.27 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 106.3398 | 213.6171 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 106.4375 | 213.7148 | 0 | 1 | -0.77 | 0.23 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 106.5469 | 213.8242 | 0 | 1 | -0.74 | 0.26 | -0.63 | 0.37 | 79.1 | 26.37
2019-09-04 | 10:41 | 106.6484 | 213.9257 | 0.01 | 1.01 | -0.76 | 0.24 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 106.75 | 214.0273 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:41 | 106.8594 | 214.1367 | -0.01 | 0.99 | -0.77 | 0.23 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 106.957 | 214.2343 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 107.0586 | 214.3359 | 0.04 | 1.04 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 107.1563 | 214.4336 | -0.04 | 0.96 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 107.2695 | 214.5468 | -0.12 | 0.88 | -0.68 | 0.32 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 107.3672 | 214.6445 | -0.15 | 0.85 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 107.4688 | 214.7461 | -0.19 | 0.81 | -0.62 | 0.38 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 107.5664 | 214.8437 | -0.05 | 0.95 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 107.6797 | 214.957 | -0.02 | 0.98 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 107.7773 | 215.0546 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 107.8789 | 215.1562 | -0.01 | 0.99 | -0.76 | 0.24 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 107.9883 | 215.2656 | 0.01 | 1.01 | -0.76 | 0.24 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 108.0898 | 215.3671 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 108.1875 | 215.4648 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:41 | 108.2891 | 215.5664 | -0.01 | 0.99 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 108.3984 | 215.6757 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:41 | 108.5 | 215.7773 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 108.5977 | 215.875 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 108.6992 | 215.9765 | -0.09 | 0.91 | -0.69 | 0.31 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 108.8086 | 216.0859 | -0.16 | 0.84 | -0.66 | 0.34 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 108.9063 | 216.1836 | -0.16 | 0.84 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:41 | 109.0078 | 216.2851 | -0.17 | 0.83 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 109.1172 | 216.3945 | -0.01 | 0.99 | -0.74 | 0.26 | -0.59 | 0.41 | 77.15 | 27.34
2019-09-04 | 10:41 | 109.2188 | 216.4961 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 109.3164 | 216.5937 | -0.01 | 0.99 | -0.76 | 0.24 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 109.418 | 216.6953 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:41 | 109.5273 | 216.8046 | -0.02 | 0.98 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 109.6289 | 216.9062 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 109.7266 | 217.0039 | 0.02 | 1.02 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:41 | 109.8281 | 217.1054 | 0 | 1 | -0.77 | 0.23 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 109.9375 | 217.2148 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:41 | 110.0391 | 217.3164 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 110.1367 | 217.414 | -0.01 | 0.99 | -0.77 | 0.23 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 110.25 | 217.5273 | -0.11 | 0.89 | -0.68 | 0.32 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 110.3477 | 217.625 | -0.13 | 0.87 | -0.65 | 0.35 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 110.4492 | 217.7265 | -0.17 | 0.83 | -0.63 | 0.37 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 110.5469 | 217.8242 | -0.06 | 0.94 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 110.6563 | 217.9336 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 110.7578 | 218.0351 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 110.8594 | 218.1367 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 110.9688 | 218.2461 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 111.0664 | 218.3437 | 0.01 | 1.01 | -0.77 | 0.23 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 111.168 | 218.4453 | -0.02 | 0.98 | -0.77 | 0.23 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 111.2695 | 218.5468 | 0.01 | 1.01 | -0.77 | 0.23 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 111.3672 | 218.6445 | 0.01 | 1.01 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 28.32
2019-09-04 | 10:41 | 111.4766 | 218.7539 | 0.01 | 1.01 | -0.76 | 0.24 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 111.5781 | 218.8554 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 111.6797 | 218.957 | -0.06 | 0.94 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 111.7891 | 219.0664 | -0.14 | 0.86 | -0.66 | 0.34 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 111.8867 | 219.164 | -0.12 | 0.88 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 111.9883 | 219.2656 | -0.15 | 0.85 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 112.0977 | 219.375 | -0.04 | 0.96 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 112.1992 | 219.4765 | -0.01 | 0.99 | -0.76 | 0.24 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 112.2969 | 219.5742 | -0.03 | 0.97 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 112.4063 | 219.6836 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 112.5078 | 219.7851 | 0 | 1 | -0.77 | 0.23 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 112.6094 | 219.8867 | -0.01 | 0.99 | -0.75 | 0.25 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 112.707 | 219.9843 | 0 | 1 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 112.8164 | 220.0937 | 0 | 1 | -0.77 | 0.23 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 112.918 | 220.1953 | 0.03 | 1.03 | -0.77 | 0.23 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 113.0195 | 220.2968 | 0.02 | 1.02 | -0.77 | 0.23 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 113.1172 | 220.3945 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 77.15 | 27.34
2019-09-04 | 10:41 | 113.2266 | 220.5039 | -0.1 | 0.9 | -0.69 | 0.31 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 113.3281 | 220.6054 | -0.13 | 0.87 | -0.66 | 0.34 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:41 | 113.4297 | 220.707 | -0.14 | 0.86 | -0.65 | 0.35 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 113.5391 | 220.8164 | -0.16 | 0.84 | -0.62 | 0.38 | -0.6 | 0.4 | 79.1 | 26.37
2019-09-04 | 10:41 | 113.6367 | 220.914 | -0.03 | 0.97 | -0.75 | 0.25 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 113.7383 | 221.0156 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 113.8398 | 221.1171 | 0.02 | 1.02 | -0.76 | 0.24 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 113.9492 | 221.2265 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 114.0469 | 221.3242 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 114.1484 | 221.4257 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 114.25 | 221.5273 | 0.01 | 1.01 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 114.3594 | 221.6367 | 0.02 | 1.02 | -0.76 | 0.24 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 114.457 | 221.7343 | 0 | 1 | -0.77 | 0.23 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 114.5586 | 221.8359 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 114.668 | 221.9453 | -0.03 | 0.97 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 28.32
2019-09-04 | 10:41 | 114.7695 | 222.0468 | -0.12 | 0.88 | -0.67 | 0.33 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 114.8672 | 222.1445 | -0.16 | 0.84 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 114.9688 | 222.2461 | -0.15 | 0.85 | -0.62 | 0.38 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:41 | 115.0781 | 222.3554 | -0.03 | 0.97 | -0.73 | 0.27 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 115.1797 | 222.457 | -0.03 | 0.97 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 115.2773 | 222.5546 | 0.02 | 1.02 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 115.3789 | 222.6562 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 115.4883 | 222.7656 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 115.5898 | 222.8671 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 115.6875 | 222.9648 | 0 | 1 | -0.76 | 0.24 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 115.7891 | 223.0664 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:41 | 115.8984 | 223.1757 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:41 | 116 | 223.2773 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 116.0977 | 223.375 | 0.03 | 1.03 | -0.76 | 0.24 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 116.207 | 223.4843 | -0.06 | 0.94 | -0.7 | 0.3 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 116.3086 | 223.5859 | -0.12 | 0.88 | -0.64 | 0.36 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:41 | 116.4063 | 223.6836 | -0.16 | 0.84 | -0.63 | 0.37 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:41 | 116.5195 | 223.7968 | -0.17 | 0.83 | -0.61 | 0.39 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 116.6172 | 223.8945 | -0.03 | 0.97 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 116.7188 | 223.9961 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 116.8164 | 224.0937 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 116.918 | 224.1953 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:41 | 117.0273 | 224.3046 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 117.1289 | 224.4062 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 117.2383 | 224.5156 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 117.3398 | 224.6171 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 117.4375 | 224.7148 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 117.5391 | 224.8164 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 117.6367 | 224.914 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 26.37
2019-09-04 | 10:41 | 117.75 | 225.0273 | -0.11 | 0.89 | -0.66 | 0.34 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 117.8477 | 225.125 | -0.14 | 0.86 | -0.62 | 0.38 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 117.9492 | 225.2265 | -0.17 | 0.83 | -0.6 | 0.4 | -0.6 | 0.4 | 80.08 | 29.3
2019-09-04 | 10:41 | 118.0586 | 225.3359 | -0.08 | 0.92 | -0.67 | 0.33 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 118.1563 | 225.4336 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 118.2578 | 225.5351 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 118.3594 | 225.6367 | 0.02 | 1.02 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 118.4688 | 225.7461 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 118.5664 | 225.8437 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 118.668 | 225.9453 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 118.7773 | 226.0546 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 118.8789 | 226.1562 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 118.9766 | 226.2539 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 119.0781 | 226.3554 | 0 | 1 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 119.1875 | 226.4648 | -0.05 | 0.95 | -0.68 | 0.32 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 119.2891 | 226.5664 | -0.12 | 0.88 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 119.3867 | 226.664 | -0.16 | 0.84 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 119.5 | 226.7773 | -0.17 | 0.83 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 26.37
2019-09-04 | 10:41 | 119.5977 | 226.875 | -0.03 | 0.97 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 119.6992 | 226.9765 | -0.04 | 0.96 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 119.7969 | 227.0742 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 119.9063 | 227.1836 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:41 | 120.0078 | 227.2851 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 120.1094 | 227.3867 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 120.207 | 227.4843 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 120.3164 | 227.5937 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 120.418 | 227.6953 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 120.5195 | 227.7968 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 120.6289 | 227.9062 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 120.7266 | 228.0039 | -0.09 | 0.91 | -0.67 | 0.33 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:41 | 120.8281 | 228.1054 | -0.13 | 0.87 | -0.63 | 0.37 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 120.9297 | 228.207 | -0.17 | 0.83 | -0.6 | 0.4 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 121.0391 | 228.3164 | -0.17 | 0.83 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:41 | 121.1367 | 228.414 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 121.2383 | 228.5156 | -0.03 | 0.97 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 121.3398 | 228.6171 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 121.4492 | 228.7265 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 77.15 | 26.37
2019-09-04 | 10:41 | 121.5469 | 228.8242 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 121.6484 | 228.9257 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 121.7578 | 229.0351 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 121.8594 | 229.1367 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 121.957 | 229.2343 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 122.0664 | 229.3437 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 122.168 | 229.4453 | -0.03 | 0.97 | -0.71 | 0.29 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 122.2695 | 229.5468 | -0.11 | 0.89 | -0.64 | 0.36 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 122.3672 | 229.6445 | -0.15 | 0.85 | -0.61 | 0.39 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:41 | 122.4688 | 229.7461 | -0.17 | 0.83 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 122.5781 | 229.8554 | -0.04 | 0.96 | -0.7 | 0.3 | -0.59 | 0.41 | 77.15 | 27.34
2019-09-04 | 10:41 | 122.6797 | 229.957 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 77.15 | 29.3
2019-09-04 | 10:41 | 122.7891 | 230.0664 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 122.8867 | 230.164 | -0.02 | 0.98 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 122.9883 | 230.2656 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 123.0898 | 230.3671 | -0.01 | 0.99 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 123.1992 | 230.4765 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 77.15 | 28.32
2019-09-04 | 10:41 | 123.2969 | 230.5742 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 123.3984 | 230.6757 | 0.03 | 1.03 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 123.5078 | 230.7851 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 123.5977 | 230.875 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:41 | 123.707 | 230.9843 | -0.07 | 0.93 | -0.68 | 0.32 | -0.61 | 0.39 | 79.1 | 26.37
2019-09-04 | 10:41 | 123.8086 | 231.0859 | -0.13 | 0.87 | -0.62 | 0.38 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 123.9063 | 231.1836 | -0.14 | 0.86 | -0.6 | 0.4 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 124.0195 | 231.2968 | -0.18 | 0.82 | -0.59 | 0.41 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:41 | 124.1172 | 231.3945 | -0.03 | 0.97 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 124.2188 | 231.4961 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 124.3281 | 231.6054 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 124.4297 | 231.707 | -0.02 | 0.98 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 124.5273 | 231.8046 | -0.01 | 0.99 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 124.6289 | 231.9062 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:41 | 124.7383 | 232.0156 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 124.8398 | 232.1171 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 124.9375 | 232.2148 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 125.0391 | 232.3164 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 125.1484 | 232.4257 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 125.25 | 232.5273 | -0.11 | 0.89 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:41 | 125.3477 | 232.625 | -0.13 | 0.87 | -0.62 | 0.38 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 125.457 | 232.7343 | -0.18 | 0.82 | -0.59 | 0.41 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 125.5586 | 232.8359 | -0.09 | 0.91 | -0.65 | 0.35 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 125.6563 | 232.9336 | -0.03 | 0.97 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 125.7578 | 233.0351 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 125.8672 | 233.1445 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 125.9688 | 233.2461 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 126.0664 | 233.3437 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 126.168 | 233.4453 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 126.2773 | 233.5546 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 126.3789 | 233.6562 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 126.4766 | 233.7539 | 0.02 | 1.02 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 126.5898 | 233.8671 | 0.01 | 1.01 | -0.75 | 0.25 | -0.64 | 0.36 | 77.15 | 27.34
2019-09-04 | 10:41 | 126.6875 | 233.9648 | -0.04 | 0.96 | -0.68 | 0.32 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 126.7891 | 234.0664 | -0.14 | 0.86 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 126.8867 | 234.164 | -0.17 | 0.83 | -0.61 | 0.39 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 127 | 234.2773 | -0.17 | 0.83 | -0.58 | 0.42 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 127.0977 | 234.375 | -0.04 | 0.96 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 127.1992 | 234.4765 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 127.2969 | 234.5742 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 127.4063 | 234.6836 | -0.02 | 0.98 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 127.5078 | 234.7851 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 127.6094 | 234.8867 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 26.37
2019-09-04 | 10:41 | 127.7188 | 234.9961 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 127.8164 | 235.0937 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 127.918 | 235.1953 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 29.3
2019-09-04 | 10:41 | 128.0195 | 235.2968 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 128.1289 | 235.4062 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 128.2266 | 235.5039 | -0.11 | 0.89 | -0.65 | 0.35 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:41 | 128.3281 | 235.6054 | -0.13 | 0.87 | -0.62 | 0.38 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 128.4297 | 235.707 | -0.15 | 0.85 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 128.5391 | 235.8164 | -0.17 | 0.83 | -0.57 | 0.43 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:41 | 128.6367 | 235.914 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 26.37
2019-09-04 | 10:41 | 128.75 | 236.0273 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 128.8477 | 236.125 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 128.9492 | 236.2265 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 129.0469 | 236.3242 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 129.1563 | 236.4336 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 129.2578 | 236.5351 | -0.01 | 0.99 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 129.3594 | 236.6367 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 129.457 | 236.7343 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 129.5664 | 236.8437 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 26.37
2019-09-04 | 10:41 | 129.668 | 236.9453 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 26.37
2019-09-04 | 10:41 | 129.7695 | 237.0468 | -0.1 | 0.9 | -0.64 | 0.36 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 129.8789 | 237.1562 | -0.13 | 0.87 | -0.63 | 0.37 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:41 | 129.9766 | 237.2539 | -0.15 | 0.85 | -0.58 | 0.42 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:41 | 130.0781 | 237.3554 | -0.04 | 0.96 | -0.69 | 0.31 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 130.1797 | 237.457 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 130.2891 | 237.5664 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 130.3867 | 237.664 | 0 | 1 | -0.71 | 0.29 | -0.59 | 0.41 | 77.15 | 27.34
2019-09-04 | 10:41 | 130.4883 | 237.7656 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 130.5898 | 237.8671 | 0.01 | 1.01 | -0.73 | 0.27 | -0.63 | 0.37 | 79.1 | 27.34
2019-09-04 | 10:41 | 130.6992 | 237.9765 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 130.7969 | 238.0742 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 130.8984 | 238.1757 | 0 | 1 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:41 | 131 | 238.2773 | 0.03 | 1.03 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 131.1094 | 238.3867 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 131.207 | 238.4843 | -0.05 | 0.95 | -0.69 | 0.31 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 131.3086 | 238.5859 | -0.09 | 0.91 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 131.418 | 238.6953 | -0.15 | 0.85 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 131.5195 | 238.7968 | -0.16 | 0.84 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 131.6172 | 238.8945 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 131.7188 | 238.9961 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 131.8281 | 239.1054 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 131.9297 | 239.207 | 0.02 | 1.02 | -0.71 | 0.29 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 132.0273 | 239.3046 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 26.37
2019-09-04 | 10:41 | 132.1367 | 239.414 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 132.2383 | 239.5156 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 132.3398 | 239.6171 | 0.04 | 1.04 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 132.4492 | 239.7265 | 0.01 | 1.01 | -0.72 | 0.28 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 132.5469 | 239.8242 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 77.15 | 27.34
2019-09-04 | 10:41 | 132.6484 | 239.9257 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 132.75 | 240.0273 | -0.1 | 0.9 | -0.65 | 0.35 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:41 | 132.8477 | 240.125 | -0.16 | 0.84 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 132.957 | 240.2343 | -0.15 | 0.85 | -0.59 | 0.41 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 133.0586 | 240.3359 | -0.13 | 0.87 | -0.64 | 0.36 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 133.1563 | 240.4336 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 26.37
2019-09-04 | 10:41 | 133.2578 | 240.5351 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 133.3672 | 240.6445 | -0.03 | 0.97 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 133.4688 | 240.7461 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 30.27
2019-09-04 | 10:41 | 133.5664 | 240.8437 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 133.6797 | 240.957 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:41 | 133.7773 | 241.0546 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 133.8867 | 241.164 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:41 | 133.9766 | 241.2539 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 134.0898 | 241.3671 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 134.1875 | 241.4648 | -0.04 | 0.96 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:41 | 134.2891 | 241.5664 | -0.14 | 0.86 | -0.65 | 0.35 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 134.3867 | 241.664 | -0.14 | 0.86 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 134.5 | 241.7773 | -0.17 | 0.83 | -0.6 | 0.4 | -0.58 | 0.42 | 79.1 | 26.37
2019-09-04 | 10:41 | 134.5977 | 241.875 | -0.05 | 0.95 | -0.71 | 0.29 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 134.707 | 241.9843 | -0.04 | 0.96 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 134.8086 | 242.0859 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 26.37
2019-09-04 | 10:41 | 134.9063 | 242.1836 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 135.0078 | 242.2851 | -0.02 | 0.98 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 135.1172 | 242.3945 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 135.2188 | 242.4961 | -0.01 | 0.99 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 135.3164 | 242.5937 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:41 | 135.418 | 242.6953 | -0.02 | 0.98 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:41 | 135.5195 | 242.7968 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 135.6289 | 242.9062 | 0.01 | 1.01 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:41 | 135.7266 | 243.0039 | -0.09 | 0.91 | -0.66 | 0.34 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:41 | 135.8398 | 243.1171 | -0.15 | 0.85 | -0.62 | 0.38 | -0.6 | 0.4 | 80.08 | 26.37
2019-09-04 | 10:41 | 135.9375 | 243.2148 | -0.15 | 0.85 | -0.6 | 0.4 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 136.0391 | 243.3164 | -0.16 | 0.84 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:41 | 136.1367 | 243.414 | -0.04 | 0.96 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:41 | 136.25 | 243.5273 | -0.04 | 0.96 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:41 | 136.3477 | 243.625 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 136.4492 | 243.7265 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:41 | 136.5469 | 243.8242 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 136.6563 | 243.9336 | -0.03 | 0.97 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:41 | 136.7578 | 244.0351 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 136.8594 | 244.1367 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 136.9688 | 244.2461 | -0.02 | 0.98 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 137.0664 | 244.3437 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:41 | 137.168 | 244.4453 | -0.02 | 0.98 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:41 | 137.2695 | 244.5468 | -0.12 | 0.88 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 137.3789 | 244.6562 | -0.18 | 0.82 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 137.4766 | 244.7539 | -0.18 | 0.82 | -0.58 | 0.42 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 137.5781 | 244.8554 | -0.07 | 0.93 | -0.68 | 0.32 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:41 | 137.6797 | 244.957 | -0.04 | 0.96 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:41 | 137.7891 | 245.0664 | -0.04 | 0.96 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 137.8867 | 245.164 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:41 | 138 | 245.2773 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 138.0977 | 245.375 | -0.04 | 0.96 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 138.1992 | 245.4765 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 138.2969 | 245.5742 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 138.3984 | 245.6757 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 138.5078 | 245.7851 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:41 | 138.6094 | 245.8867 | 0 | 1 | -0.73 | 0.27 | -0.63 | 0.37 | 80.08 | 28.32
2019-09-04 | 10:41 | 138.707 | 245.9843 | -0.07 | 0.93 | -0.68 | 0.32 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 138.8086 | 246.0859 | -0.13 | 0.87 | -0.64 | 0.36 | -0.61 | 0.39 | 80.08 | 29.3
2019-09-04 | 10:41 | 138.918 | 246.1953 | -0.17 | 0.83 | -0.58 | 0.42 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:41 | 139.0195 | 246.2968 | -0.19 | 0.81 | -0.59 | 0.41 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:41 | 139.1172 | 246.3945 | -0.04 | 0.96 | -0.69 | 0.31 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:41 | 139.2266 | 246.5039 | -0.03 | 0.97 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:41 | 139.3281 | 246.6054 | -0.03 | 0.97 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:41 | 139.4297 | 246.707 | -0.03 | 0.97 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:41 | 139.5391 | 246.8164 | -0.03 | 0.97 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 139.6367 | 246.914 | -0.02 | 0.98 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 139.7383 | 247.0156 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 139.8398 | 247.1171 | -0.02 | 0.98 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:42 | 139.9375 | 247.2148 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 140.0469 | 247.3242 | -0.01 | 0.99 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 140.1484 | 247.4257 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:42 | 140.25 | 247.5273 | -0.11 | 0.89 | -0.66 | 0.34 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 140.3594 | 247.6367 | -0.15 | 0.85 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 140.457 | 247.7343 | -0.15 | 0.85 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 140.5586 | 247.8359 | -0.17 | 0.83 | -0.59 | 0.41 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 140.668 | 247.9453 | -0.04 | 0.96 | -0.7 | 0.3 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:42 | 140.7695 | 248.0468 | -0.03 | 0.97 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 140.8672 | 248.1445 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 140.9688 | 248.2461 | -0.02 | 0.98 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 26.37
2019-09-04 | 10:42 | 141.0781 | 248.3554 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 81.05 | 29.3
2019-09-04 | 10:42 | 141.1797 | 248.457 | 0.02 | 1.02 | -0.73 | 0.27 | -0.62 | 0.38 | 80.08 | 27.34
2019-09-04 | 10:42 | 141.2773 | 248.5546 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 141.3789 | 248.6562 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 141.4883 | 248.7656 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 141.5898 | 248.8671 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:42 | 141.6875 | 248.9648 | -0.05 | 0.95 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 141.7969 | 249.0742 | -0.13 | 0.87 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 141.8984 | 249.1757 | -0.16 | 0.84 | -0.61 | 0.39 | -0.59 | 0.41 | 80.08 | 30.27
2019-09-04 | 10:42 | 142 | 249.2773 | -0.16 | 0.84 | -0.59 | 0.41 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 142.0977 | 249.375 | -0.05 | 0.95 | -0.71 | 0.29 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 142.207 | 249.4843 | -0.03 | 0.97 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 142.3086 | 249.5859 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 142.4063 | 249.6836 | -0.03 | 0.97 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 142.5078 | 249.7851 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 142.6172 | 249.8945 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 142.7188 | 249.9961 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 142.8164 | 250.0937 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 142.9297 | 250.207 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 143.0273 | 250.3046 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 143.1289 | 250.4062 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 143.2266 | 250.5039 | -0.09 | 0.91 | -0.66 | 0.34 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 143.3398 | 250.6171 | -0.15 | 0.85 | -0.62 | 0.38 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 143.4375 | 250.7148 | -0.15 | 0.85 | -0.61 | 0.39 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 143.5391 | 250.8164 | -0.17 | 0.83 | -0.59 | 0.41 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 143.6367 | 250.914 | -0.04 | 0.96 | -0.73 | 0.27 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 143.75 | 251.0273 | -0.01 | 0.99 | -0.73 | 0.27 | -0.6 | 0.4 | 81.05 | 28.32
2019-09-04 | 10:42 | 143.8477 | 251.125 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 30.27
2019-09-04 | 10:42 | 143.9492 | 251.2265 | 0 | 1 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 144.0469 | 251.3242 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 144.1563 | 251.4336 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 144.2578 | 251.5351 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 144.3594 | 251.6367 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 144.4688 | 251.7461 | 0.02 | 1.02 | -0.75 | 0.25 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 144.5664 | 251.8437 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 144.668 | 251.9453 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 144.7695 | 252.0468 | -0.11 | 0.89 | -0.67 | 0.33 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 144.8789 | 252.1562 | -0.15 | 0.85 | -0.62 | 0.38 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 144.9766 | 252.2539 | -0.15 | 0.85 | -0.62 | 0.38 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 145.0898 | 252.3671 | -0.05 | 0.95 | -0.69 | 0.31 | -0.59 | 0.41 | 79.1 | 26.37
2019-09-04 | 10:42 | 145.1875 | 252.4648 | -0.03 | 0.97 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 26.37
2019-09-04 | 10:42 | 145.2891 | 252.5664 | -0.03 | 0.97 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 145.3867 | 252.664 | -0.01 | 0.99 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 145.5 | 252.7773 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 145.5977 | 252.875 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 145.6992 | 252.9765 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 145.7969 | 253.0742 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 145.8984 | 253.1757 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 146.0078 | 253.2851 | 0 | 1 | -0.76 | 0.24 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 146.1094 | 253.3867 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 146.2188 | 253.4961 | -0.05 | 0.95 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:42 | 146.3164 | 253.5937 | -0.11 | 0.89 | -0.66 | 0.34 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 146.418 | 253.6953 | -0.17 | 0.83 | -0.63 | 0.37 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 146.5195 | 253.7968 | -0.15 | 0.85 | -0.61 | 0.39 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 146.6289 | 253.9062 | -0.02 | 0.98 | -0.71 | 0.29 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 146.7266 | 254.0039 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 146.8281 | 254.1054 | 0 | 1 | -0.73 | 0.27 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:42 | 146.9297 | 254.207 | -0.01 | 0.99 | -0.74 | 0.26 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 147.0391 | 254.3164 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 147.1367 | 254.414 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 147.2383 | 254.5156 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 147.3477 | 254.625 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 147.4492 | 254.7265 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 147.5469 | 254.8242 | 0 | 1 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 147.6484 | 254.9257 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 147.7578 | 255.0351 | -0.09 | 0.91 | -0.68 | 0.32 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 147.8594 | 255.1367 | -0.14 | 0.86 | -0.63 | 0.37 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:42 | 147.957 | 255.2343 | -0.17 | 0.83 | -0.61 | 0.39 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 148.0586 | 255.3359 | -0.17 | 0.83 | -0.6 | 0.4 | -0.59 | 0.41 | 81.05 | 28.32
2019-09-04 | 10:42 | 148.168 | 255.4453 | -0.02 | 0.98 | -0.73 | 0.27 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 148.2695 | 255.5468 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 148.3672 | 255.6445 | -0.02 | 0.98 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 148.4766 | 255.7539 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 148.5781 | 255.8554 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 148.6797 | 255.957 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 148.7773 | 256.0546 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:42 | 148.8867 | 256.164 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 148.9883 | 256.2656 | -0.01 | 0.99 | -0.76 | 0.24 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 149.0898 | 256.3671 | 0.02 | 1.02 | -0.75 | 0.25 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:42 | 149.1875 | 256.4648 | -0.01 | 0.99 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:42 | 149.2969 | 256.5742 | -0.11 | 0.89 | -0.65 | 0.35 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 149.3984 | 256.6757 | -0.15 | 0.85 | -0.62 | 0.38 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 149.5 | 256.7773 | -0.15 | 0.85 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 149.5977 | 256.875 | -0.05 | 0.95 | -0.72 | 0.28 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 149.707 | 256.9843 | -0.03 | 0.97 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 149.8164 | 257.0937 | -0.02 | 0.98 | -0.73 | 0.27 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 149.9063 | 257.1836 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 150.0195 | 257.2968 | -0.02 | 0.98 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 150.1172 | 257.3945 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 30.27
2019-09-04 | 10:42 | 150.2188 | 257.4961 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 150.3164 | 257.5937 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 150.4297 | 257.707 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 150.5273 | 257.8046 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 79.1 | 27.34
2019-09-04 | 10:42 | 150.6289 | 257.9062 | 0.01 | 1.01 | -0.75 | 0.25 | -0.63 | 0.37 | 79.1 | 27.34
2019-09-04 | 10:42 | 150.7266 | 258.0039 | -0.06 | 0.94 | -0.7 | 0.3 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 150.8398 | 258.1171 | -0.13 | 0.87 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 150.9375 | 258.2148 | -0.16 | 0.84 | -0.63 | 0.37 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 151.0391 | 258.3164 | -0.16 | 0.84 | -0.6 | 0.4 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 151.1484 | 258.4257 | -0.04 | 0.96 | -0.73 | 0.27 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 151.25 | 258.5273 | -0.03 | 0.97 | -0.74 | 0.26 | -0.61 | 0.39 | 82.03 | 27.34
2019-09-04 | 10:42 | 151.3477 | 258.625 | -0.02 | 0.98 | -0.74 | 0.26 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 151.4492 | 258.7265 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 151.5586 | 258.8359 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 151.6563 | 258.9336 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 151.7578 | 259.0351 | -0.01 | 0.99 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 151.8594 | 259.1367 | 0 | 1 | -0.75 | 0.25 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 151.9688 | 259.2461 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 152.0664 | 259.3437 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:42 | 152.1797 | 259.457 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 152.2773 | 259.5546 | -0.11 | 0.89 | -0.65 | 0.35 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 152.3789 | 259.6562 | -0.17 | 0.83 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 152.4766 | 259.7539 | -0.18 | 0.82 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 152.5898 | 259.8671 | -0.09 | 0.91 | -0.69 | 0.31 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 152.6875 | 259.9648 | -0.03 | 0.97 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 152.7891 | 260.0664 | -0.02 | 0.98 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 152.8867 | 260.164 | -0.03 | 0.97 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 152.9883 | 260.2656 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 153.0977 | 260.375 | -0.03 | 0.97 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 153.1992 | 260.4765 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 153.3086 | 260.5859 | -0.02 | 0.98 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 153.4063 | 260.6836 | -0.01 | 0.99 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 153.5078 | 260.7851 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 153.6094 | 260.8867 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 153.7188 | 260.9961 | -0.04 | 0.96 | -0.7 | 0.3 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 153.8164 | 261.0937 | -0.14 | 0.86 | -0.64 | 0.36 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 153.918 | 261.1953 | -0.16 | 0.84 | -0.61 | 0.39 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 154.0195 | 261.2968 | -0.18 | 0.82 | -0.59 | 0.41 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:42 | 154.1289 | 261.4062 | -0.04 | 0.96 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 154.2266 | 261.5039 | -0.03 | 0.97 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 154.3281 | 261.6054 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 154.4375 | 261.7148 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 154.5391 | 261.8164 | -0.04 | 0.96 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 154.6367 | 261.914 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 154.7383 | 262.0156 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 154.8477 | 262.125 | -0.01 | 0.99 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 154.9492 | 262.2265 | 0 | 1 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 155.0469 | 262.3242 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:42 | 155.1484 | 262.4257 | -0.02 | 0.98 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 155.2578 | 262.5351 | -0.1 | 0.9 | -0.66 | 0.34 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 155.3594 | 262.6367 | -0.17 | 0.83 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 155.457 | 262.7343 | -0.17 | 0.83 | -0.61 | 0.39 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 155.5664 | 262.8437 | -0.16 | 0.84 | -0.61 | 0.39 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 155.668 | 262.9453 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 26.37
2019-09-04 | 10:42 | 155.7695 | 263.0468 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 155.8789 | 263.1562 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 30.27
2019-09-04 | 10:42 | 155.9766 | 263.2539 | -0.02 | 0.98 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 156.0781 | 263.3554 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 156.1797 | 263.457 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 156.2773 | 263.5546 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 156.3867 | 263.664 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 156.4883 | 263.7656 | -0.01 | 0.99 | -0.76 | 0.24 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 156.5898 | 263.8671 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 156.6992 | 263.9765 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 80.08 | 30.27
2019-09-04 | 10:42 | 156.7969 | 264.0742 | -0.11 | 0.89 | -0.66 | 0.34 | -0.61 | 0.39 | 81.05 | 28.32
2019-09-04 | 10:42 | 156.8984 | 264.1757 | -0.15 | 0.85 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 157.0078 | 264.2851 | -0.16 | 0.84 | -0.61 | 0.39 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 157.1094 | 264.3867 | -0.04 | 0.96 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 157.207 | 264.4843 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 157.3086 | 264.5859 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 157.4063 | 264.6836 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 157.5195 | 264.7968 | -0.01 | 0.99 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 157.6172 | 264.8945 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 157.7188 | 264.9961 | -0.02 | 0.98 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 157.8164 | 265.0937 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:42 | 157.9297 | 265.207 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 158.0273 | 265.3046 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 158.1289 | 265.4062 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 30.27
2019-09-04 | 10:42 | 158.2383 | 265.5156 | -0.07 | 0.93 | -0.68 | 0.32 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 158.3398 | 265.6171 | -0.12 | 0.88 | -0.64 | 0.36 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 158.4375 | 265.7148 | -0.14 | 0.86 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 158.5469 | 265.8242 | -0.15 | 0.85 | -0.61 | 0.39 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 158.6484 | 265.9257 | -0.03 | 0.97 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 158.75 | 266.0273 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 158.8477 | 266.125 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 158.957 | 266.2343 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 159.0586 | 266.3359 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 159.1563 | 266.4336 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 159.2578 | 266.5351 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 159.3672 | 266.6445 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 159.4688 | 266.7461 | 0.01 | 1.01 | -0.76 | 0.24 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 159.5664 | 266.8437 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 159.6797 | 266.957 | 0 | 1 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 159.7773 | 267.0546 | -0.1 | 0.9 | -0.66 | 0.34 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 159.8789 | 267.1562 | -0.13 | 0.87 | -0.62 | 0.38 | -0.6 | 0.4 | 81.05 | 28.32
2019-09-04 | 10:42 | 159.9766 | 267.2539 | -0.14 | 0.86 | -0.61 | 0.39 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:42 | 160.0898 | 267.3671 | -0.05 | 0.95 | -0.67 | 0.33 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 160.1875 | 267.4648 | -0.01 | 0.99 | -0.73 | 0.27 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 160.2891 | 267.5664 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 160.3984 | 267.6757 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 160.5 | 267.7773 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 160.5977 | 267.875 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 160.6992 | 267.9765 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 160.8086 | 268.0859 | 0.03 | 1.03 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 160.9063 | 268.1836 | 0.03 | 1.03 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 161.0078 | 268.2851 | 0.02 | 1.02 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:42 | 161.1094 | 268.3867 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 161.2188 | 268.4961 | -0.02 | 0.98 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 161.3164 | 268.5937 | -0.11 | 0.89 | -0.65 | 0.35 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 161.418 | 268.6953 | -0.13 | 0.87 | -0.63 | 0.37 | -0.59 | 0.41 | 81.05 | 28.32
2019-09-04 | 10:42 | 161.5273 | 268.8046 | -0.17 | 0.83 | -0.61 | 0.39 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:42 | 161.6289 | 268.9062 | -0.03 | 0.97 | -0.72 | 0.28 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:42 | 161.7266 | 269.0039 | 0.01 | 1.01 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 161.8281 | 269.1054 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 161.9375 | 269.2148 | 0.01 | 1.01 | -0.74 | 0.26 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 162.0391 | 269.3164 | 0 | 1 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:42 | 162.1367 | 269.414 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:42 | 162.2383 | 269.5156 | 0.03 | 1.03 | -0.75 | 0.25 | -0.62 | 0.38 | 79.1 | 29.3
2019-09-04 | 10:42 | 162.3477 | 269.625 | -0.01 | 0.99 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 162.4492 | 269.7265 | 0.01 | 1.01 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 162.5469 | 269.8242 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 162.6484 | 269.9257 | 0.01 | 1.01 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:42 | 162.7578 | 270.0351 | -0.07 | 0.93 | -0.69 | 0.31 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 162.8594 | 270.1367 | -0.13 | 0.87 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 162.9688 | 270.2461 | -0.13 | 0.87 | -0.62 | 0.38 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:42 | 163.0664 | 270.3437 | -0.16 | 0.84 | -0.6 | 0.4 | -0.58 | 0.42 | 79.1 | 28.32
2019-09-04 | 10:42 | 163.168 | 270.4453 | 0 | 1 | -0.71 | 0.29 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 163.2695 | 270.5468 | -0.01 | 0.99 | -0.73 | 0.27 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 163.3672 | 270.6445 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:42 | 163.4766 | 270.7539 | 0.01 | 1.01 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 163.5781 | 270.8554 | 0 | 1 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 163.6797 | 270.957 | 0.01 | 1.01 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 163.7773 | 271.0546 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 163.8867 | 271.164 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 163.9883 | 271.2656 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 164.0977 | 271.375 | 0.02 | 1.02 | -0.75 | 0.25 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 164.1992 | 271.4765 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 164.2969 | 271.5742 | -0.1 | 0.9 | -0.65 | 0.35 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 164.3984 | 271.6757 | -0.11 | 0.89 | -0.63 | 0.37 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 164.5078 | 271.7851 | -0.15 | 0.85 | -0.61 | 0.39 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:42 | 164.6094 | 271.8867 | 0 | 1 | -0.71 | 0.29 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 164.707 | 271.9843 | 0 | 1 | -0.72 | 0.28 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 164.8086 | 272.0859 | 0.01 | 1.01 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 164.918 | 272.1953 | 0 | 1 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 165.0195 | 272.2968 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:42 | 165.1172 | 272.3945 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:42 | 165.2266 | 272.5039 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 165.3281 | 272.6054 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 165.4297 | 272.707 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 165.5273 | 272.8046 | 0.01 | 1.01 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 165.6367 | 272.914 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 165.7383 | 273.0156 | -0.06 | 0.94 | -0.69 | 0.31 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:42 | 165.8398 | 273.1171 | -0.1 | 0.9 | -0.65 | 0.35 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 165.9375 | 273.2148 | -0.16 | 0.84 | -0.6 | 0.4 | -0.6 | 0.4 | 80.08 | 29.3
2019-09-04 | 10:42 | 166.0469 | 273.3242 | -0.18 | 0.82 | -0.58 | 0.42 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 166.1484 | 273.4257 | -0.03 | 0.97 | -0.72 | 0.28 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 166.25 | 273.5273 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 166.3594 | 273.6367 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 166.457 | 273.7343 | 0.04 | 1.04 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 166.5586 | 273.8359 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 166.6563 | 273.9336 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 166.7695 | 274.0468 | 0.02 | 1.02 | -0.74 | 0.26 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 166.8672 | 274.1445 | 0.03 | 1.03 | -0.73 | 0.27 | -0.61 | 0.39 | 80.08 | 29.3
2019-09-04 | 10:42 | 166.9688 | 274.2461 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 167.0664 | 274.3437 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 81.05 | 28.32
2019-09-04 | 10:42 | 167.1797 | 274.457 | 0.03 | 1.03 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 167.2773 | 274.5546 | -0.06 | 0.94 | -0.67 | 0.33 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 167.3789 | 274.6562 | -0.11 | 0.89 | -0.64 | 0.36 | -0.61 | 0.39 | 77.15 | 27.34
2019-09-04 | 10:42 | 167.4883 | 274.7656 | -0.15 | 0.85 | -0.61 | 0.39 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 167.5898 | 274.8671 | -0.09 | 0.91 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 167.6875 | 274.9648 | -0.02 | 0.98 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 167.7891 | 275.0664 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 167.8984 | 275.1757 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 81.05 | 29.3
2019-09-04 | 10:42 | 168 | 275.2773 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 30.27
2019-09-04 | 10:42 | 168.0977 | 275.375 | 0 | 1 | -0.73 | 0.27 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 168.1992 | 275.4765 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 168.3086 | 275.5859 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 168.4063 | 275.6836 | 0.01 | 1.01 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 168.5078 | 275.7851 | 0.03 | 1.03 | -0.75 | 0.25 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 168.6094 | 275.8867 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 168.7188 | 275.9961 | -0.04 | 0.96 | -0.68 | 0.32 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 168.8164 | 276.0937 | -0.13 | 0.87 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 168.9297 | 276.207 | -0.13 | 0.87 | -0.61 | 0.39 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:42 | 169.0273 | 276.3046 | -0.15 | 0.85 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 169.1289 | 276.4062 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 169.2266 | 276.5039 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 169.3281 | 276.6054 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 169.4375 | 276.7148 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 169.5391 | 276.8164 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 169.6367 | 276.914 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 169.7383 | 277.0156 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 169.8477 | 277.125 | 0.04 | 1.04 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 169.9492 | 277.2265 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 170.0586 | 277.3359 | 0.01 | 1.01 | -0.75 | 0.25 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:42 | 170.1563 | 277.4336 | 0.01 | 1.01 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 170.2578 | 277.5351 | -0.08 | 0.92 | -0.67 | 0.33 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 170.3594 | 277.6367 | -0.13 | 0.87 | -0.63 | 0.37 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 170.457 | 277.7343 | -0.15 | 0.85 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:42 | 170.5664 | 277.8437 | -0.16 | 0.84 | -0.59 | 0.41 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 170.668 | 277.9453 | -0.01 | 0.99 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 170.7695 | 278.0468 | -0.01 | 0.99 | -0.71 | 0.29 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:42 | 170.8789 | 278.1562 | -0.01 | 0.99 | -0.71 | 0.29 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:42 | 170.9766 | 278.2539 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 171.0781 | 278.3554 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 171.1875 | 278.4648 | 0.04 | 1.04 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 171.2891 | 278.5664 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:42 | 171.3867 | 278.664 | 0 | 1 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 171.4883 | 278.7656 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 171.5977 | 278.875 | 0.03 | 1.03 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 171.6992 | 278.9765 | 0 | 1 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:42 | 171.7969 | 279.0742 | -0.08 | 0.92 | -0.64 | 0.36 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 171.8984 | 279.1757 | -0.12 | 0.88 | -0.62 | 0.38 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 172.0078 | 279.2851 | -0.14 | 0.86 | -0.59 | 0.41 | -0.6 | 0.4 | 80.08 | 30.27
2019-09-04 | 10:42 | 172.1094 | 279.3867 | -0.04 | 0.96 | -0.69 | 0.31 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:42 | 172.207 | 279.4843 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 172.3086 | 279.5859 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 172.418 | 279.6953 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 172.5195 | 279.7968 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 172.6172 | 279.8945 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 172.7266 | 280.0039 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 172.8281 | 280.1054 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 172.9297 | 280.207 | 0.04 | 1.04 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 173.0273 | 280.3046 | -0.01 | 0.99 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 173.1367 | 280.414 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 173.2383 | 280.5156 | -0.06 | 0.94 | -0.69 | 0.31 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:42 | 173.3398 | 280.6171 | -0.11 | 0.89 | -0.64 | 0.36 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 173.4492 | 280.7265 | -0.17 | 0.83 | -0.6 | 0.4 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 173.5469 | 280.8242 | -0.17 | 0.83 | -0.59 | 0.41 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 173.6484 | 280.9257 | -0.03 | 0.97 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 173.75 | 281.0273 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 173.8594 | 281.1367 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 173.957 | 281.2343 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 174.0586 | 281.3359 | 0.02 | 1.02 | -0.71 | 0.29 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 174.1563 | 281.4336 | -0.01 | 0.99 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 174.2695 | 281.5468 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 80.08 | 30.27
2019-09-04 | 10:42 | 174.3672 | 281.6445 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 174.4688 | 281.7461 | 0.02 | 1.02 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 26.37
2019-09-04 | 10:42 | 174.5781 | 281.8554 | 0 | 1 | -0.74 | 0.26 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 174.6797 | 281.957 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 174.7773 | 282.0546 | -0.12 | 0.88 | -0.64 | 0.36 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 174.8867 | 282.164 | -0.14 | 0.86 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 174.9883 | 282.2656 | -0.15 | 0.85 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 175.0898 | 282.3671 | -0.17 | 0.83 | -0.58 | 0.42 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 175.1875 | 282.4648 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 175.2891 | 282.5664 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 175.3984 | 282.6757 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 175.5 | 282.7773 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 175.6094 | 282.8867 | -0.01 | 0.99 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 175.6992 | 282.9765 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 175.8086 | 283.0859 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 175.9063 | 283.1836 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 176.0195 | 283.2968 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 176.1172 | 283.3945 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 176.2188 | 283.4961 | 0.01 | 1.01 | -0.7 | 0.3 | -0.63 | 0.37 | 78.12 | 27.34
2019-09-04 | 10:42 | 176.3164 | 283.5937 | -0.11 | 0.89 | -0.63 | 0.37 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 176.418 | 283.6953 | -0.14 | 0.86 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 176.5273 | 283.8046 | -0.16 | 0.84 | -0.59 | 0.41 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:42 | 176.6289 | 283.9062 | -0.04 | 0.96 | -0.69 | 0.31 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 176.7383 | 284.0156 | -0.02 | 0.98 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 176.8398 | 284.1171 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 176.9375 | 284.2148 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:42 | 177.0391 | 284.3164 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 177.1484 | 284.4257 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:42 | 177.25 | 284.5273 | -0.01 | 0.99 | -0.7 | 0.3 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 177.3477 | 284.625 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 177.4492 | 284.7265 | 0 | 1 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 177.5586 | 284.8359 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 177.6563 | 284.9336 | 0 | 1 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 177.7578 | 285.0351 | -0.1 | 0.9 | -0.65 | 0.35 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 177.8594 | 285.1367 | -0.14 | 0.86 | -0.62 | 0.38 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 177.9688 | 285.2461 | -0.14 | 0.86 | -0.59 | 0.41 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 178.0664 | 285.3437 | -0.16 | 0.84 | -0.58 | 0.42 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 178.168 | 285.4453 | -0.04 | 0.96 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 178.2773 | 285.5546 | -0.02 | 0.98 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 178.3789 | 285.6562 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 178.4766 | 285.7539 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 178.5781 | 285.8554 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 178.6875 | 285.9648 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 178.7891 | 286.0664 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 178.8867 | 286.164 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 178.9883 | 286.2656 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 179.0977 | 286.375 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 179.1992 | 286.4765 | 0 | 1 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 179.2969 | 286.5742 | -0.09 | 0.91 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 179.4063 | 286.6836 | -0.13 | 0.87 | -0.6 | 0.4 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 179.5078 | 286.7851 | -0.16 | 0.84 | -0.59 | 0.41 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 179.6094 | 286.8867 | -0.05 | 0.95 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 179.707 | 286.9843 | -0.02 | 0.98 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 179.8164 | 287.0937 | -0.02 | 0.98 | -0.69 | 0.31 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 179.918 | 287.1953 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 180.0195 | 287.2968 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 180.1289 | 287.4062 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 180.2266 | 287.5039 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 180.3281 | 287.6054 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 180.4297 | 287.707 | 0.02 | 1.02 | -0.71 | 0.29 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 180.5391 | 287.8164 | 0 | 1 | -0.72 | 0.28 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:42 | 180.6367 | 287.914 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:42 | 180.7383 | 288.0156 | -0.06 | 0.94 | -0.68 | 0.32 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 180.8477 | 288.125 | -0.14 | 0.86 | -0.63 | 0.37 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 180.9492 | 288.2265 | -0.16 | 0.84 | -0.59 | 0.41 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 181.0469 | 288.3242 | -0.16 | 0.84 | -0.57 | 0.43 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 181.1484 | 288.4257 | -0.03 | 0.97 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 181.25 | 288.5273 | -0.02 | 0.98 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 181.3594 | 288.6367 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 181.4609 | 288.7382 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 181.5703 | 288.8476 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:42 | 181.668 | 288.9453 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 181.7695 | 289.0468 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 181.8789 | 289.1562 | 0.02 | 1.02 | -0.72 | 0.28 | -0.59 | 0.41 | 80.08 | 30.27
2019-09-04 | 10:42 | 181.9805 | 289.2578 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 182.0781 | 289.3554 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 182.1797 | 289.457 | -0.02 | 0.98 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 182.2773 | 289.5546 | -0.08 | 0.92 | -0.65 | 0.35 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 182.3789 | 289.6562 | -0.14 | 0.86 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 182.4883 | 289.7656 | -0.14 | 0.86 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 182.5898 | 289.8671 | -0.17 | 0.83 | -0.58 | 0.42 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 182.6992 | 289.9765 | -0.03 | 0.97 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 182.8008 | 290.0781 | -0.02 | 0.98 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 182.8984 | 290.1757 | 0 | 1 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 183 | 290.2773 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 183.1094 | 290.3867 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 183.2109 | 290.4882 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 183.3086 | 290.5859 | -0.01 | 0.99 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:42 | 183.4102 | 290.6875 | 0.02 | 1.02 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 183.5195 | 290.7968 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 183.6172 | 290.8945 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:42 | 183.7188 | 290.9961 | -0.04 | 0.96 | -0.68 | 0.32 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 183.8281 | 291.1054 | -0.11 | 0.89 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 183.9297 | 291.207 | -0.15 | 0.85 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 184.0273 | 291.3046 | -0.16 | 0.84 | -0.57 | 0.43 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:42 | 184.1289 | 291.4062 | -0.03 | 0.97 | -0.68 | 0.32 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 184.2383 | 291.5156 | -0.04 | 0.96 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 184.3398 | 291.6171 | 0 | 1 | -0.69 | 0.31 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 184.4375 | 291.7148 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 184.5391 | 291.8164 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 184.6484 | 291.9257 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 26.37
2019-09-04 | 10:42 | 184.75 | 292.0273 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 184.8477 | 292.125 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 184.9492 | 292.2265 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 185.0586 | 292.3359 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 185.1602 | 292.4375 | 0.01 | 1.01 | -0.71 | 0.29 | -0.62 | 0.38 | 80.08 | 29.3
2019-09-04 | 10:42 | 185.2578 | 292.5351 | -0.08 | 0.92 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 185.3672 | 292.6445 | -0.13 | 0.87 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 185.4688 | 292.7461 | -0.17 | 0.83 | -0.57 | 0.43 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:42 | 185.5703 | 292.8476 | -0.17 | 0.83 | -0.56 | 0.44 | -0.58 | 0.42 | 79.1 | 28.32
2019-09-04 | 10:42 | 185.668 | 292.9453 | -0.02 | 0.98 | -0.68 | 0.32 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:42 | 185.7773 | 293.0546 | -0.01 | 0.99 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 185.8906 | 293.1679 | -0.02 | 0.98 | -0.69 | 0.31 | -0.6 | 0.4 | 79.1 | 30.27
2019-09-04 | 10:42 | 185.9805 | 293.2578 | 0 | 1 | -0.69 | 0.31 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 186.0781 | 293.3554 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 186.1875 | 293.4648 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 186.2891 | 293.5664 | 0.02 | 1.02 | -0.71 | 0.29 | -0.62 | 0.38 | 80.08 | 26.37
2019-09-04 | 10:42 | 186.3906 | 293.6679 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 186.5 | 293.7773 | 0.01 | 1.01 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 186.5977 | 293.875 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 186.6992 | 293.9765 | -0.03 | 0.97 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 186.8008 | 294.0781 | -0.1 | 0.9 | -0.62 | 0.38 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 186.9102 | 294.1875 | -0.14 | 0.86 | -0.61 | 0.39 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 187.0078 | 294.2851 | -0.17 | 0.83 | -0.58 | 0.42 | -0.58 | 0.42 | 77.15 | 28.32
2019-09-04 | 10:42 | 187.1094 | 294.3867 | -0.06 | 0.94 | -0.66 | 0.34 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 187.2109 | 294.4882 | -0.03 | 0.97 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:42 | 187.3203 | 294.5976 | -0.02 | 0.98 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 187.418 | 294.6953 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 187.5273 | 294.8046 | -0.01 | 0.99 | -0.7 | 0.3 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:42 | 187.6289 | 294.9062 | -0.02 | 0.98 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 187.7305 | 295.0078 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 187.8281 | 295.1054 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 187.9375 | 295.2148 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 188.0391 | 295.3164 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 188.1406 | 295.4179 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 26.37
2019-09-04 | 10:42 | 188.2383 | 295.5156 | -0.04 | 0.96 | -0.67 | 0.33 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 188.3398 | 295.6171 | -0.12 | 0.88 | -0.62 | 0.38 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 188.4492 | 295.7265 | -0.13 | 0.87 | -0.6 | 0.4 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 188.5508 | 295.8281 | -0.15 | 0.85 | -0.59 | 0.41 | -0.58 | 0.42 | 79.1 | 28.32
2019-09-04 | 10:42 | 188.6602 | 295.9375 | -0.03 | 0.97 | -0.68 | 0.32 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 188.7578 | 296.0351 | -0.02 | 0.98 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 188.8594 | 296.1367 | -0.01 | 0.99 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 188.9688 | 296.2461 | -0.01 | 0.99 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 189.0703 | 296.3476 | 0.01 | 1.01 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 189.168 | 296.4453 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 189.2695 | 296.5468 | 0.01 | 1.01 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 189.3672 | 296.6445 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 26.37
2019-09-04 | 10:42 | 189.4805 | 296.7578 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 77.15 | 28.32
2019-09-04 | 10:42 | 189.5781 | 296.8554 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 189.6797 | 296.957 | 0.04 | 1.04 | -0.72 | 0.28 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:42 | 189.7891 | 297.0664 | -0.1 | 0.9 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 189.8906 | 297.1679 | -0.16 | 0.84 | -0.6 | 0.4 | -0.59 | 0.41 | 81.05 | 28.32
2019-09-04 | 10:42 | 189.9883 | 297.2656 | -0.13 | 0.87 | -0.59 | 0.41 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:42 | 190.0977 | 297.375 | -0.15 | 0.85 | -0.58 | 0.42 | -0.58 | 0.42 | 80.08 | 27.34
2019-09-04 | 10:42 | 190.1992 | 297.4765 | 0 | 1 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 190.3008 | 297.5781 | 0 | 1 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 190.3984 | 297.6757 | -0.02 | 0.98 | -0.68 | 0.32 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 190.5078 | 297.7851 | 0 | 1 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 190.6094 | 297.8867 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 190.7109 | 297.9882 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 190.8203 | 298.0976 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 190.9102 | 298.1875 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 191.0195 | 298.2968 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 191.1289 | 298.4062 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 191.2305 | 298.5078 | 0 | 1 | -0.7 | 0.3 | -0.62 | 0.38 | 80.08 | 27.34
2019-09-04 | 10:42 | 191.3281 | 298.6054 | -0.09 | 0.91 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 191.4297 | 298.707 | -0.12 | 0.88 | -0.59 | 0.41 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:42 | 191.5391 | 298.8164 | -0.15 | 0.85 | -0.57 | 0.43 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:42 | 191.6289 | 298.9062 | -0.05 | 0.95 | -0.68 | 0.32 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 191.7383 | 299.0156 | -0.02 | 0.98 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 191.8398 | 299.1171 | 0 | 1 | -0.69 | 0.31 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 191.9492 | 299.2265 | 0.01 | 1.01 | -0.68 | 0.32 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 192.0391 | 299.3164 | 0 | 1 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:42 | 192.1484 | 299.4257 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 192.2578 | 299.5351 | 0 | 1 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 192.3477 | 299.625 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 192.4609 | 299.7382 | 0 | 1 | -0.71 | 0.29 | -0.63 | 0.37 | 78.12 | 26.37
2019-09-04 | 10:42 | 192.5586 | 299.8359 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 192.668 | 299.9453 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 192.7695 | 300.0468 | -0.08 | 0.92 | -0.65 | 0.35 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 192.8672 | 300.1445 | -0.13 | 0.87 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 192.9688 | 300.2461 | -0.14 | 0.86 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 26.37
2019-09-04 | 10:42 | 193.0703 | 300.3476 | -0.15 | 0.85 | -0.58 | 0.42 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 193.1797 | 300.457 | -0.03 | 0.97 | -0.69 | 0.31 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 193.2773 | 300.5546 | -0.02 | 0.98 | -0.69 | 0.31 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 193.3789 | 300.6562 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 193.4883 | 300.7656 | 0.01 | 1.01 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:42 | 193.5898 | 300.8671 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 193.6875 | 300.9648 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 193.7891 | 301.0664 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:42 | 193.8984 | 301.1757 | 0.01 | 1.01 | -0.7 | 0.3 | -0.61 | 0.39 | 80.08 | 29.3
2019-09-04 | 10:42 | 194 | 301.2773 | 0.04 | 1.04 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 194.0977 | 301.375 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 30.27
2019-09-04 | 10:42 | 194.2109 | 301.4882 | 0 | 1 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:42 | 194.3086 | 301.5859 | -0.09 | 0.91 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 194.4102 | 301.6875 | -0.12 | 0.88 | -0.6 | 0.4 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:42 | 194.5195 | 301.7968 | -0.14 | 0.86 | -0.57 | 0.43 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:42 | 194.6172 | 301.8945 | -0.05 | 0.95 | -0.64 | 0.36 | -0.58 | 0.42 | 79.1 | 28.32
2019-09-04 | 10:42 | 194.7188 | 301.9961 | -0.01 | 0.99 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 194.8203 | 302.0976 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 194.918 | 302.1953 | 0 | 1 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 195.0273 | 302.3046 | 0.01 | 1.01 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 195.1289 | 302.4062 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 26.37
2019-09-04 | 10:42 | 195.2305 | 302.5078 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 195.3281 | 302.6054 | 0.02 | 1.02 | -0.71 | 0.29 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:42 | 195.4375 | 302.7148 | 0.01 | 1.01 | -0.71 | 0.29 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:42 | 195.5391 | 302.8164 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 195.6406 | 302.9179 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 195.75 | 303.0273 | -0.05 | 0.95 | -0.67 | 0.33 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:42 | 195.8594 | 303.1367 | -0.14 | 0.86 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 195.9492 | 303.2265 | -0.15 | 0.85 | -0.59 | 0.41 | -0.58 | 0.42 | 80.08 | 29.3
2019-09-04 | 10:42 | 196.0508 | 303.3281 | -0.17 | 0.83 | -0.59 | 0.41 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:42 | 196.1602 | 303.4375 | -0.02 | 0.98 | -0.69 | 0.31 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:42 | 196.2695 | 303.5468 | -0.01 | 0.99 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 196.3594 | 303.6367 | 0 | 1 | -0.7 | 0.3 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:42 | 196.4609 | 303.7382 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 196.5703 | 303.8476 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 196.668 | 303.9453 | 0.03 | 1.03 | -0.71 | 0.29 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 196.7695 | 304.0468 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 80.08 | 27.34
2019-09-04 | 10:42 | 196.8789 | 304.1562 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:42 | 196.9805 | 304.2578 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 197.0898 | 304.3671 | 0.04 | 1.04 | -0.71 | 0.29 | -0.61 | 0.39 | 81.05 | 28.32
2019-09-04 | 10:42 | 197.1875 | 304.4648 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:42 | 197.2891 | 304.5664 | -0.07 | 0.93 | -0.65 | 0.35 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 197.3906 | 304.6679 | -0.13 | 0.87 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 197.5 | 304.7773 | -0.14 | 0.86 | -0.59 | 0.41 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:42 | 197.5977 | 304.875 | -0.14 | 0.86 | -0.58 | 0.42 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:42 | 197.6992 | 304.9765 | -0.03 | 0.97 | -0.68 | 0.32 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 197.8008 | 305.0781 | 0.02 | 1.02 | -0.7 | 0.3 | -0.58 | 0.42 | 79.1 | 28.32
2019-09-04 | 10:42 | 197.8984 | 305.1757 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 198 | 305.2773 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:42 | 198.1094 | 305.3867 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 198.2188 | 305.4961 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 198.3203 | 305.5976 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 198.418 | 305.6953 | 0.02 | 1.02 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:42 | 198.5195 | 305.7968 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 198.6289 | 305.9062 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 198.7305 | 306.0078 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 198.8281 | 306.1054 | -0.09 | 0.91 | -0.63 | 0.37 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:42 | 198.9297 | 306.207 | -0.12 | 0.88 | -0.62 | 0.38 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:42 | 199.0273 | 306.3046 | -0.16 | 0.84 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 26.37
2019-09-04 | 10:42 | 199.1289 | 306.4062 | -0.03 | 0.97 | -0.68 | 0.32 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:42 | 199.2383 | 306.5156 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 199.3398 | 306.6171 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 199.4375 | 306.7148 | 0.02 | 1.02 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:42 | 199.5508 | 306.8281 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 199.6484 | 306.9257 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:42 | 199.75 | 307.0273 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:42 | 199.8594 | 307.1367 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 80.08 | 29.3
2019-09-04 | 10:42 | 199.9609 | 307.2382 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:42 | 200.0586 | 307.3359 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:42 | 200.1602 | 307.4375 | 0.04 | 1.04 | -0.72 | 0.28 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:42 | 200.2578 | 307.5351 | -0.04 | 0.96 | -0.69 | 0.31 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:42 | 200.3672 | 307.6445 | -0.09 | 0.91 | -0.64 | 0.36 | -0.62 | 0.38 | 80.08 | 28.32
2019-09-04 | 10:42 | 200.4688 | 307.7461 | -0.13 | 0.87 | -0.61 | 0.39 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:43 | 200.5781 | 307.8554 | -0.15 | 0.85 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 200.6797 | 307.957 | -0.02 | 0.98 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 200.7773 | 308.0546 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 200.8906 | 308.1679 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 200.9883 | 308.2656 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 201.0898 | 308.3671 | 0.02 | 1.02 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 201.1875 | 308.4648 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 201.2891 | 308.5664 | 0.02 | 1.02 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 201.3984 | 308.6757 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 201.5 | 308.7773 | 0 | 1 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 201.5977 | 308.875 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 201.7109 | 308.9882 | 0 | 1 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 201.8086 | 309.0859 | -0.08 | 0.92 | -0.65 | 0.35 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:43 | 201.9102 | 309.1875 | -0.12 | 0.88 | -0.62 | 0.38 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:43 | 202.0078 | 309.2851 | -0.14 | 0.86 | -0.6 | 0.4 | -0.58 | 0.42 | 81.05 | 29.3
2019-09-04 | 10:43 | 202.1172 | 309.3945 | -0.09 | 0.91 | -0.63 | 0.37 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:43 | 202.2188 | 309.4961 | 0 | 1 | -0.7 | 0.3 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 202.3203 | 309.5976 | 0 | 1 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 202.418 | 309.6953 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 202.5273 | 309.8046 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 202.6289 | 309.9062 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 202.7305 | 310.0078 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 202.8281 | 310.1054 | 0.03 | 1.03 | -0.73 | 0.27 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 202.9375 | 310.2148 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 203.0391 | 310.3164 | 0.04 | 1.04 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 203.1406 | 310.4179 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 203.25 | 310.5273 | 0 | 1 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 203.3477 | 310.625 | -0.09 | 0.91 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 203.4492 | 310.7265 | -0.12 | 0.88 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 203.5508 | 310.8281 | -0.14 | 0.86 | -0.59 | 0.41 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:43 | 203.6602 | 310.9375 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 203.7578 | 311.0351 | 0.01 | 1.01 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 203.8594 | 311.1367 | 0.02 | 1.02 | -0.7 | 0.3 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:43 | 203.9609 | 311.2382 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:43 | 204.0703 | 311.3476 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 204.168 | 311.4453 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 204.2773 | 311.5546 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:43 | 204.3789 | 311.6562 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 204.4805 | 311.7578 | 0.03 | 1.03 | -0.73 | 0.27 | -0.62 | 0.38 | 80.08 | 29.3
2019-09-04 | 10:43 | 204.5781 | 311.8554 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:43 | 204.6797 | 311.957 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 204.7891 | 312.0664 | -0.08 | 0.92 | -0.65 | 0.35 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:43 | 204.8906 | 312.1679 | -0.1 | 0.9 | -0.63 | 0.37 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 204.9883 | 312.2656 | -0.15 | 0.85 | -0.59 | 0.41 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 205.0898 | 312.3671 | -0.15 | 0.85 | -0.58 | 0.42 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:43 | 205.1992 | 312.4765 | -0.02 | 0.98 | -0.71 | 0.29 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 205.3008 | 312.5781 | -0.01 | 0.99 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 205.4102 | 312.6875 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 205.5078 | 312.7851 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 205.6094 | 312.8867 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:43 | 205.7109 | 312.9882 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 205.8086 | 313.0859 | 0.04 | 1.04 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 29.3
2019-09-04 | 10:43 | 205.918 | 313.1953 | 0.04 | 1.04 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 206.0195 | 313.2968 | 0.02 | 1.02 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 206.1172 | 313.3945 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 206.2305 | 313.5078 | 0.02 | 1.02 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 206.3281 | 313.6054 | -0.07 | 0.93 | -0.65 | 0.35 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 206.4297 | 313.707 | -0.12 | 0.88 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 206.5391 | 313.8164 | -0.15 | 0.85 | -0.59 | 0.41 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:43 | 206.6406 | 313.9179 | -0.02 | 0.98 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 206.7383 | 314.0156 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 206.8398 | 314.1171 | 0.03 | 1.03 | -0.71 | 0.29 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 206.9492 | 314.2265 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:43 | 207.0508 | 314.3281 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 207.1484 | 314.4257 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 207.25 | 314.5273 | 0.01 | 1.01 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 207.3594 | 314.6367 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 207.4609 | 314.7382 | 0.02 | 1.02 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:43 | 207.5703 | 314.8476 | 0.01 | 1.01 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 207.6602 | 314.9375 | 0.03 | 1.03 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 207.7695 | 315.0468 | -0.07 | 0.93 | -0.67 | 0.33 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 207.8789 | 315.1562 | -0.13 | 0.87 | -0.62 | 0.38 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 207.9688 | 315.2461 | -0.14 | 0.86 | -0.6 | 0.4 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:43 | 208.0781 | 315.3554 | -0.16 | 0.84 | -0.59 | 0.41 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:43 | 208.1797 | 315.457 | -0.03 | 0.97 | -0.71 | 0.29 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:43 | 208.2773 | 315.5546 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 208.3789 | 315.6562 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 208.4883 | 315.7656 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 208.5898 | 315.8671 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 208.6875 | 315.9648 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 208.7891 | 316.0664 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 77.15 | 27.34
2019-09-04 | 10:43 | 208.8984 | 316.1757 | 0.02 | 1.02 | -0.74 | 0.26 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 209 | 316.2773 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 209.0977 | 316.375 | 0.04 | 1.04 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 209.2109 | 316.4882 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 209.3086 | 316.5859 | -0.08 | 0.92 | -0.64 | 0.36 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 209.4102 | 316.6875 | -0.12 | 0.88 | -0.62 | 0.38 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:43 | 209.5078 | 316.7851 | -0.16 | 0.84 | -0.59 | 0.41 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:43 | 209.6172 | 316.8945 | -0.13 | 0.87 | -0.59 | 0.41 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 209.7188 | 316.9961 | 0 | 1 | -0.72 | 0.28 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 209.8203 | 317.0976 | 0.04 | 1.04 | -0.71 | 0.29 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:43 | 209.9297 | 317.207 | 0 | 1 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 210.0273 | 317.3046 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:43 | 210.1289 | 317.4062 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 210.2305 | 317.5078 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 210.3398 | 317.6171 | 0.01 | 1.01 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 210.4375 | 317.7148 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 210.5391 | 317.8164 | 0.02 | 1.02 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 210.6406 | 317.9179 | 0.01 | 1.01 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:43 | 210.75 | 318.0273 | -0.01 | 0.99 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 210.8477 | 318.125 | -0.09 | 0.91 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 210.9492 | 318.2265 | -0.11 | 0.89 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 211.0586 | 318.3359 | -0.14 | 0.86 | -0.6 | 0.4 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:43 | 211.1602 | 318.4375 | 0 | 1 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 211.2578 | 318.5351 | 0.01 | 1.01 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:43 | 211.3594 | 318.6367 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 211.4688 | 318.7461 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 211.5703 | 318.8476 | 0.03 | 1.03 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 211.668 | 318.9453 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 211.7695 | 319.0468 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 211.8789 | 319.1562 | 0.04 | 1.04 | -0.73 | 0.27 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:43 | 211.9805 | 319.2578 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 212.0781 | 319.3554 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 212.1875 | 319.4648 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 212.2891 | 319.5664 | -0.04 | 0.96 | -0.67 | 0.33 | -0.62 | 0.38 | 79.1 | 29.3
2019-09-04 | 10:43 | 212.3906 | 319.6679 | -0.11 | 0.89 | -0.63 | 0.37 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 212.5 | 319.7773 | -0.13 | 0.87 | -0.6 | 0.4 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:43 | 212.5977 | 319.875 | -0.16 | 0.84 | -0.58 | 0.42 | -0.57 | 0.43 | 78.12 | 28.32
2019-09-04 | 10:43 | 212.6992 | 319.9765 | -0.01 | 0.99 | -0.71 | 0.29 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 212.8008 | 320.0781 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 212.9102 | 320.1875 | 0.04 | 1.04 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 213.0078 | 320.2851 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:43 | 213.1094 | 320.3867 | 0.04 | 1.04 | -0.72 | 0.28 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 213.2109 | 320.4882 | 0.02 | 1.02 | -0.71 | 0.29 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 213.3203 | 320.5976 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:43 | 213.418 | 320.6953 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:43 | 213.5195 | 320.7968 | 0.03 | 1.03 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 213.6172 | 320.8945 | 0.04 | 1.04 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 213.7305 | 321.0078 | 0 | 1 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 213.8281 | 321.1054 | -0.09 | 0.91 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 213.9297 | 321.207 | -0.12 | 0.88 | -0.61 | 0.39 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 214.0391 | 321.3164 | -0.11 | 0.89 | -0.59 | 0.41 | -0.58 | 0.42 | 80.08 | 28.32
2019-09-04 | 10:43 | 214.1406 | 321.4179 | -0.02 | 0.98 | -0.67 | 0.33 | -0.58 | 0.42 | 80.08 | 29.3
2019-09-04 | 10:43 | 214.2383 | 321.5156 | -0.02 | 0.98 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 214.3398 | 321.6171 | 0 | 1 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 214.4492 | 321.7265 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 214.5508 | 321.8281 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 214.6484 | 321.9257 | 0.03 | 1.03 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 214.75 | 322.0273 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 214.8594 | 322.1367 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 214.9609 | 322.2382 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:43 | 215.0703 | 322.3476 | 0.03 | 1.03 | -0.73 | 0.27 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 215.168 | 322.4453 | 0.04 | 1.04 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:43 | 215.2695 | 322.5468 | -0.03 | 0.97 | -0.68 | 0.32 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 215.3672 | 322.6445 | -0.07 | 0.93 | -0.63 | 0.37 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 215.4688 | 322.7461 | -0.13 | 0.87 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 215.5781 | 322.8554 | -0.13 | 0.87 | -0.6 | 0.4 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 215.6797 | 322.957 | -0.01 | 0.99 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 215.7773 | 323.0546 | 0 | 1 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 215.8906 | 323.1679 | 0.01 | 1.01 | -0.71 | 0.29 | -0.59 | 0.41 | 79.1 | 30.27
2019-09-04 | 10:43 | 215.9883 | 323.2656 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 216.0898 | 323.3671 | 0 | 1 | -0.72 | 0.28 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:43 | 216.1992 | 323.4765 | 0.01 | 1.01 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 216.3008 | 323.5781 | 0.02 | 1.02 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 216.3984 | 323.6757 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:43 | 216.5078 | 323.7851 | 0.02 | 1.02 | -0.73 | 0.27 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 216.5977 | 323.875 | 0.02 | 1.02 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:43 | 216.7109 | 323.9882 | 0.03 | 1.03 | -0.74 | 0.26 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 216.8086 | 324.0859 | -0.07 | 0.93 | -0.65 | 0.35 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 216.9102 | 324.1875 | -0.12 | 0.88 | -0.61 | 0.39 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 217.0195 | 324.2968 | -0.14 | 0.86 | -0.58 | 0.42 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:43 | 217.1172 | 324.3945 | -0.14 | 0.86 | -0.59 | 0.41 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:43 | 217.2188 | 324.4961 | 0 | 1 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 217.3281 | 324.6054 | 0 | 1 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 217.4297 | 324.707 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 217.5273 | 324.8046 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 217.6289 | 324.9062 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 217.7383 | 325.0156 | 0.03 | 1.03 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 217.8398 | 325.1171 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 217.9375 | 325.2148 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 218.0391 | 325.3164 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:43 | 218.1484 | 325.4257 | 0.04 | 1.04 | -0.73 | 0.27 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 218.25 | 325.5273 | -0.01 | 0.99 | -0.7 | 0.3 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:43 | 218.3477 | 325.625 | -0.08 | 0.92 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 218.4609 | 325.7382 | -0.13 | 0.87 | -0.6 | 0.4 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 218.5586 | 325.8359 | -0.14 | 0.86 | -0.59 | 0.41 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:43 | 218.6602 | 325.9375 | -0.02 | 0.98 | -0.69 | 0.31 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:43 | 218.7578 | 326.0351 | 0 | 1 | -0.7 | 0.3 | -0.59 | 0.41 | 80.08 | 28.32
2019-09-04 | 10:43 | 218.8672 | 326.1445 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 218.9688 | 326.2461 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 219.0703 | 326.3476 | 0.04 | 1.04 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 219.168 | 326.4453 | 0.04 | 1.04 | -0.73 | 0.27 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 219.2773 | 326.5546 | 0.04 | 1.04 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 219.3789 | 326.6562 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:43 | 219.4805 | 326.7578 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 219.5781 | 326.8554 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 219.6875 | 326.9648 | 0.04 | 1.04 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 219.7891 | 327.0664 | -0.05 | 0.95 | -0.66 | 0.34 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:43 | 219.8984 | 327.1757 | -0.12 | 0.88 | -0.61 | 0.39 | -0.59 | 0.41 | 80.08 | 29.3
2019-09-04 | 10:43 | 220 | 327.2773 | -0.14 | 0.86 | -0.59 | 0.41 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:43 | 220.0977 | 327.375 | -0.13 | 0.87 | -0.58 | 0.42 | -0.59 | 0.41 | 80.08 | 30.27
2019-09-04 | 10:43 | 220.1992 | 327.4765 | 0.01 | 1.01 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 220.3008 | 327.5781 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 220.4102 | 327.6875 | 0 | 1 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 220.5078 | 327.7851 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 220.6094 | 327.8867 | 0.03 | 1.03 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 220.7109 | 327.9882 | 0.03 | 1.03 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 220.8203 | 328.0976 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 220.918 | 328.1953 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 221.0195 | 328.2968 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 221.1289 | 328.4062 | 0.01 | 1.01 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 221.2305 | 328.5078 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:43 | 221.3281 | 328.6054 | -0.07 | 0.93 | -0.65 | 0.35 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 221.4297 | 328.707 | -0.13 | 0.87 | -0.61 | 0.39 | -0.6 | 0.4 | 81.05 | 29.3
2019-09-04 | 10:43 | 221.5391 | 328.8164 | -0.13 | 0.87 | -0.58 | 0.42 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:43 | 221.6406 | 328.9179 | -0.03 | 0.97 | -0.66 | 0.34 | -0.58 | 0.42 | 80.08 | 29.3
2019-09-04 | 10:43 | 221.7383 | 329.0156 | 0 | 1 | -0.71 | 0.29 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 221.8398 | 329.1171 | 0.02 | 1.02 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 221.9492 | 329.2265 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 222.0508 | 329.3281 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 222.1484 | 329.4257 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 222.2578 | 329.5351 | 0.01 | 1.01 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 222.3594 | 329.6367 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 222.4609 | 329.7382 | 0.02 | 1.02 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 222.5703 | 329.8476 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 29.3
2019-09-04 | 10:43 | 222.668 | 329.9453 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 222.7695 | 330.0468 | 0 | 1 | -0.69 | 0.31 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:43 | 222.8789 | 330.1562 | -0.07 | 0.93 | -0.62 | 0.38 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 222.9805 | 330.2578 | -0.13 | 0.87 | -0.61 | 0.39 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 223.0781 | 330.3554 | -0.14 | 0.86 | -0.58 | 0.42 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:43 | 223.1797 | 330.457 | 0 | 1 | -0.68 | 0.32 | -0.59 | 0.41 | 80.08 | 29.3
2019-09-04 | 10:43 | 223.2891 | 330.5664 | 0.02 | 1.02 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 223.3906 | 330.6679 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 81.05 | 29.3
2019-09-04 | 10:43 | 223.4883 | 330.7656 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:43 | 223.5898 | 330.8671 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:43 | 223.6875 | 330.9648 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 223.8008 | 331.0781 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 223.8984 | 331.1757 | 0.02 | 1.02 | -0.72 | 0.28 | -0.6 | 0.4 | 80.08 | 29.3
2019-09-04 | 10:43 | 224 | 331.2773 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 224.0977 | 331.375 | 0.03 | 1.03 | -0.71 | 0.29 | -0.62 | 0.38 | 79.1 | 26.37
2019-09-04 | 10:43 | 224.2109 | 331.4882 | 0.04 | 1.04 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:43 | 224.3086 | 331.5859 | -0.07 | 0.93 | -0.66 | 0.34 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 224.418 | 331.6953 | -0.1 | 0.9 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 224.5195 | 331.7968 | -0.13 | 0.87 | -0.58 | 0.42 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 224.6172 | 331.8945 | -0.13 | 0.87 | -0.57 | 0.43 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 224.7188 | 331.9961 | 0.01 | 1.01 | -0.69 | 0.31 | -0.59 | 0.41 | 80.08 | 27.34
2019-09-04 | 10:43 | 224.8281 | 332.1054 | -0.01 | 0.99 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 224.9297 | 332.207 | 0.03 | 1.03 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 225.0273 | 332.3046 | 0.03 | 1.03 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 225.1289 | 332.4062 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 225.2305 | 332.5078 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 225.3398 | 332.6171 | 0.01 | 1.01 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 225.4375 | 332.7148 | 0.04 | 1.04 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 225.5391 | 332.8164 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 225.6406 | 332.9179 | 0.04 | 1.04 | -0.72 | 0.28 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 225.75 | 333.0273 | 0.02 | 1.02 | -0.7 | 0.3 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 225.8477 | 333.125 | -0.08 | 0.92 | -0.62 | 0.38 | -0.61 | 0.39 | 81.05 | 29.3
2019-09-04 | 10:43 | 225.9609 | 333.2382 | -0.12 | 0.88 | -0.58 | 0.42 | -0.59 | 0.41 | 81.05 | 27.34
2019-09-04 | 10:43 | 226.0586 | 333.3359 | -0.11 | 0.89 | -0.58 | 0.42 | -0.59 | 0.41 | 79.1 | 30.27
2019-09-04 | 10:43 | 226.1602 | 333.4375 | -0.02 | 0.98 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 226.2578 | 333.5351 | -0.01 | 0.99 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 226.3672 | 333.6445 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 226.4688 | 333.7461 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 226.5703 | 333.8476 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 226.668 | 333.9453 | 0.04 | 1.04 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:43 | 226.7773 | 334.0546 | 0.03 | 1.03 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 226.8789 | 334.1562 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 226.9805 | 334.2578 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:43 | 227.0898 | 334.3671 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 227.1875 | 334.4648 | 0.02 | 1.02 | -0.72 | 0.28 | -0.63 | 0.37 | 79.1 | 28.32
2019-09-04 | 10:43 | 227.2891 | 334.5664 | -0.02 | 0.98 | -0.67 | 0.33 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 227.3906 | 334.6679 | -0.11 | 0.89 | -0.62 | 0.38 | -0.6 | 0.4 | 80.08 | 27.34
2019-09-04 | 10:43 | 227.5 | 334.7773 | -0.13 | 0.87 | -0.59 | 0.41 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 227.5977 | 334.875 | -0.15 | 0.85 | -0.56 | 0.44 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:43 | 227.6992 | 334.9765 | 0 | 1 | -0.69 | 0.31 | -0.58 | 0.42 | 79.1 | 28.32
2019-09-04 | 10:43 | 227.8008 | 335.0781 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 227.9102 | 335.1875 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 228.0078 | 335.2851 | 0.01 | 1.01 | -0.68 | 0.32 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 228.1094 | 335.3867 | 0.02 | 1.02 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 228.2188 | 335.4961 | 0.03 | 1.03 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 228.3203 | 335.5976 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 228.418 | 335.6953 | 0.03 | 1.03 | -0.71 | 0.29 | -0.62 | 0.38 | 80.08 | 29.3
2019-09-04 | 10:43 | 228.5195 | 335.7968 | 0.04 | 1.04 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:43 | 228.6289 | 335.9062 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 80.08 | 29.3
2019-09-04 | 10:43 | 228.7305 | 336.0078 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 228.8281 | 336.1054 | -0.06 | 0.94 | -0.64 | 0.36 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:43 | 228.9375 | 336.2148 | -0.11 | 0.89 | -0.6 | 0.4 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 229.0391 | 336.3164 | -0.15 | 0.85 | -0.56 | 0.44 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 229.1406 | 336.4179 | -0.05 | 0.95 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:43 | 229.25 | 336.5273 | 0 | 1 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:43 | 229.3477 | 336.625 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 229.4492 | 336.7265 | 0.02 | 1.02 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 229.5508 | 336.8281 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 229.6484 | 336.9257 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 79.1 | 27.34
2019-09-04 | 10:43 | 229.7578 | 337.0351 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 229.8594 | 337.1367 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 80.08 | 29.3
2019-09-04 | 10:43 | 229.9609 | 337.2382 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 27.34
2019-09-04 | 10:43 | 230.0703 | 337.3476 | 0.04 | 1.04 | -0.72 | 0.28 | -0.61 | 0.39 | 81.05 | 29.3
2019-09-04 | 10:43 | 230.168 | 337.4453 | 0.04 | 1.04 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:43 | 230.2695 | 337.5468 | -0.03 | 0.97 | -0.67 | 0.33 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:43 | 230.3789 | 337.6562 | -0.12 | 0.88 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:43 | 230.4805 | 337.7578 | -0.13 | 0.87 | -0.59 | 0.41 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 230.5781 | 337.8554 | -0.13 | 0.87 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 230.6797 | 337.957 | 0.01 | 1.01 | -0.68 | 0.32 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 230.7891 | 338.0664 | 0 | 1 | -0.69 | 0.31 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 230.8906 | 338.1679 | 0.01 | 1.01 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 230.9883 | 338.2656 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 231.0898 | 338.3671 | 0.04 | 1.04 | -0.71 | 0.29 | -0.61 | 0.39 | 81.05 | 28.32
2019-09-04 | 10:43 | 231.1992 | 338.4765 | 0.02 | 1.02 | -0.69 | 0.31 | -0.6 | 0.4 | 79.1 | 29.3
2019-09-04 | 10:43 | 231.3008 | 338.5781 | 0.04 | 1.04 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 231.3984 | 338.6757 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 80.08 | 29.3
2019-09-04 | 10:43 | 231.5078 | 338.7851 | 0.02 | 1.02 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 231.6094 | 338.8867 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 231.7109 | 338.9882 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 231.8086 | 339.0859 | -0.05 | 0.95 | -0.65 | 0.35 | -0.62 | 0.38 | 79.1 | 29.3
2019-09-04 | 10:43 | 231.918 | 339.1953 | -0.1 | 0.9 | -0.61 | 0.39 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 232.0195 | 339.2968 | -0.13 | 0.87 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:43 | 232.1172 | 339.3945 | -0.13 | 0.87 | -0.57 | 0.43 | -0.6 | 0.4 | 80.08 | 28.32
2019-09-04 | 10:43 | 232.2188 | 339.4961 | 0.01 | 1.01 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 232.3281 | 339.6054 | 0.01 | 1.01 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 232.4297 | 339.707 | 0.04 | 1.04 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 232.5273 | 339.8046 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 232.6289 | 339.9062 | 0.03 | 1.03 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:43 | 232.7383 | 340.0156 | 0.03 | 1.03 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:43 | 232.8398 | 340.1171 | 0.03 | 1.03 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 28.32
2019-09-04 | 10:43 | 232.9375 | 340.2148 | 0.04 | 1.04 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 233.0508 | 340.3281 | 0.03 | 1.03 | -0.71 | 0.29 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:43 | 233.1484 | 340.4257 | 0.03 | 1.03 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:43 | 233.25 | 340.5273 | -0.01 | 0.99 | -0.69 | 0.31 | -0.61 | 0.39 | 79.1 | 28.32
2019-09-04 | 10:43 | 233.3477 | 340.625 | -0.09 | 0.91 | -0.62 | 0.38 | -0.62 | 0.38 | 79.1 | 28.32
2019-09-04 | 10:43 | 233.4609 | 340.7382 | -0.12 | 0.88 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 233.5586 | 340.8359 | -0.14 | 0.86 | -0.58 | 0.42 | -0.58 | 0.42 | 80.08 | 29.3
2019-09-04 | 10:43 | 233.668 | 340.9453 | -0.03 | 0.97 | -0.67 | 0.33 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:43 | 233.7578 | 341.0351 | 0.04 | 1.04 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 233.8672 | 341.1445 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 233.9688 | 341.2461 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 234.0703 | 341.3476 | 0.03 | 1.03 | -0.69 | 0.31 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 234.1797 | 341.457 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 80.08 | 27.34
2019-09-04 | 10:43 | 234.2773 | 341.5546 | 0.04 | 1.04 | -0.7 | 0.3 | -0.62 | 0.38 | 79.1 | 27.34
2019-09-04 | 10:43 | 234.3789 | 341.6562 | 0.04 | 1.04 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 29.3
2019-09-04 | 10:43 | 234.4805 | 341.7578 | 0.03 | 1.03 | -0.72 | 0.28 | -0.63 | 0.37 | 78.12 | 28.32
2019-09-04 | 10:43 | 234.5898 | 341.8671 | 0.03 | 1.03 | -0.72 | 0.28 | -0.63 | 0.37 | 79.1 | 28.32
2019-09-04 | 10:43 | 234.6875 | 341.9648 | 0.03 | 1.03 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 234.7891 | 342.0664 | -0.05 | 0.95 | -0.64 | 0.36 | -0.63 | 0.37 | 78.12 | 29.3
2019-09-04 | 10:43 | 234.8984 | 342.1757 | -0.11 | 0.89 | -0.6 | 0.4 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 235 | 342.2773 | -0.13 | 0.87 | -0.57 | 0.43 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 235.0977 | 342.375 | -0.14 | 0.86 | -0.57 | 0.43 | -0.57 | 0.43 | 78.12 | 28.32
2019-09-04 | 10:43 | 235.2109 | 342.4882 | 0 | 1 | -0.68 | 0.32 | -0.59 | 0.41 | 79.1 | 27.34
2019-09-04 | 10:43 | 235.3086 | 342.5859 | 0.01 | 1.01 | -0.68 | 0.32 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 235.4102 | 342.6875 | 0.04 | 1.04 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 235.5078 | 342.7851 | 0.03 | 1.03 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 235.6094 | 342.8867 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 235.7188 | 342.9961 | 0.04 | 1.04 | -0.69 | 0.31 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 235.8203 | 343.0976 | 0.04 | 1.04 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 235.918 | 343.1953 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 236.0273 | 343.3046 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 236.1289 | 343.4062 | 0.04 | 1.04 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 236.2305 | 343.5078 | 0.02 | 1.02 | -0.71 | 0.29 | -0.61 | 0.39 | 80.08 | 28.32
2019-09-04 | 10:43 | 236.3398 | 343.6171 | -0.07 | 0.93 | -0.63 | 0.37 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:43 | 236.4375 | 343.7148 | -0.11 | 0.89 | -0.6 | 0.4 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 236.5391 | 343.8164 | -0.14 | 0.86 | -0.58 | 0.42 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 236.6406 | 343.9179 | -0.08 | 0.92 | -0.62 | 0.38 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:43 | 236.75 | 344.0273 | 0 | 1 | -0.67 | 0.33 | -0.6 | 0.4 | 78.12 | 29.3
2019-09-04 | 10:43 | 236.8477 | 344.125 | 0.03 | 1.03 | -0.7 | 0.3 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 236.9492 | 344.2265 | 0 | 1 | -0.69 | 0.31 | -0.61 | 0.39 | 78.12 | 27.34
2019-09-04 | 10:43 | 237.0508 | 344.3281 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 237.1484 | 344.4257 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 237.2578 | 344.5351 | 0.02 | 1.02 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 29.3
2019-09-04 | 10:43 | 237.3594 | 344.6367 | 0.02 | 1.02 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 237.4609 | 344.7382 | 0.04 | 1.04 | -0.69 | 0.31 | -0.6 | 0.4 | 77.15 | 29.3
2019-09-04 | 10:43 | 237.5703 | 344.8476 | 0.04 | 1.04 | -0.72 | 0.28 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 237.668 | 344.9453 | 0.03 | 1.03 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 28.32
2019-09-04 | 10:43 | 237.7695 | 345.0468 | -0.02 | 0.98 | -0.67 | 0.33 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 237.8789 | 345.1562 | -0.11 | 0.89 | -0.6 | 0.4 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:43 | 237.9805 | 345.2578 | -0.13 | 0.87 | -0.57 | 0.43 | -0.58 | 0.42 | 78.12 | 29.3
2019-09-04 | 10:43 | 238.0781 | 345.3554 | -0.12 | 0.88 | -0.56 | 0.44 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:43 | 238.1797 | 345.457 | 0 | 1 | -0.66 | 0.34 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:43 | 238.2891 | 345.5664 | 0 | 1 | -0.69 | 0.31 | -0.58 | 0.42 | 78.12 | 29.3
2019-09-04 | 10:43 | 238.3906 | 345.6679 | 0.03 | 1.03 | -0.68 | 0.32 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:43 | 238.4883 | 345.7656 | 0.01 | 1.01 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 238.5898 | 345.8671 | 0.02 | 1.02 | -0.68 | 0.32 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:43 | 238.6875 | 345.9648 | 0.04 | 1.04 | -0.68 | 0.32 | -0.59 | 0.41 | 79.1 | 29.3
2019-09-04 | 10:43 | 238.8008 | 346.0781 | 0.03 | 1.03 | -0.68 | 0.32 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 238.8984 | 346.1757 | 0.04 | 1.04 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 30.27
2019-09-04 | 10:43 | 239.0078 | 346.2851 | 0.04 | 1.04 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 28.32
2019-09-04 | 10:43 | 239.1094 | 346.3867 | 0.04 | 1.04 | -0.71 | 0.29 | -0.6 | 0.4 | 79.1 | 27.34
2019-09-04 | 10:43 | 239.2109 | 346.4882 | 0.03 | 1.03 | -0.7 | 0.3 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 239.3086 | 346.5859 | -0.06 | 0.94 | -0.62 | 0.38 | -0.59 | 0.41 | 78.12 | 27.34
2019-09-04 | 10:43 | 239.418 | 346.6953 | -0.09 | 0.91 | -0.59 | 0.41 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 239.5195 | 346.7968 | -0.14 | 0.86 | -0.57 | 0.43 | -0.57 | 0.43 | 78.12 | 27.34
2019-09-04 | 10:43 | 239.6172 | 346.8945 | -0.14 | 0.86 | -0.56 | 0.44 | -0.58 | 0.42 | 77.15 | 27.34
2019-09-04 | 10:43 | 239.7305 | 347.0078 | -0.01 | 0.99 | -0.66 | 0.34 | -0.57 | 0.43 | 79.1 | 29.3
2019-09-04 | 10:43 | 239.8281 | 347.1054 | 0.01 | 1.01 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 28.32
2019-09-04 | 10:43 | 239.9297 | 347.207 | 0.01 | 1.01 | -0.67 | 0.33 | -0.59 | 0.41 | 79.1 | 30.27
2019-09-04 | 10:43 | 240.0273 | 347.3046 | 0.02 | 1.02 | -0.68 | 0.32 | -0.58 | 0.42 | 80.08 | 28.32
2019-09-04 | 10:43 | 240.1406 | 347.4179 | 0.02 | 1.02 | -0.68 | 0.32 | -0.58 | 0.42 | 78.12 | 28.32
2019-09-04 | 10:43 | 240.2383 | 347.5156 | 0.02 | 1.02 | -0.68 | 0.32 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:43 | 240.3398 | 347.6171 | 0.03 | 1.03 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 29.3
2019-09-04 | 10:43 | 240.4375 | 347.7148 | 0.02 | 1.02 | -0.68 | 0.32 | -0.58 | 0.42 | 79.1 | 27.34
2019-09-04 | 10:43 | 240.5508 | 347.8281 | 0.01 | 1.01 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 27.34
2019-09-04 | 10:43 | 240.6484 | 347.9257 | 0.03 | 1.03 | -0.69 | 0.31 | -0.59 | 0.41 | 79.1 | 28.32
2019-09-04 | 10:43 | 240.75 | 348.0273 | 0.01 | 1.01 | -0.68 | 0.32 | -0.6 | 0.4 | 79.1 | 28.32
2019-09-04 | 10:43 | 240.8477 | 348.125 | -0.07 | 0.93 | -0.61 | 0.39 | -0.56 | 0.44 | 79.1 | 28.32
2019-09-04 | 10:43 | 240.9609 | 348.2382 | -0.11 | 0.89 | -0.59 | 0.41 | -0.58 | 0.42 | 78.12 | 27.34
2019-09-04 | 10:43 | 241.0586 | 348.3359 | -0.14 | 0.86 | -0.55 | 0.45 | -0.57 | 0.43 | 79.1 | 28.32
2019-09-04 | 10:43 | 241.168 | 348.4453 | 0 | 1 | -0.64 | 0.36 | -0.58 | 0.42 | 77.15 | 28.32
2019-09-04 | 10:43 | 241.2695 | 348.5468 | 0 | 1 | -0.67 | 0.33 | -0.57 | 0.43 | 79.1 | 29.3
2019-09-04 | 10:43 | 241.3672 | 348.6445 | 0.03 | 1.03 | -0.67 | 0.33 | -0.57 | 0.43 | 78.12 | 28.32
2019-09-04 | 10:43 | 241.4805 | 348.7578 | 0.01 | 1.01 | -0.67 | 0.33 | -0.57 | 0.43 | 77.15 | 27.34
2019-09-04 | 10:43 | 241.5781 | 348.8554 | 0.02 | 1.02 | -0.67 | 0.33 | -0.57 | 0.43 | 77.15 | 28.32
2019-09-04 | 10:43 | 241.6797 | 348.957 | 0.02 | 1.02 | -0.68 | 0.32 | -0.58 | 0.42 | 78.12 | 29.3
2019-09-04 | 10:43 | 241.7773 | 349.0546 | 0.03 | 1.03 | -0.68 | 0.32 | -0.58 | 0.42 | 77.15 | 27.34
2019-09-04 | 10:43 | 241.8789 | 349.1562 | 0.03 | 1.03 | -0.67 | 0.33 | -0.57 | 0.43 | 78.12 | 28.32
2019-09-04 | 10:43 | 241.9883 | 349.2656 | 0.02 | 1.02 | -0.67 | 0.33 | -0.59 | 0.41 | 77.15 | 29.3
2019-09-04 | 10:43 | 242.0898 | 349.3671 | 0.04 | 1.04 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 28.32

## 17.3mL s
|  |  | BoilerPressure |  | HEPressure |  | SCPressure
Date | Clock | Timer | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | HETemperature | SCTemperature
2019-09-04 | 11:09 | 0.16016 | 0.01 | 1.01 | -0.21 | 0.79 | -0.21 | 0.79 | 32.23 | 24.41 |  | Flow
2019-09-04 | 11:09 | 0.23047 | 0.04 | 1.04 | -0.24 | 0.76 | -0.2 | 0.8 | 33.2 | 23.44 |  | mL | seconds | flow
2019-09-04 | 11:09 | 0.32812 | 0.05 | 1.05 | -0.25 | 0.75 | -0.21 | 0.79 | 31.25 | 23.44 |  | 100 | 5 | 20 | start
2019-09-04 | 11:09 | 0.4375 | 0.07 | 1.07 | -0.25 | 0.75 | -0.22 | 0.78 | 31.25 | 23.44 |  | 100 | 5 | 16.7
2019-09-04 | 11:09 | 0.53906 | 0.07 | 1.07 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 24.41 |  | 100 | 6 | 16.7
2019-09-04 | 11:09 | 0.64062 | 0.07 | 1.07 | -0.27 | 0.73 | -0.21 | 0.79 | 33.2 | 23.44
2019-09-04 | 11:09 | 0.75 | 0.07 | 1.07 | -0.27 | 0.73 | -0.22 | 0.78 | 31.25 | 24.41 |  | 100 | 6 | 16.7 | end
2019-09-04 | 11:09 | 0.84766 | 0.08 | 1.08 | -0.26 | 0.74 | -0.23 | 0.77 | 33.2 | 23.44 |  | 100 | 6 | 16.7
2019-09-04 | 11:09 | 0.94922 | 0.07 | 1.07 | -0.26 | 0.74 | -0.23 | 0.77 | 32.23 | 23.44 |  | 100 | 6 | 16.7
2019-09-04 | 11:09 | 1.0508 | 0.07 | 1.07 | -0.27 | 0.73 | -0.22 | 0.78 | 31.25 | 22.46
2019-09-04 | 11:09 | 1.1602 | 0.08 | 1.08 | -0.26 | 0.74 | -0.24 | 0.76 | 34.18 | 25.39 |  |  |  | 17.25 | average
2019-09-04 | 11:09 | 1.2578 | 0.06 | 1.06 | -0.27 | 0.73 | -0.22 | 0.78 | 32.23 | 24.41
2019-09-04 | 11:09 | 1.3594 | 0.03 | 1.03 | -0.24 | 0.76 | -0.21 | 0.79 | 32.23 | 24.41
2019-09-04 | 11:09 | 1.4609 | 0.03 | 1.03 | -0.23 | 0.77 | -0.2 | 0.8 | 35.16 | 25.39
2019-09-04 | 11:09 | 1.5703 | 0.02 | 1.02 | -0.22 | 0.78 | -0.21 | 0.79 | 33.2 | 23.44
2019-09-04 | 11:09 | 1.668 | 0 | 1 | -0.21 | 0.79 | -0.19 | 0.81 | 32.23 | 23.44
2019-09-04 | 11:09 | 1.7695 | 0.06 | 1.06 | -0.25 | 0.75 | -0.19 | 0.81 | 33.2 | 23.44
2019-09-04 | 11:09 | 1.8711 | 0.06 | 1.06 | -0.25 | 0.75 | -0.21 | 0.79 | 32.23 | 24.41
2019-09-04 | 11:09 | 1.9805 | 0.06 | 1.06 | -0.27 | 0.73 | -0.21 | 0.79 | 33.2 | 23.44
2019-09-04 | 11:09 | 2.0781 | 0.06 | 1.06 | -0.25 | 0.75 | -0.2 | 0.8 | 32.23 | 23.44
2019-09-04 | 11:09 | 2.1797 | 0.06 | 1.06 | -0.27 | 0.73 | -0.22 | 0.78 | 33.2 | 25.39
2019-09-04 | 11:09 | 2.2891 | 0.09 | 1.09 | -0.27 | 0.73 | -0.23 | 0.77 | 34.18 | 24.41
2019-09-04 | 11:09 | 2.3906 | 0.08 | 1.08 | -0.27 | 0.73 | -0.22 | 0.78 | 32.23 | 25.39
2019-09-04 | 11:09 | 2.4883 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 31.25 | 23.44
2019-09-04 | 11:09 | 2.5977 | 0.06 | 1.06 | -0.26 | 0.74 | -0.22 | 0.78 | 33.2 | 24.41
2019-09-04 | 11:09 | 2.6992 | 0.08 | 1.08 | -0.28 | 0.72 | -0.23 | 0.77 | 33.2 | 26.37
2019-09-04 | 11:09 | 2.8008 | 0.01 | 1.01 | -0.24 | 0.76 | -0.21 | 0.79 | 33.2 | 24.41
2019-09-04 | 11:09 | 2.8984 | 0.02 | 1.02 | -0.23 | 0.77 | -0.21 | 0.79 | 32.23 | 23.44
2019-09-04 | 11:09 | 3 | 0.01 | 1.01 | -0.21 | 0.79 | -0.2 | 0.8 | 33.2 | 24.41
2019-09-04 | 11:09 | 3.1094 | 0 | 1 | -0.21 | 0.79 | -0.21 | 0.79 | 32.23 | 22.46
2019-09-04 | 11:09 | 3.2109 | 0 | 1 | -0.19 | 0.81 | -0.2 | 0.8 | 32.23 | 23.44
2019-09-04 | 11:09 | 3.3203 | 0.04 | 1.04 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 23.44
2019-09-04 | 11:09 | 3.418 | 0.06 | 1.06 | -0.26 | 0.74 | -0.21 | 0.79 | 33.2 | 24.41 |  | Equilibrium pressures from 150 seconds
2019-09-04 | 11:09 | 3.5195 | 0.07 | 1.07 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 24.41
2019-09-04 | 11:09 | 3.6211 | 0.08 | 1.08 | -0.27 | 0.73 | -0.22 | 0.78 | 32.23 | 23.44 |  | minimum boiler pressure from 150 seconds is: |  |  |  |  | 0.84 |  | average Pb | 1.0135
2019-09-04 | 11:09 | 3.7188 | 0.07 | 1.07 | -0.27 | 0.73 | -0.21 | 0.79 | 32.23 | 23.44 |  | maximum boiler pressure from 150 seconds is: |  |  |  |  | 1.08
2019-09-04 | 11:09 | 3.8281 | 0.06 | 1.06 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 22.46
2019-09-04 | 11:09 | 3.9297 | 0.07 | 1.07 | -0.27 | 0.73 | -0.22 | 0.78 | 33.2 | 25.39 |  | minimum heat exchanger pressure from 150 seconds is: |  |  |  |  | 0.2 |  | average Phe | 0.2474
2019-09-04 | 11:09 | 4.0273 | 0.07 | 1.07 | -0.27 | 0.73 | -0.24 | 0.76 | 32.23 | 23.44 |  | maximum heat exchanger pressure from 150 seconds is |  |  |  |  | 0.41
2019-09-04 | 11:09 | 4.1289 | 0.08 | 1.08 | -0.26 | 0.74 | -0.23 | 0.77 | 32.23 | 22.46
2019-09-04 | 11:09 | 4.2383 | 0.07 | 1.07 | -0.28 | 0.72 | -0.23 | 0.77 | 33.2 | 23.44
2019-09-04 | 11:09 | 4.3398 | 0.01 | 1.01 | -0.22 | 0.78 | -0.21 | 0.79 | 33.2 | 23.44
2019-09-04 | 11:09 | 4.4492 | 0.02 | 1.02 | -0.22 | 0.78 | -0.21 | 0.79 | 33.2 | 24.41
2019-09-04 | 11:09 | 4.5508 | 0.01 | 1.01 | -0.22 | 0.78 | -0.21 | 0.79 | 32.23 | 24.41
2019-09-04 | 11:09 | 4.6484 | 0 | 1 | -0.21 | 0.79 | -0.19 | 0.81 | 32.23 | 23.44
2019-09-04 | 11:09 | 4.75 | 0.06 | 1.06 | -0.25 | 0.75 | -0.2 | 0.8 | 33.2 | 24.41
2019-09-04 | 11:09 | 4.8477 | 0.04 | 1.04 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 25.39
2019-09-04 | 11:09 | 4.9609 | 0.05 | 1.05 | -0.26 | 0.74 | -0.21 | 0.79 | 31.25 | 23.44
2019-09-04 | 11:09 | 5.0586 | 0.07 | 1.07 | -0.26 | 0.74 | -0.22 | 0.78 | 33.2 | 23.44
2019-09-04 | 11:09 | 5.1602 | 0.06 | 1.06 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 23.44
2019-09-04 | 11:09 | 5.2578 | 0.08 | 1.08 | -0.26 | 0.74 | -0.23 | 0.77 | 32.23 | 23.44
2019-09-04 | 11:09 | 5.3711 | 0.06 | 1.06 | -0.26 | 0.74 | -0.23 | 0.77 | 32.23 | 24.41
2019-09-04 | 11:09 | 5.4688 | 0.07 | 1.07 | -0.27 | 0.73 | -0.23 | 0.77 | 34.18 | 24.41
2019-09-04 | 11:09 | 5.5703 | 0.07 | 1.07 | -0.25 | 0.75 | -0.23 | 0.77 | 32.23 | 24.41
2019-09-04 | 11:09 | 5.6797 | 0.08 | 1.08 | -0.27 | 0.73 | -0.23 | 0.77 | 33.2 | 25.39
2019-09-04 | 11:09 | 5.7773 | 0.04 | 1.04 | -0.25 | 0.75 | -0.23 | 0.77 | 32.23 | 25.39
2019-09-04 | 11:09 | 5.8789 | 0.02 | 1.02 | -0.23 | 0.77 | -0.2 | 0.8 | 33.2 | 24.41
2019-09-04 | 11:09 | 5.9883 | 0 | 1 | -0.22 | 0.78 | -0.2 | 0.8 | 33.2 | 25.39
2019-09-04 | 11:09 | 6.0898 | 0.01 | 1.01 | -0.21 | 0.79 | -0.21 | 0.79 | 32.23 | 25.39
2019-09-04 | 11:09 | 6.1875 | 0.01 | 1.01 | -0.22 | 0.78 | -0.19 | 0.81 | 33.2 | 23.44
2019-09-04 | 11:09 | 6.2891 | 0.06 | 1.06 | -0.25 | 0.75 | -0.2 | 0.8 | 33.2 | 23.44
2019-09-04 | 11:09 | 6.3984 | 0.07 | 1.07 | -0.25 | 0.75 | -0.22 | 0.78 | 33.2 | 25.39 |  | temperature equilibrium from 125 seconds
2019-09-04 | 11:09 | 6.5 | 0.08 | 1.08 | -0.25 | 0.75 | -0.21 | 0.79 | 33.2 | 24.41
2019-09-04 | 11:09 | 6.5977 | 0.08 | 1.08 | -0.27 | 0.73 | -0.22 | 0.78 | 31.25 | 23.44 |  | minimum heat exchanger outlet temperature is: |  |  |  |  | 68.36 |  | average SC bath temp |  | 29.5422
2019-09-04 | 11:09 | 6.6992 | 0.07 | 1.07 | -0.26 | 0.74 | -0.21 | 0.79 | 33.2 | 24.41 |  | maximum heat exchanger outlet temperature is: |  |  |  |  | 73.24
2019-09-04 | 11:09 | 6.8086 | 0.07 | 1.07 | -0.25 | 0.75 | -0.21 | 0.79 | 31.25 | 23.44
2019-09-04 | 11:09 | 6.9102 | 0.07 | 1.07 | -0.27 | 0.73 | -0.23 | 0.77 | 31.25 | 24.41 |  | average HE outlet temperature is: |  |  |  | 70.9211
2019-09-04 | 11:09 | 7.0078 | 0.07 | 1.07 | -0.27 | 0.73 | -0.22 | 0.78 | 32.23 | 24.41
2019-09-04 | 11:09 | 7.1211 | 0.07 | 1.07 | -0.28 | 0.72 | -0.23 | 0.77 | 33.2 | 24.41 |  | number of temperature points measured is: |  |  |  | 1711 |  | STDEV | 0.91666
2019-09-04 | 11:09 | 7.2188 | 0.08 | 1.08 | -0.27 | 0.73 | -0.23 | 0.77 | 33.2 | 23.44
2019-09-04 | 11:09 | 7.3203 | 0.02 | 1.02 | -0.22 | 0.78 | -0.21 | 0.79 | 33.2 | 25.39
2019-09-04 | 11:09 | 7.418 | 0.03 | 1.03 | -0.22 | 0.78 | -0.21 | 0.79 | 33.2 | 24.41
2019-09-04 | 11:09 | 7.5273 | 0 | 1 | -0.22 | 0.78 | -0.2 | 0.8 | 33.2 | 25.39
2019-09-04 | 11:09 | 7.6289 | 0.02 | 1.02 | -0.21 | 0.79 | -0.2 | 0.8 | 33.2 | 22.46
2019-09-04 | 11:09 | 7.7305 | 0.04 | 1.04 | -0.23 | 0.77 | -0.2 | 0.8 | 33.2 | 25.39
2019-09-04 | 11:09 | 7.8281 | 0.05 | 1.05 | -0.24 | 0.76 | -0.21 | 0.79 | 33.2 | 25.39
2019-09-04 | 11:09 | 7.9375 | 0.06 | 1.06 | -0.25 | 0.75 | -0.22 | 0.78 | 33.2 | 23.44
2019-09-04 | 11:09 | 8.0391 | 0.05 | 1.05 | -0.26 | 0.74 | -0.22 | 0.78 | 32.23 | 24.41
2019-09-04 | 11:09 | 8.1406 | 0.07 | 1.07 | -0.26 | 0.74 | -0.21 | 0.79 | 32.23 | 23.44
2019-09-04 | 11:09 | 8.25 | 0.08 | 1.08 | -0.25 | 0.75 | -0.23 | 0.77 | 32.23 | 24.41
2019-09-04 | 11:09 | 8.3477 | 0.06 | 1.06 | -0.25 | 0.75 | -0.22 | 0.78 | 34.18 | 25.39
2019-09-04 | 11:09 | 8.4492 | 0.07 | 1.07 | -0.26 | 0.74 | -0.23 | 0.77 | 32.23 | 24.41
2019-09-04 | 11:10 | 8.5508 | 0.06 | 1.06 | -0.27 | 0.73 | -0.22 | 0.78 | 32.23 | 25.39
2019-09-04 | 11:10 | 8.6602 | 0.07 | 1.07 | -0.28 | 0.72 | -0.24 | 0.76 | 33.2 | 24.41
2019-09-04 | 11:10 | 8.7578 | 0.06 | 1.06 | -0.25 | 0.75 | -0.23 | 0.77 | 32.23 | 24.41
2019-09-04 | 11:10 | 8.8594 | 0.02 | 1.02 | -0.23 | 0.77 | -0.21 | 0.79 | 32.23 | 23.44
2019-09-04 | 11:10 | 8.9609 | 0 | 1 | -0.23 | 0.77 | -0.22 | 0.78 | 32.23 | 24.41
2019-09-04 | 11:10 | 9.0703 | 0.02 | 1.02 | -0.21 | 0.79 | -0.22 | 0.78 | 32.23 | 23.44
2019-09-04 | 11:10 | 9.168 | 0 | 1 | -0.22 | 0.78 | -0.2 | 0.8 | 34.18 | 24.41
2019-09-04 | 11:10 | 9.2695 | 0.07 | 1.07 | -0.24 | 0.76 | -0.21 | 0.79 | 32.23 | 22.46
2019-09-04 | 11:10 | 9.3789 | 0.05 | 1.05 | -0.25 | 0.75 | -0.2 | 0.8 | 33.2 | 25.39
2019-09-04 | 11:10 | 9.4805 | 0.06 | 1.06 | -0.25 | 0.75 | -0.2 | 0.8 | 32.23 | 24.41
2019-09-04 | 11:10 | 9.5781 | 0.08 | 1.08 | -0.26 | 0.74 | -0.22 | 0.78 | 32.23 | 23.44
2019-09-04 | 11:10 | 9.6797 | 0.07 | 1.07 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 23.44
2019-09-04 | 11:10 | 9.7891 | 0.08 | 1.08 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 24.41
2019-09-04 | 11:10 | 9.8906 | 0.09 | 1.09 | -0.27 | 0.73 | -0.22 | 0.78 | 32.23 | 25.39
2019-09-04 | 11:10 | 9.9883 | 0.07 | 1.07 | -0.28 | 0.72 | -0.23 | 0.77 | 33.2 | 23.44
2019-09-04 | 11:10 | 10.0898 | 0.07 | 1.07 | -0.26 | 0.74 | -0.23 | 0.77 | 32.23 | 24.41
2019-09-04 | 11:10 | 10.1992 | 0.08 | 1.08 | -0.27 | 0.73 | -0.23 | 0.77 | 33.2 | 23.44
2019-09-04 | 11:10 | 10.3008 | 0.04 | 1.04 | -0.24 | 0.76 | -0.22 | 0.78 | 32.23 | 22.46
2019-09-04 | 11:10 | 10.3984 | 0.01 | 1.01 | -0.23 | 0.77 | -0.21 | 0.79 | 32.23 | 23.44
2019-09-04 | 11:10 | 10.5 | 0.04 | 1.04 | -0.22 | 0.78 | -0.21 | 0.79 | 33.2 | 25.39
2019-09-04 | 11:10 | 10.6094 | 0.01 | 1.01 | -0.21 | 0.79 | -0.2 | 0.8 | 32.23 | 25.39
2019-09-04 | 11:10 | 10.7109 | 0.02 | 1.02 | -0.21 | 0.79 | -0.18 | 0.82 | 33.2 | 25.39
2019-09-04 | 11:10 | 10.8203 | 0.07 | 1.07 | -0.24 | 0.76 | -0.2 | 0.8 | 33.2 | 26.37
2019-09-04 | 11:10 | 10.918 | 0.06 | 1.06 | -0.23 | 0.77 | -0.2 | 0.8 | 32.23 | 23.44
2019-09-04 | 11:10 | 11.0195 | 0.07 | 1.07 | -0.25 | 0.75 | -0.21 | 0.79 | 32.23 | 23.44
2019-09-04 | 11:10 | 11.1211 | 0.07 | 1.07 | -0.26 | 0.74 | -0.21 | 0.79 | 31.25 | 23.44
2019-09-04 | 11:10 | 11.2188 | 0.08 | 1.08 | -0.26 | 0.74 | -0.22 | 0.78 | 32.23 | 24.41
2019-09-04 | 11:10 | 11.3281 | 0.08 | 1.08 | -0.26 | 0.74 | -0.21 | 0.79 | 33.2 | 25.39
2019-09-04 | 11:10 | 11.4297 | 0.07 | 1.07 | -0.28 | 0.72 | -0.23 | 0.77 | 33.2 | 24.41
2019-09-04 | 11:10 | 11.5273 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 32.23 | 24.41
2019-09-04 | 11:10 | 11.6289 | 0.06 | 1.06 | -0.27 | 0.73 | -0.23 | 0.77 | 32.23 | 23.44
2019-09-04 | 11:10 | 11.7383 | 0.06 | 1.06 | -0.28 | 0.72 | -0.22 | 0.78 | 32.23 | 23.44
2019-09-04 | 11:10 | 11.8398 | 0.02 | 1.02 | -0.23 | 0.77 | -0.21 | 0.79 | 33.2 | 25.39
2019-09-04 | 11:10 | 11.9492 | 0 | 1 | -0.21 | 0.79 | -0.21 | 0.79 | 32.23 | 23.44
2019-09-04 | 11:10 | 12.0508 | 0.01 | 1.01 | -0.22 | 0.78 | -0.2 | 0.8 | 33.2 | 24.41
2019-09-04 | 11:10 | 12.1484 | 0.01 | 1.01 | -0.22 | 0.78 | -0.2 | 0.8 | 33.2 | 24.41
2019-09-04 | 11:10 | 12.25 | 0.05 | 1.05 | -0.24 | 0.76 | -0.2 | 0.8 | 32.23 | 23.44
2019-09-04 | 11:10 | 12.3477 | 0.06 | 1.06 | -0.24 | 0.76 | -0.2 | 0.8 | 32.23 | 24.41
2019-09-04 | 11:10 | 12.4609 | 0.07 | 1.07 | -0.25 | 0.75 | -0.22 | 0.78 | 33.2 | 24.41
2019-09-04 | 11:10 | 12.5586 | 0.08 | 1.08 | -0.25 | 0.75 | -0.21 | 0.79 | 34.18 | 24.41
2019-09-04 | 11:10 | 12.6602 | 0.07 | 1.07 | -0.25 | 0.75 | -0.21 | 0.79 | 32.23 | 24.41
2019-09-04 | 11:10 | 12.7695 | 0.08 | 1.08 | -0.26 | 0.74 | -0.22 | 0.78 | 32.23 | 23.44
2019-09-04 | 11:10 | 12.8711 | 0.07 | 1.07 | -0.28 | 0.72 | -0.22 | 0.78 | 33.2 | 26.37
2019-09-04 | 11:10 | 12.9688 | 0.08 | 1.08 | -0.27 | 0.73 | -0.23 | 0.77 | 32.23 | 23.44
2019-09-04 | 11:10 | 13.0781 | 0.08 | 1.08 | -0.29 | 0.71 | -0.23 | 0.77 | 31.25 | 24.41
2019-09-04 | 11:10 | 13.1797 | 0.06 | 1.06 | -0.31 | 0.69 | -0.26 | 0.74 | 32.23 | 24.41
2019-09-04 | 11:10 | 13.2773 | 0.05 | 1.05 | -0.27 | 0.73 | -0.26 | 0.74 | 33.2 | 25.39
2019-09-04 | 11:10 | 13.3789 | 0.02 | 1.02 | -0.26 | 0.74 | -0.24 | 0.76 | 35.16 | 25.39
2019-09-04 | 11:10 | 13.4883 | 0 | 1 | -0.26 | 0.74 | -0.24 | 0.76 | 38.09 | 23.44
2019-09-04 | 11:10 | 13.5898 | -0.01 | 0.99 | -0.25 | 0.75 | -0.24 | 0.76 | 40.04 | 23.44
2019-09-04 | 11:10 | 13.6875 | -0.01 | 0.99 | -0.26 | 0.74 | -0.24 | 0.76 | 39.06 | 24.41
2019-09-04 | 11:10 | 13.7891 | 0.05 | 1.05 | -0.31 | 0.69 | -0.26 | 0.74 | 41.02 | 24.41
2019-09-04 | 11:10 | 13.8984 | 0.06 | 1.06 | -0.32 | 0.68 | -0.28 | 0.72 | 43.95 | 24.41
2019-09-04 | 11:10 | 14 | 0.07 | 1.07 | -0.34 | 0.66 | -0.3 | 0.7 | 46.88 | 25.39
2019-09-04 | 11:10 | 14.0977 | 0.09 | 1.09 | -0.34 | 0.66 | -0.3 | 0.7 | 48.83 | 23.44
2019-09-04 | 11:10 | 14.1992 | 0.07 | 1.07 | -0.36 | 0.64 | -0.31 | 0.69 | 51.76 | 25.39
2019-09-04 | 11:10 | 14.3086 | 0.06 | 1.06 | -0.36 | 0.64 | -0.33 | 0.67 | 53.71 | 25.39
2019-09-04 | 11:10 | 14.4102 | 0.06 | 1.06 | -0.38 | 0.62 | -0.34 | 0.66 | 55.66 | 24.41
2019-09-04 | 11:10 | 14.5078 | 0.07 | 1.07 | -0.39 | 0.61 | -0.35 | 0.65 | 56.64 | 24.41
2019-09-04 | 11:10 | 14.6211 | 0.06 | 1.06 | -0.39 | 0.61 | -0.35 | 0.65 | 57.62 | 23.44
2019-09-04 | 11:10 | 14.7188 | 0.06 | 1.06 | -0.4 | 0.6 | -0.36 | 0.64 | 61.52 | 26.37
2019-09-04 | 11:10 | 14.8203 | 0.02 | 1.02 | -0.35 | 0.65 | -0.37 | 0.63 | 63.48 | 26.37
2019-09-04 | 11:10 | 14.918 | 0 | 1 | -0.33 | 0.67 | -0.35 | 0.65 | 65.43 | 25.39
2019-09-04 | 11:10 | 15.0273 | -0.02 | 0.98 | -0.34 | 0.66 | -0.36 | 0.64 | 64.45 | 24.41
2019-09-04 | 11:10 | 15.1289 | -0.03 | 0.97 | -0.34 | 0.66 | -0.35 | 0.65 | 56.64 | 24.41
2019-09-04 | 11:10 | 15.2305 | -0.01 | 0.99 | -0.35 | 0.65 | -0.35 | 0.65 | 64.45 | 24.41
2019-09-04 | 11:10 | 15.3281 | 0.05 | 1.05 | -0.41 | 0.59 | -0.37 | 0.63 | 68.36 | 24.41
2019-09-04 | 11:10 | 15.4375 | 0.1 | 1.1 | -0.42 | 0.58 | -0.37 | 0.63 | 70.31 | 25.39
2019-09-04 | 11:10 | 15.5391 | 0.07 | 1.07 | -0.43 | 0.57 | -0.4 | 0.6 | 70.31 | 23.44
2019-09-04 | 11:10 | 15.6406 | 0.09 | 1.09 | -0.45 | 0.55 | -0.41 | 0.59 | 71.29 | 26.37
2019-09-04 | 11:10 | 15.75 | 0.07 | 1.07 | -0.46 | 0.54 | -0.41 | 0.59 | 70.31 | 25.39
2019-09-04 | 11:10 | 15.8477 | 0.08 | 1.08 | -0.46 | 0.54 | -0.41 | 0.59 | 68.36 | 25.39
2019-09-04 | 11:10 | 15.9492 | 0.08 | 1.08 | -0.46 | 0.54 | -0.43 | 0.57 | 68.36 | 23.44
2019-09-04 | 11:10 | 16.0508 | 0.06 | 1.06 | -0.48 | 0.52 | -0.41 | 0.59 | 71.29 | 25.39
2019-09-04 | 11:10 | 16.1602 | 0.07 | 1.07 | -0.47 | 0.53 | -0.43 | 0.57 | 73.24 | 25.39
2019-09-04 | 11:10 | 16.2578 | 0.07 | 1.07 | -0.48 | 0.52 | -0.43 | 0.57 | 72.27 | 26.37
2019-09-04 | 11:10 | 16.3594 | 0.01 | 1.01 | -0.39 | 0.61 | -0.4 | 0.6 | 73.24 | 24.41
2019-09-04 | 11:10 | 16.4688 | -0.01 | 0.99 | -0.39 | 0.61 | -0.4 | 0.6 | 73.24 | 25.39
2019-09-04 | 11:10 | 16.5703 | -0.04 | 0.96 | -0.37 | 0.63 | -0.4 | 0.6 | 62.5 | 25.39
2019-09-04 | 11:10 | 16.668 | -0.03 | 0.97 | -0.37 | 0.63 | -0.39 | 0.61 | 68.36 | 25.39
2019-09-04 | 11:10 | 16.7695 | 0.04 | 1.04 | -0.46 | 0.54 | -0.42 | 0.58 | 73.24 | 25.39
2019-09-04 | 11:10 | 16.8789 | 0.08 | 1.08 | -0.47 | 0.53 | -0.43 | 0.57 | 71.29 | 24.41
2019-09-04 | 11:10 | 16.9805 | 0.06 | 1.06 | -0.48 | 0.52 | -0.44 | 0.56 | 72.27 | 25.39
2019-09-04 | 11:10 | 17.0781 | 0.08 | 1.08 | -0.49 | 0.51 | -0.44 | 0.56 | 74.22 | 25.39
2019-09-04 | 11:10 | 17.1797 | 0.06 | 1.06 | -0.49 | 0.51 | -0.45 | 0.55 | 72.27 | 24.41
2019-09-04 | 11:10 | 17.2891 | 0.1 | 1.1 | -0.49 | 0.51 | -0.46 | 0.54 | 68.36 | 24.41
2019-09-04 | 11:10 | 17.3906 | 0.05 | 1.05 | -0.5 | 0.5 | -0.46 | 0.54 | 71.29 | 25.39
2019-09-04 | 11:10 | 17.4883 | 0.06 | 1.06 | -0.5 | 0.5 | -0.46 | 0.54 | 70.31 | 24.41
2019-09-04 | 11:10 | 17.5898 | 0.08 | 1.08 | -0.52 | 0.48 | -0.47 | 0.53 | 72.27 | 25.39
2019-09-04 | 11:10 | 17.6992 | 0.08 | 1.08 | -0.51 | 0.49 | -0.48 | 0.52 | 70.31 | 25.39
2019-09-04 | 11:10 | 17.8008 | 0.06 | 1.06 | -0.51 | 0.49 | -0.48 | 0.52 | 71.29 | 26.37
2019-09-04 | 11:10 | 17.9102 | 0 | 1 | -0.42 | 0.58 | -0.46 | 0.54 | 71.29 | 26.37
2019-09-04 | 11:10 | 18.0078 | -0.03 | 0.97 | -0.42 | 0.58 | -0.45 | 0.55 | 72.27 | 26.37
2019-09-04 | 11:10 | 18.1094 | -0.09 | 0.91 | -0.39 | 0.61 | -0.44 | 0.56 | 70.31 | 26.37
2019-09-04 | 11:10 | 18.2109 | -0.05 | 0.95 | -0.4 | 0.6 | -0.44 | 0.56 | 70.31 | 27.34
2019-09-04 | 11:10 | 18.3203 | 0.05 | 1.05 | -0.51 | 0.49 | -0.47 | 0.53 | 69.34 | 26.37
2019-09-04 | 11:10 | 18.418 | 0.05 | 1.05 | -0.52 | 0.48 | -0.47 | 0.53 | 70.31 | 26.37
2019-09-04 | 11:10 | 18.5195 | 0.06 | 1.06 | -0.52 | 0.48 | -0.47 | 0.53 | 71.29 | 27.34
2019-09-04 | 11:10 | 18.6211 | 0.07 | 1.07 | -0.53 | 0.47 | -0.5 | 0.5 | 71.29 | 28.32
2019-09-04 | 11:10 | 18.7188 | 0.06 | 1.06 | -0.53 | 0.47 | -0.48 | 0.52 | 71.29 | 28.32
2019-09-04 | 11:10 | 18.8281 | 0.07 | 1.07 | -0.53 | 0.47 | -0.5 | 0.5 | 71.29 | 27.34
2019-09-04 | 11:10 | 18.9297 | 0.09 | 1.09 | -0.54 | 0.46 | -0.49 | 0.51 | 71.29 | 29.3
2019-09-04 | 11:10 | 19.0273 | 0.08 | 1.08 | -0.54 | 0.46 | -0.5 | 0.5 | 71.29 | 28.32
2019-09-04 | 11:10 | 19.1289 | 0.06 | 1.06 | -0.54 | 0.46 | -0.5 | 0.5 | 70.31 | 28.32
2019-09-04 | 11:10 | 19.2383 | 0.08 | 1.08 | -0.56 | 0.44 | -0.5 | 0.5 | 71.29 | 29.3
2019-09-04 | 11:10 | 19.3398 | -0.01 | 0.99 | -0.46 | 0.54 | -0.49 | 0.51 | 70.31 | 28.32
2019-09-04 | 11:10 | 19.4492 | -0.03 | 0.97 | -0.45 | 0.55 | -0.48 | 0.52 | 71.29 | 31.25
2019-09-04 | 11:10 | 19.5508 | -0.07 | 0.93 | -0.42 | 0.58 | -0.47 | 0.53 | 69.34 | 29.3
2019-09-04 | 11:10 | 19.6484 | -0.04 | 0.96 | -0.43 | 0.57 | -0.47 | 0.53 | 70.31 | 29.3
2019-09-04 | 11:10 | 19.75 | 0.04 | 1.04 | -0.51 | 0.49 | -0.48 | 0.52 | 72.27 | 30.27
2019-09-04 | 11:10 | 19.8477 | 0.06 | 1.06 | -0.55 | 0.45 | -0.5 | 0.5 | 69.34 | 29.3
2019-09-04 | 11:10 | 19.9609 | 0.07 | 1.07 | -0.54 | 0.46 | -0.52 | 0.48 | 70.31 | 29.3
2019-09-04 | 11:10 | 20.0586 | 0.07 | 1.07 | -0.56 | 0.44 | -0.5 | 0.5 | 69.34 | 30.27
2019-09-04 | 11:10 | 20.1602 | 0.07 | 1.07 | -0.57 | 0.43 | -0.52 | 0.48 | 69.34 | 29.3
2019-09-04 | 11:10 | 20.2578 | 0.06 | 1.06 | -0.57 | 0.43 | -0.52 | 0.48 | 69.34 | 30.27
2019-09-04 | 11:10 | 20.3711 | 0.08 | 1.08 | -0.55 | 0.45 | -0.52 | 0.48 | 70.31 | 30.27
2019-09-04 | 11:10 | 20.4688 | 0.08 | 1.08 | -0.56 | 0.44 | -0.52 | 0.48 | 71.29 | 31.25
2019-09-04 | 11:10 | 20.5781 | 0.06 | 1.06 | -0.57 | 0.43 | -0.51 | 0.49 | 69.34 | 30.27
2019-09-04 | 11:10 | 20.6797 | 0.07 | 1.07 | -0.57 | 0.43 | -0.53 | 0.47 | 69.34 | 30.27
2019-09-04 | 11:10 | 20.7773 | 0.09 | 1.09 | -0.57 | 0.43 | -0.53 | 0.47 | 70.31 | 31.25
2019-09-04 | 11:10 | 20.8789 | 0.03 | 1.03 | -0.52 | 0.48 | -0.5 | 0.5 | 71.29 | 31.25
2019-09-04 | 11:10 | 20.9883 | -0.03 | 0.97 | -0.46 | 0.54 | -0.51 | 0.49 | 70.31 | 31.25
2019-09-04 | 11:10 | 21.0898 | -0.06 | 0.94 | -0.45 | 0.55 | -0.5 | 0.5 | 69.34 | 32.23
2019-09-04 | 11:10 | 21.1875 | -0.06 | 0.94 | -0.44 | 0.56 | -0.5 | 0.5 | 71.29 | 33.2
2019-09-04 | 11:10 | 21.2891 | 0.05 | 1.05 | -0.56 | 0.44 | -0.51 | 0.49 | 70.31 | 32.23
2019-09-04 | 11:10 | 21.3984 | 0.06 | 1.06 | -0.57 | 0.43 | -0.54 | 0.46 | 70.31 | 32.23
2019-09-04 | 11:10 | 21.5 | 0.06 | 1.06 | -0.58 | 0.42 | -0.52 | 0.48 | 70.31 | 33.2
2019-09-04 | 11:10 | 21.5977 | 0.06 | 1.06 | -0.58 | 0.42 | -0.54 | 0.46 | 70.31 | 34.18
2019-09-04 | 11:10 | 21.7109 | 0.07 | 1.07 | -0.59 | 0.41 | -0.55 | 0.45 | 69.34 | 32.23
2019-09-04 | 11:10 | 21.8086 | 0.08 | 1.08 | -0.59 | 0.41 | -0.54 | 0.46 | 69.34 | 32.23
2019-09-04 | 11:10 | 21.9102 | 0.07 | 1.07 | -0.58 | 0.42 | -0.53 | 0.47 | 70.31 | 33.2
2019-09-04 | 11:10 | 22.0078 | 0.05 | 1.05 | -0.59 | 0.41 | -0.55 | 0.45 | 68.36 | 33.2
2019-09-04 | 11:10 | 22.1211 | 0.08 | 1.08 | -0.59 | 0.41 | -0.55 | 0.45 | 70.31 | 33.2
2019-09-04 | 11:10 | 22.2188 | 0.06 | 1.06 | -0.6 | 0.4 | -0.56 | 0.44 | 70.31 | 32.23
2019-09-04 | 11:10 | 22.3203 | 0.05 | 1.05 | -0.57 | 0.43 | -0.55 | 0.45 | 69.34 | 35.16
2019-09-04 | 11:10 | 22.418 | -0.02 | 0.98 | -0.48 | 0.52 | -0.52 | 0.48 | 70.31 | 34.18
2019-09-04 | 11:10 | 22.5273 | -0.05 | 0.95 | -0.45 | 0.55 | -0.52 | 0.48 | 70.31 | 33.2
2019-09-04 | 11:10 | 22.6289 | -0.08 | 0.92 | -0.44 | 0.56 | -0.5 | 0.5 | 70.31 | 35.16
2019-09-04 | 11:10 | 22.7305 | -0.05 | 0.95 | -0.46 | 0.54 | -0.51 | 0.49 | 69.34 | 36.13
2019-09-04 | 11:10 | 22.8281 | 0.04 | 1.04 | -0.59 | 0.41 | -0.53 | 0.47 | 71.29 | 36.13
2019-09-04 | 11:10 | 22.9375 | 0.08 | 1.08 | -0.6 | 0.4 | -0.54 | 0.46 | 69.34 | 35.16
2019-09-04 | 11:10 | 23.0391 | 0.08 | 1.08 | -0.6 | 0.4 | -0.55 | 0.45 | 69.34 | 34.18
2019-09-04 | 11:10 | 23.1406 | 0.07 | 1.07 | -0.6 | 0.4 | -0.55 | 0.45 | 69.34 | 36.13
2019-09-04 | 11:10 | 23.25 | 0.07 | 1.07 | -0.61 | 0.39 | -0.56 | 0.44 | 68.36 | 35.16
2019-09-04 | 11:10 | 23.3477 | 0.07 | 1.07 | -0.61 | 0.39 | -0.56 | 0.44 | 69.34 | 35.16
2019-09-04 | 11:10 | 23.4492 | 0.07 | 1.07 | -0.6 | 0.4 | -0.55 | 0.45 | 69.34 | 36.13
2019-09-04 | 11:10 | 23.5508 | 0.07 | 1.07 | -0.6 | 0.4 | -0.56 | 0.44 | 69.34 | 36.13
2019-09-04 | 11:10 | 23.6602 | 0.06 | 1.06 | -0.61 | 0.39 | -0.58 | 0.42 | 69.34 | 36.13
2019-09-04 | 11:10 | 23.7578 | 0.07 | 1.07 | -0.61 | 0.39 | -0.57 | 0.43 | 69.34 | 35.16
2019-09-04 | 11:10 | 23.8711 | 0 | 1 | -0.53 | 0.47 | -0.55 | 0.45 | 68.36 | 36.13
2019-09-04 | 11:10 | 23.9688 | -0.05 | 0.95 | -0.46 | 0.54 | -0.54 | 0.46 | 69.34 | 37.11
2019-09-04 | 11:10 | 24.0703 | -0.07 | 0.93 | -0.46 | 0.54 | -0.52 | 0.48 | 70.31 | 36.13
2019-09-04 | 11:10 | 24.168 | -0.09 | 0.91 | -0.46 | 0.54 | -0.53 | 0.47 | 71.29 | 37.11
2019-09-04 | 11:10 | 24.2773 | 0.04 | 1.04 | -0.57 | 0.43 | -0.54 | 0.46 | 72.27 | 36.13
2019-09-04 | 11:10 | 24.3789 | 0.07 | 1.07 | -0.61 | 0.39 | -0.56 | 0.44 | 69.34 | 37.11
2019-09-04 | 11:10 | 24.4805 | 0.06 | 1.06 | -0.6 | 0.4 | -0.56 | 0.44 | 69.34 | 37.11
2019-09-04 | 11:10 | 24.5781 | 0.06 | 1.06 | -0.61 | 0.39 | -0.56 | 0.44 | 68.36 | 36.13
2019-09-04 | 11:10 | 24.6797 | 0.08 | 1.08 | -0.6 | 0.4 | -0.56 | 0.44 | 68.36 | 37.11
2019-09-04 | 11:10 | 24.7891 | 0.06 | 1.06 | -0.62 | 0.38 | -0.57 | 0.43 | 68.36 | 39.06
2019-09-04 | 11:10 | 24.8906 | 0.07 | 1.07 | -0.62 | 0.38 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 11:10 | 24.9883 | 0.06 | 1.06 | -0.61 | 0.39 | -0.57 | 0.43 | 68.36 | 37.11
2019-09-04 | 11:10 | 25.0898 | 0.07 | 1.07 | -0.62 | 0.38 | -0.59 | 0.41 | 69.34 | 37.11
2019-09-04 | 11:10 | 25.1992 | 0.07 | 1.07 | -0.62 | 0.38 | -0.57 | 0.43 | 68.36 | 37.11
2019-09-04 | 11:10 | 25.3008 | 0.06 | 1.06 | -0.62 | 0.38 | -0.58 | 0.42 | 68.36 | 39.06
2019-09-04 | 11:10 | 25.4102 | -0.03 | 0.97 | -0.51 | 0.49 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 11:10 | 25.5078 | -0.07 | 0.93 | -0.47 | 0.53 | -0.54 | 0.46 | 68.36 | 38.09
2019-09-04 | 11:10 | 25.6094 | -0.09 | 0.91 | -0.46 | 0.54 | -0.52 | 0.48 | 69.34 | 38.09
2019-09-04 | 11:10 | 25.7109 | -0.08 | 0.92 | -0.44 | 0.56 | -0.54 | 0.46 | 69.34 | 38.09
2019-09-04 | 11:10 | 25.8203 | 0.05 | 1.05 | -0.61 | 0.39 | -0.56 | 0.44 | 68.36 | 38.09
2019-09-04 | 11:10 | 25.918 | 0.06 | 1.06 | -0.61 | 0.39 | -0.56 | 0.44 | 67.38 | 37.11
2019-09-04 | 11:10 | 26.0195 | 0.04 | 1.04 | -0.62 | 0.38 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 11:10 | 26.1211 | 0.07 | 1.07 | -0.62 | 0.38 | -0.58 | 0.42 | 68.36 | 38.09
2019-09-04 | 11:10 | 26.2305 | 0.08 | 1.08 | -0.62 | 0.38 | -0.56 | 0.44 | 67.38 | 39.06
2019-09-04 | 11:10 | 26.3281 | 0.08 | 1.08 | -0.63 | 0.37 | -0.58 | 0.42 | 69.34 | 39.06
2019-09-04 | 11:10 | 26.4297 | 0.07 | 1.07 | -0.62 | 0.38 | -0.57 | 0.43 | 69.34 | 39.06
2019-09-04 | 11:10 | 26.5273 | 0.1 | 1.1 | -0.62 | 0.38 | -0.58 | 0.42 | 68.36 | 38.09
2019-09-04 | 11:10 | 26.6406 | 0.06 | 1.06 | -0.63 | 0.37 | -0.59 | 0.41 | 68.36 | 39.06
2019-09-04 | 11:10 | 26.7383 | 0.06 | 1.06 | -0.63 | 0.37 | -0.59 | 0.41 | 70.31 | 41.02
2019-09-04 | 11:10 | 26.8398 | 0.02 | 1.02 | -0.58 | 0.42 | -0.59 | 0.41 | 69.34 | 39.06
2019-09-04 | 11:10 | 26.9492 | -0.03 | 0.97 | -0.53 | 0.47 | -0.57 | 0.43 | 69.34 | 39.06
2019-09-04 | 11:10 | 27.0508 | -0.07 | 0.93 | -0.47 | 0.53 | -0.56 | 0.44 | 69.34 | 40.04
2019-09-04 | 11:10 | 27.1484 | -0.09 | 0.91 | -0.49 | 0.51 | -0.56 | 0.44 | 68.36 | 38.09
2019-09-04 | 11:10 | 27.25 | 0.03 | 1.03 | -0.55 | 0.45 | -0.58 | 0.42 | 69.34 | 39.06
2019-09-04 | 11:10 | 27.3594 | 0.04 | 1.04 | -0.63 | 0.37 | -0.58 | 0.42 | 69.34 | 39.06
2019-09-04 | 11:10 | 27.4609 | 0.07 | 1.07 | -0.62 | 0.38 | -0.59 | 0.41 | 68.36 | 39.06
2019-09-04 | 11:10 | 27.5586 | 0.06 | 1.06 | -0.63 | 0.37 | -0.58 | 0.42 | 69.34 | 39.06
2019-09-04 | 11:10 | 27.6602 | 0.07 | 1.07 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 11:10 | 27.7695 | 0.06 | 1.06 | -0.64 | 0.36 | -0.6 | 0.4 | 68.36 | 39.06
2019-09-04 | 11:10 | 27.8711 | 0.08 | 1.08 | -0.63 | 0.37 | -0.59 | 0.41 | 68.36 | 40.04
2019-09-04 | 11:10 | 27.9688 | 0.09 | 1.09 | -0.64 | 0.36 | -0.59 | 0.41 | 68.36 | 38.09
2019-09-04 | 11:10 | 28.0781 | 0.09 | 1.09 | -0.64 | 0.36 | -0.59 | 0.41 | 69.34 | 40.04
2019-09-04 | 11:10 | 28.1797 | 0.07 | 1.07 | -0.63 | 0.37 | -0.61 | 0.39 | 68.36 | 38.09
2019-09-04 | 11:10 | 28.2773 | 0.08 | 1.08 | -0.63 | 0.37 | -0.6 | 0.4 | 68.36 | 40.04
2019-09-04 | 11:10 | 28.3789 | -0.02 | 0.98 | -0.55 | 0.45 | -0.58 | 0.42 | 68.36 | 39.06
2019-09-04 | 11:10 | 28.4883 | -0.08 | 0.92 | -0.5 | 0.5 | -0.55 | 0.45 | 69.34 | 40.04
2019-09-04 | 11:10 | 28.5898 | -0.08 | 0.92 | -0.47 | 0.53 | -0.56 | 0.44 | 69.34 | 39.06
2019-09-04 | 11:10 | 28.6875 | -0.08 | 0.92 | -0.47 | 0.53 | -0.54 | 0.46 | 68.36 | 38.09
2019-09-04 | 11:10 | 28.8008 | 0.05 | 1.05 | -0.6 | 0.4 | -0.55 | 0.45 | 69.34 | 40.04
2019-09-04 | 11:10 | 28.8984 | 0.04 | 1.04 | -0.61 | 0.39 | -0.58 | 0.42 | 67.38 | 38.09
2019-09-04 | 11:10 | 29 | 0.07 | 1.07 | -0.62 | 0.38 | -0.57 | 0.43 | 69.34 | 40.04
2019-09-04 | 11:10 | 29.0977 | 0.06 | 1.06 | -0.62 | 0.38 | -0.57 | 0.43 | 69.34 | 39.06
2019-09-04 | 11:10 | 29.2109 | 0.07 | 1.07 | -0.62 | 0.38 | -0.58 | 0.42 | 68.36 | 38.09
2019-09-04 | 11:10 | 29.3086 | 0.09 | 1.09 | -0.62 | 0.38 | -0.58 | 0.42 | 69.34 | 38.09
2019-09-04 | 11:10 | 29.4102 | 0.06 | 1.06 | -0.63 | 0.37 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 11:10 | 29.5078 | 0.08 | 1.08 | -0.62 | 0.38 | -0.58 | 0.42 | 67.38 | 38.09
2019-09-04 | 11:10 | 29.6211 | 0.05 | 1.05 | -0.62 | 0.38 | -0.57 | 0.43 | 67.38 | 38.09
2019-09-04 | 11:10 | 29.7188 | 0.07 | 1.07 | -0.62 | 0.38 | -0.58 | 0.42 | 69.34 | 39.06
2019-09-04 | 11:10 | 29.8203 | 0.05 | 1.05 | -0.61 | 0.39 | -0.57 | 0.43 | 67.38 | 39.06
2019-09-04 | 11:10 | 29.9297 | -0.02 | 0.98 | -0.52 | 0.48 | -0.56 | 0.44 | 68.36 | 39.06
2019-09-04 | 11:10 | 30.0273 | -0.08 | 0.92 | -0.49 | 0.51 | -0.55 | 0.45 | 69.34 | 40.04
2019-09-04 | 11:10 | 30.1289 | -0.06 | 0.94 | -0.49 | 0.51 | -0.55 | 0.45 | 68.36 | 38.09
2019-09-04 | 11:10 | 30.2305 | -0.09 | 0.91 | 0.01 |  | -0.54 | 0.46 | 70.31 | 39.06 | anomalous heat exchanger value, removed from plot and analysis
2019-09-04 | 11:10 | 30.3398 | 0.04 | 1.04 | -0.63 | 0.37 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 11:10 | 30.4375 | 0.04 | 1.04 | -0.63 | 0.37 | -0.6 | 0.4 | 67.38 | 38.09
2019-09-04 | 11:10 | 30.5391 | 0.05 | 1.05 | -0.64 | 0.36 | -0.6 | 0.4 | 67.38 | 38.09
2019-09-04 | 11:10 | 30.6406 | 0.09 | 1.09 | -0.65 | 0.35 | -0.59 | 0.41 | 69.34 | 38.09
2019-09-04 | 11:10 | 30.75 | 0.07 | 1.07 | -0.63 | 0.37 | -0.6 | 0.4 | 68.36 | 40.04
2019-09-04 | 11:10 | 30.8477 | 0.07 | 1.07 | -0.64 | 0.36 | -0.6 | 0.4 | 67.38 | 38.09
2019-09-04 | 11:10 | 30.9492 | 0.07 | 1.07 | -0.66 | 0.34 | -0.61 | 0.39 | 69.34 | 38.09
2019-09-04 | 11:10 | 31.0508 | 0.06 | 1.06 | -0.65 | 0.35 | -0.61 | 0.39 | 69.34 | 38.09
2019-09-04 | 11:10 | 31.1602 | 0.08 | 1.08 | -0.66 | 0.34 | -0.6 | 0.4 | 67.38 | 38.09
2019-09-04 | 11:10 | 31.2578 | 0.06 | 1.06 | -0.66 | 0.34 | -0.61 | 0.39 | 68.36 | 39.06
2019-09-04 | 11:10 | 31.3594 | 0.01 | 1.01 | -0.6 | 0.4 | -0.61 | 0.39 | 68.36 | 38.09
2019-09-04 | 11:10 | 31.4688 | -0.06 | 0.94 | -0.52 | 0.48 | -0.6 | 0.4 | 69.34 | 40.04
2019-09-04 | 11:10 | 31.5703 | -0.07 | 0.93 | -0.51 | 0.49 | -0.61 | 0.39 | 68.36 | 38.09
2019-09-04 | 11:10 | 31.668 | -0.07 | 0.93 | -0.5 | 0.5 | -0.6 | 0.4 | 67.38 | 38.09
2019-09-04 | 11:10 | 31.7773 | 0.02 | 1.02 | -0.63 | 0.37 | -0.61 | 0.39 | 67.38 | 38.09
2019-09-04 | 11:10 | 31.8789 | 0.05 | 1.05 | -0.65 | 0.35 | -0.61 | 0.39 | 68.36 | 40.04
2019-09-04 | 11:10 | 31.9805 | 0.06 | 1.06 | -0.65 | 0.35 | -0.61 | 0.39 | 67.38 | 39.06
2019-09-04 | 11:10 | 32.0781 | 0.06 | 1.06 | -0.65 | 0.35 | -0.6 | 0.4 | 67.38 | 37.11
2019-09-04 | 11:10 | 32.1875 | 0.06 | 1.06 | -0.67 | 0.33 | -0.61 | 0.39 | 67.38 | 38.09
2019-09-04 | 11:10 | 32.2891 | 0.07 | 1.07 | -0.65 | 0.35 | -0.61 | 0.39 | 67.38 | 38.09
2019-09-04 | 11:10 | 32.3906 | 0.06 | 1.06 | -0.66 | 0.34 | -0.62 | 0.38 | 69.34 | 39.06
2019-09-04 | 11:10 | 32.4883 | 0.06 | 1.06 | -0.66 | 0.34 | -0.61 | 0.39 | 67.38 | 37.11
2019-09-04 | 11:10 | 32.5898 | 0.07 | 1.07 | -0.65 | 0.35 | -0.61 | 0.39 | 67.38 | 38.09
2019-09-04 | 11:10 | 32.6992 | 0.06 | 1.06 | -0.66 | 0.34 | -0.62 | 0.38 | 67.38 | 38.09
2019-09-04 | 11:10 | 32.8008 | 0.09 | 1.09 | -0.65 | 0.35 | -0.62 | 0.38 | 67.38 | 38.09
2019-09-04 | 11:10 | 32.9102 | -0.02 | 0.98 | -0.56 | 0.44 | -0.61 | 0.39 | 68.36 | 39.06
2019-09-04 | 11:10 | 33.0078 | -0.04 | 0.96 | -0.53 | 0.47 | -0.59 | 0.41 | 68.36 | 39.06
2019-09-04 | 11:10 | 33.1094 | -0.09 | 0.91 | -0.49 | 0.51 | -0.58 | 0.42 | 67.38 | 38.09
2019-09-04 | 11:10 | 33.2109 | -0.09 | 0.91 | -0.5 | 0.5 | -0.57 | 0.43 | 68.36 | 38.09
2019-09-04 | 11:10 | 33.3086 | 0.07 | 1.07 | -0.63 | 0.37 | -0.59 | 0.41 | 68.36 | 37.11
2019-09-04 | 11:10 | 33.418 | 0.05 | 1.05 | -0.64 | 0.36 | -0.61 | 0.39 | 67.38 | 38.09
2019-09-04 | 11:10 | 33.5195 | 0.06 | 1.06 | -0.65 | 0.35 | -0.6 | 0.4 | 70.31 | 40.04
2019-09-04 | 11:10 | 33.6289 | 0.07 | 1.07 | -0.65 | 0.35 | -0.61 | 0.39 | 67.38 | 38.09
2019-09-04 | 11:10 | 33.7305 | 0.06 | 1.06 | -0.64 | 0.36 | -0.6 | 0.4 | 68.36 | 38.09
2019-09-04 | 11:10 | 33.8281 | 0.07 | 1.07 | -0.64 | 0.36 | -0.6 | 0.4 | 67.38 | 38.09
2019-09-04 | 11:10 | 33.9297 | 0.06 | 1.06 | -0.65 | 0.35 | -0.62 | 0.38 | 67.38 | 38.09
2019-09-04 | 11:10 | 34.0391 | 0.08 | 1.08 | -0.66 | 0.34 | -0.63 | 0.37 | 67.38 | 37.11
2019-09-04 | 11:10 | 34.1406 | 0.07 | 1.07 | -0.65 | 0.35 | -0.6 | 0.4 | 68.36 | 38.09
2019-09-04 | 11:10 | 34.2383 | 0.07 | 1.07 | -0.64 | 0.36 | -0.6 | 0.4 | 68.36 | 38.09
2019-09-04 | 11:10 | 34.3398 | 0.04 | 1.04 | -0.62 | 0.38 | -0.61 | 0.39 | 69.34 | 38.09
2019-09-04 | 11:10 | 34.4492 | -0.04 | 0.96 | -0.55 | 0.45 | -0.58 | 0.42 | 68.36 | 38.09
2019-09-04 | 11:10 | 34.5508 | -0.08 | 0.92 | -0.53 | 0.47 | -0.58 | 0.42 | 67.38 | 38.09
2019-09-04 | 11:10 | 34.6484 | -0.08 | 0.92 | -0.51 | 0.49 | -0.59 | 0.41 | 68.36 | 39.06
2019-09-04 | 11:10 | 34.75 | -0.03 | 0.97 | -0.57 | 0.43 | -0.57 | 0.43 | 69.34 | 39.06
2019-09-04 | 11:10 | 34.8594 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 67.38 | 38.09
2019-09-04 | 11:10 | 34.9609 | 0.05 | 1.05 | -0.65 | 0.35 | -0.63 | 0.37 | 68.36 | 38.09
2019-09-04 | 11:10 | 35.0586 | 0.07 | 1.07 | -0.66 | 0.34 | -0.62 | 0.38 | 69.34 | 38.09
2019-09-04 | 11:10 | 35.168 | 0.07 | 1.07 | -0.65 | 0.35 | -0.61 | 0.39 | 69.34 | 39.06
2019-09-04 | 11:10 | 35.2695 | 0.07 | 1.07 | -0.67 | 0.33 | -0.63 | 0.37 | 68.36 | 38.09
2019-09-04 | 11:10 | 35.3711 | 0.07 | 1.07 | -0.67 | 0.33 | -0.64 | 0.36 | 68.36 | 39.06
2019-09-04 | 11:10 | 35.4688 | 0.08 | 1.08 | -0.67 | 0.33 | -0.62 | 0.38 | 69.34 | 39.06
2019-09-04 | 11:10 | 35.5781 | 0.07 | 1.07 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 38.09
2019-09-04 | 11:10 | 35.6797 | 0.07 | 1.07 | -0.69 | 0.31 | -0.63 | 0.37 | 68.36 | 38.09
2019-09-04 | 11:10 | 35.7773 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 38.09
2019-09-04 | 11:10 | 35.8789 | 0.03 | 1.03 | -0.62 | 0.38 | -0.63 | 0.37 | 69.34 | 38.09
2019-09-04 | 11:10 | 35.9883 | -0.08 | 0.92 | -0.55 | 0.45 | -0.62 | 0.38 | 68.36 | 39.06
2019-09-04 | 11:10 | 36.0898 | -0.08 | 0.92 | -0.54 | 0.46 | -0.62 | 0.38 | 68.36 | 38.09
2019-09-04 | 11:10 | 36.1875 | -0.08 | 0.92 | -0.53 | 0.47 | -0.61 | 0.39 | 69.34 | 38.09
2019-09-04 | 11:10 | 36.2891 | 0.04 | 1.04 | -0.66 | 0.34 | -0.63 | 0.37 | 69.34 | 38.09
2019-09-04 | 11:10 | 36.3984 | 0.05 | 1.05 | -0.68 | 0.32 | -0.63 | 0.37 | 68.36 | 37.11
2019-09-04 | 11:10 | 36.5 | 0.07 | 1.07 | -0.68 | 0.32 | -0.64 | 0.36 | 70.31 | 40.04
2019-09-04 | 11:10 | 36.5977 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 68.36 | 37.11
2019-09-04 | 11:10 | 36.7109 | 0.09 | 1.09 | -0.7 | 0.3 | -0.65 | 0.35 | 69.34 | 38.09
2019-09-04 | 11:10 | 36.8086 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 68.36 | 38.09
2019-09-04 | 11:10 | 36.9102 | 0.08 | 1.08 | -0.7 | 0.3 | -0.66 | 0.34 | 70.31 | 39.06
2019-09-04 | 11:10 | 37.0078 | 0.06 | 1.06 | -0.71 | 0.29 | -0.65 | 0.35 | 68.36 | 38.09
2019-09-04 | 11:10 | 37.1211 | 0.06 | 1.06 | -0.7 | 0.3 | -0.66 | 0.34 | 68.36 | 37.11
2019-09-04 | 11:10 | 37.2188 | 0.08 | 1.08 | -0.71 | 0.29 | -0.67 | 0.33 | 68.36 | 37.11
2019-09-04 | 11:10 | 37.3203 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 70.31 | 38.09
2019-09-04 | 11:10 | 37.4297 | -0.04 | 0.96 | -0.61 | 0.39 | -0.65 | 0.35 | 69.34 | 37.11
2019-09-04 | 11:10 | 37.5273 | -0.09 | 0.91 | -0.55 | 0.45 | -0.64 | 0.36 | 68.36 | 38.09
2019-09-04 | 11:10 | 37.6289 | -0.11 | 0.89 | -0.54 | 0.46 | -0.63 | 0.37 | 69.34 | 37.11
2019-09-04 | 11:10 | 37.7383 | -0.11 | 0.89 | -0.53 | 0.47 | -0.63 | 0.37 | 69.34 | 37.11
2019-09-04 | 11:10 | 37.8398 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 69.34 | 38.09
2019-09-04 | 11:10 | 37.9375 | 0.07 | 1.07 | -0.7 | 0.3 | -0.66 | 0.34 | 69.34 | 38.09
2019-09-04 | 11:10 | 38.0391 | 0.06 | 1.06 | -0.69 | 0.31 | -0.65 | 0.35 | 68.36 | 37.11
2019-09-04 | 11:10 | 38.1406 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 68.36 | 37.11
2019-09-04 | 11:10 | 38.25 | 0.07 | 1.07 | -0.71 | 0.29 | -0.66 | 0.34 | 69.34 | 36.13
2019-09-04 | 11:10 | 38.3477 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 68.36 | 37.11
2019-09-04 | 11:10 | 38.4492 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 38.09
2019-09-04 | 11:10 | 38.5508 | 0.06 | 1.06 | -0.72 | 0.28 | -0.66 | 0.34 | 68.36 | 37.11
2019-09-04 | 11:10 | 38.6602 | 0.07 | 1.07 | -0.72 | 0.28 | -0.67 | 0.33 | 68.36 | 36.13
2019-09-04 | 11:10 | 38.7578 | 0.06 | 1.06 | -0.71 | 0.29 | -0.68 | 0.32 | 61.52 | 38.09
2019-09-04 | 11:10 | 38.8711 | 0.04 | 1.04 | -0.69 | 0.31 | -0.66 | 0.34 | 71.29 | 38.09
2019-09-04 | 11:10 | 38.9688 | -0.06 | 0.94 | -0.59 | 0.41 | -0.65 | 0.35 | 69.34 | 37.11
2019-09-04 | 11:10 | 39.0703 | -0.1 | 0.9 | -0.55 | 0.45 | -0.64 | 0.36 | 71.29 | 38.09
2019-09-04 | 11:10 | 39.168 | -0.1 | 0.9 | -0.53 | 0.47 | -0.64 | 0.36 | 71.29 | 39.06
2019-09-04 | 11:10 | 39.2773 | 0.04 | 1.04 | -0.67 | 0.33 | -0.64 | 0.36 | 70.31 | 36.13
2019-09-04 | 11:10 | 39.3789 | 0.04 | 1.04 | -0.7 | 0.3 | -0.66 | 0.34 | 69.34 | 38.09
2019-09-04 | 11:10 | 39.4805 | 0.07 | 1.07 | -0.7 | 0.3 | -0.67 | 0.33 | 68.36 | 36.13
2019-09-04 | 11:10 | 39.5781 | 0.05 | 1.05 | -0.71 | 0.29 | -0.67 | 0.33 | 68.36 | 37.11
2019-09-04 | 11:10 | 39.6875 | 0.06 | 1.06 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 36.13
2019-09-04 | 11:10 | 39.7891 | 0.07 | 1.07 | -0.72 | 0.28 | -0.67 | 0.33 | 69.34 | 37.11
2019-09-04 | 11:10 | 39.8906 | 0.07 | 1.07 | -0.72 | 0.28 | -0.68 | 0.32 | 69.34 | 38.09
2019-09-04 | 11:10 | 40 | 0.08 | 1.08 | -0.72 | 0.28 | -0.68 | 0.32 | 70.31 | 38.09
2019-09-04 | 11:10 | 40.0977 | 0.06 | 1.06 | -0.72 | 0.28 | -0.68 | 0.32 | 68.36 | 37.11
2019-09-04 | 11:10 | 40.1992 | 0.08 | 1.08 | -0.73 | 0.27 | -0.68 | 0.32 | 68.36 | 36.13
2019-09-04 | 11:10 | 40.3008 | 0.07 | 1.07 | -0.72 | 0.28 | -0.68 | 0.32 | 68.36 | 36.13
2019-09-04 | 11:10 | 40.4102 | 0.01 | 1.01 | -0.66 | 0.34 | -0.67 | 0.33 | 70.31 | 36.13
2019-09-04 | 11:10 | 40.5078 | -0.1 | 0.9 | -0.57 | 0.43 | -0.66 | 0.34 | 69.34 | 37.11
2019-09-04 | 11:10 | 40.6094 | -0.11 | 0.89 | -0.56 | 0.44 | -0.65 | 0.35 | 69.34 | 36.13
2019-09-04 | 11:10 | 40.7109 | -0.12 | 0.88 | -0.53 | 0.47 | -0.64 | 0.36 | 70.31 | 37.11
2019-09-04 | 11:10 | 40.8203 | 0.04 | 1.04 | -0.7 | 0.3 | -0.65 | 0.35 | 70.31 | 37.11
2019-09-04 | 11:10 | 40.918 | 0.04 | 1.04 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 38.09
2019-09-04 | 11:10 | 41.0195 | 0.05 | 1.05 | -0.72 | 0.28 | -0.65 | 0.35 | 69.34 | 37.11
2019-09-04 | 11:10 | 41.1211 | 0.05 | 1.05 | -0.72 | 0.28 | -0.68 | 0.32 | 68.36 | 36.13
2019-09-04 | 11:10 | 41.2305 | 0.06 | 1.06 | -0.72 | 0.28 | -0.67 | 0.33 | 68.36 | 36.13
2019-09-04 | 11:10 | 41.3281 | 0.08 | 1.08 | -0.72 | 0.28 | -0.68 | 0.32 | 69.34 | 36.13
2019-09-04 | 11:10 | 41.4297 | 0.07 | 1.07 | -0.73 | 0.27 | -0.68 | 0.32 | 69.34 | 37.11
2019-09-04 | 11:10 | 41.5391 | 0.06 | 1.06 | -0.73 | 0.27 | -0.69 | 0.31 | 68.36 | 36.13
2019-09-04 | 11:10 | 41.6406 | 0.07 | 1.07 | -0.73 | 0.27 | -0.68 | 0.32 | 70.31 | 36.13
2019-09-04 | 11:10 | 41.7383 | 0.09 | 1.09 | -0.75 | 0.25 | -0.69 | 0.31 | 68.36 | 35.16
2019-09-04 | 11:10 | 41.8398 | 0.09 | 1.09 | -0.73 | 0.27 | -0.69 | 0.31 | 68.36 | 36.13
2019-09-04 | 11:10 | 41.9492 | -0.03 | 0.97 | -0.62 | 0.38 | -0.67 | 0.33 | 69.34 | 36.13
2019-09-04 | 11:10 | 42.0508 | -0.08 | 0.92 | -0.57 | 0.43 | -0.67 | 0.33 | 69.34 | 35.16
2019-09-04 | 11:10 | 42.1602 | -0.11 | 0.89 | -0.54 | 0.46 | -0.66 | 0.34 | 70.31 | 36.13
2019-09-04 | 11:10 | 42.2578 | -0.05 | 0.95 | -0.58 | 0.42 | -0.64 | 0.36 | 70.31 | 37.11
2019-09-04 | 11:10 | 42.3594 | 0.05 | 1.05 | -0.7 | 0.3 | -0.65 | 0.35 | 68.36 | 36.13
2019-09-04 | 11:10 | 42.4609 | 0.05 | 1.05 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 35.16
2019-09-04 | 11:10 | 42.5586 | 0.07 | 1.07 | -0.73 | 0.27 | -0.67 | 0.33 | 68.36 | 38.09
2019-09-04 | 11:10 | 42.668 | 0.05 | 1.05 | -0.73 | 0.27 | -0.67 | 0.33 | 68.36 | 36.13
2019-09-04 | 11:10 | 42.7695 | 0.07 | 1.07 | -0.73 | 0.27 | -0.69 | 0.31 | 68.36 | 36.13
2019-09-04 | 11:10 | 42.8711 | 0.07 | 1.07 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 35.16
2019-09-04 | 11:10 | 42.9688 | 0.07 | 1.07 | -0.75 | 0.25 | -0.68 | 0.32 | 69.34 | 35.16
2019-09-04 | 11:10 | 43.0781 | 0.09 | 1.09 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 37.11
2019-09-04 | 11:10 | 43.1797 | 0.08 | 1.08 | -0.74 | 0.26 | -0.69 | 0.31 | 69.34 | 35.16
2019-09-04 | 11:10 | 43.2773 | 0.08 | 1.08 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 36.13
2019-09-04 | 11:10 | 43.3789 | 0.05 | 1.05 | -0.73 | 0.27 | -0.69 | 0.31 | 70.31 | 37.11
2019-09-04 | 11:10 | 43.4883 | -0.07 | 0.93 | -0.62 | 0.38 | -0.67 | 0.33 | 70.31 | 35.16
2019-09-04 | 11:10 | 43.5898 | -0.1 | 0.9 | -0.56 | 0.44 | -0.67 | 0.33 | 69.34 | 36.13
2019-09-04 | 11:10 | 43.6875 | -0.1 | 0.9 | -0.56 | 0.44 | -0.66 | 0.34 | 69.34 | 36.13
2019-09-04 | 11:10 | 43.8008 | 0.04 | 1.04 | -0.7 | 0.3 | -0.68 | 0.32 | 68.36 | 36.13
2019-09-04 | 11:10 | 43.8984 | 0.06 | 1.06 | -0.72 | 0.28 | -0.68 | 0.32 | 69.34 | 36.13
2019-09-04 | 11:10 | 44 | 0.04 | 1.04 | -0.72 | 0.28 | -0.67 | 0.33 | 68.36 | 35.16
2019-09-04 | 11:10 | 44.0977 | 0.06 | 1.06 | -0.74 | 0.26 | -0.7 | 0.3 | 68.36 | 36.13
2019-09-04 | 11:10 | 44.2109 | 0.07 | 1.07 | -0.74 | 0.26 | -0.68 | 0.32 | 69.34 | 36.13
2019-09-04 | 11:10 | 44.3086 | 0.06 | 1.06 | -0.75 | 0.25 | -0.69 | 0.31 | 68.36 | 36.13
2019-09-04 | 11:10 | 44.4102 | 0.1 | 1.1 | -0.75 | 0.25 | -0.69 | 0.31 | 70.31 | 36.13
2019-09-04 | 11:10 | 44.5078 | 0.08 | 1.08 | -0.75 | 0.25 | -0.69 | 0.31 | 70.31 | 36.13
2019-09-04 | 11:10 | 44.6211 | 0.08 | 1.08 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 34.18
2019-09-04 | 11:10 | 44.7188 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 69.34 | 35.16
2019-09-04 | 11:10 | 44.8281 | 0.06 | 1.06 | -0.76 | 0.24 | -0.7 | 0.3 | 69.34 | 36.13
2019-09-04 | 11:10 | 44.9297 | 0 | 1 | -0.68 | 0.32 | -0.68 | 0.32 | 68.36 | 35.16
2019-09-04 | 11:10 | 45.0273 | -0.08 | 0.92 | -0.61 | 0.39 | -0.68 | 0.32 | 69.34 | 37.11
2019-09-04 | 11:10 | 45.1289 | -0.1 | 0.9 | -0.6 | 0.4 | -0.67 | 0.33 | 70.31 | 34.18
2019-09-04 | 11:10 | 45.2383 | -0.09 | 0.91 | -0.57 | 0.43 | -0.67 | 0.33 | 69.34 | 35.16
2019-09-04 | 11:10 | 45.3398 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 68.36 | 34.18
2019-09-04 | 11:10 | 45.4375 | 0.06 | 1.06 | -0.75 | 0.25 | -0.68 | 0.32 | 69.34 | 35.16
2019-09-04 | 11:10 | 45.5391 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 68.36 | 34.18
2019-09-04 | 11:10 | 45.6406 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 67.38 | 34.18
2019-09-04 | 11:10 | 45.75 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 69.34 | 34.18
2019-09-04 | 11:10 | 45.8477 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 68.36 | 33.2
2019-09-04 | 11:10 | 45.9492 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 68.36 | 35.16
2019-09-04 | 11:10 | 46.0586 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 67.38 | 34.18
2019-09-04 | 11:10 | 46.1602 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 68.36 | 34.18
2019-09-04 | 11:10 | 46.2578 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 35.16
2019-09-04 | 11:10 | 46.3711 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 35.16
2019-09-04 | 11:10 | 46.4688 | -0.04 | 0.96 | -0.67 | 0.33 | -0.69 | 0.31 | 68.36 | 34.18
2019-09-04 | 11:10 | 46.5703 | -0.1 | 0.9 | -0.61 | 0.39 | -0.67 | 0.33 | 67.38 | 33.2
2019-09-04 | 11:10 | 46.668 | -0.11 | 0.89 | -0.59 | 0.41 | -0.66 | 0.34 | 67.38 | 33.2
2019-09-04 | 11:10 | 46.7773 | 0.04 | 1.04 | -0.71 | 0.29 | -0.67 | 0.33 | 68.36 | 33.2
2019-09-04 | 11:10 | 46.8789 | 0.06 | 1.06 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 35.16
2019-09-04 | 11:10 | 46.9805 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 67.38 | 34.18
2019-09-04 | 11:10 | 47.0781 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 68.36 | 33.2
2019-09-04 | 11:10 | 47.1875 | 0.07 | 1.07 | -0.76 | 0.24 | -0.71 | 0.29 | 68.36 | 34.18
2019-09-04 | 11:10 | 47.2891 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 67.38 | 34.18
2019-09-04 | 11:10 | 47.3906 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 47.5 | 0.09 | 1.09 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 33.2
2019-09-04 | 11:10 | 47.5977 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 47.6992 | 0.06 | 1.06 | -0.8 | 0.2 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 47.8008 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 32.23
2019-09-04 | 11:10 | 47.9102 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 68.36 | 34.18
2019-09-04 | 11:10 | 48.0078 | -0.08 | 0.92 | -0.66 | 0.34 | -0.68 | 0.32 | 68.36 | 33.2
2019-09-04 | 11:10 | 48.1094 | -0.1 | 0.9 | -0.61 | 0.39 | -0.67 | 0.33 | 70.31 | 33.2
2019-09-04 | 11:10 | 48.2188 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 67.38 | 33.2
2019-09-04 | 11:10 | 48.3203 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 67.38 | 33.2
2019-09-04 | 11:10 | 48.418 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 67.38 | 33.2
2019-09-04 | 11:10 | 48.5195 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 34.18
2019-09-04 | 11:10 | 48.6289 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 68.36 | 34.18
2019-09-04 | 11:10 | 48.7305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 35.16
2019-09-04 | 11:10 | 48.8281 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 48.9297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 49.0391 | 0.06 | 1.06 | -0.79 | 0.21 | -0.72 | 0.28 | 69.34 | 33.2
2019-09-04 | 11:10 | 49.1406 | 0.06 | 1.06 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 33.2
2019-09-04 | 11:10 | 49.2383 | 0.07 | 1.07 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 33.2
2019-09-04 | 11:10 | 49.3398 | 0.06 | 1.06 | -0.8 | 0.2 | -0.73 | 0.27 | 67.38 | 33.2
2019-09-04 | 11:10 | 49.4492 | -0.02 | 0.98 | -0.71 | 0.29 | -0.7 | 0.3 | 67.38 | 33.2
2019-09-04 | 11:10 | 49.5508 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 67.38 | 33.2
2019-09-04 | 11:10 | 49.6602 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 69.34 | 33.2
2019-09-04 | 11:10 | 49.7578 | -0.12 | 0.88 | -0.61 | 0.39 | -0.67 | 0.33 | 69.34 | 34.18
2019-09-04 | 11:10 | 49.8594 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 68.36 | 32.23
2019-09-04 | 11:10 | 49.9609 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 33.2
2019-09-04 | 11:10 | 50.0586 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 67.38 | 32.23
2019-09-04 | 11:10 | 50.168 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 34.18
2019-09-04 | 11:10 | 50.2695 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 50.3711 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 33.2
2019-09-04 | 11:10 | 50.4688 | 0.08 | 1.08 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 33.2
2019-09-04 | 11:10 | 50.5781 | 0.06 | 1.06 | -0.81 | 0.19 | -0.72 | 0.28 | 67.38 | 32.23
2019-09-04 | 11:10 | 50.6797 | 0.06 | 1.06 | -0.8 | 0.2 | -0.72 | 0.28 | 69.34 | 33.2
2019-09-04 | 11:10 | 50.7773 | 0.09 | 1.09 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 50.8906 | 0.09 | 1.09 | -0.8 | 0.2 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 50.9883 | -0.06 | 0.94 | -0.71 | 0.29 | -0.69 | 0.31 | 67.38 | 32.23
2019-09-04 | 11:10 | 51.0898 | -0.12 | 0.88 | -0.63 | 0.37 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 11:10 | 51.1875 | -0.09 | 0.91 | -0.65 | 0.35 | -0.67 | 0.33 | 68.36 | 33.2
2019-09-04 | 11:10 | 51.3008 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 67.38 | 32.23
2019-09-04 | 11:10 | 51.3984 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 67.38 | 32.23
2019-09-04 | 11:10 | 51.5 | 0.05 | 1.05 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 32.23
2019-09-04 | 11:10 | 51.5977 | 0.06 | 1.06 | -0.8 | 0.2 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 51.7109 | 0.05 | 1.05 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 33.2
2019-09-04 | 11:10 | 51.8086 | 0.09 | 1.09 | -0.8 | 0.2 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 51.9102 | 0.06 | 1.06 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 52.0078 | 0.07 | 1.07 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 33.2
2019-09-04 | 11:10 | 52.1211 | 0.06 | 1.06 | -0.82 | 0.18 | -0.72 | 0.28 | 67.38 | 32.23
2019-09-04 | 11:10 | 52.2188 | 0.06 | 1.06 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 52.3281 | 0.07 | 1.07 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 52.4297 | 0.02 | 1.02 | -0.76 | 0.24 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 52.5273 | -0.04 | 0.96 | -0.69 | 0.31 | -0.68 | 0.32 | 69.34 | 33.2
2019-09-04 | 11:10 | 52.6289 | -0.1 | 0.9 | -0.64 | 0.36 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:10 | 52.7383 | -0.12 | 0.88 | -0.63 | 0.37 | -0.68 | 0.32 | 68.36 | 33.2
2019-09-04 | 11:10 | 52.8398 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 67.38 | 33.2
2019-09-04 | 11:10 | 52.9375 | 0.07 | 1.07 | -0.8 | 0.2 | -0.69 | 0.31 | 68.36 | 35.16
2019-09-04 | 11:10 | 53.0391 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 67.38 | 33.2
2019-09-04 | 11:10 | 53.1406 | 0.06 | 1.06 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 34.18
2019-09-04 | 11:10 | 53.25 | 0.08 | 1.08 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 34.18
2019-09-04 | 11:10 | 53.3477 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 53.4609 | 0.07 | 1.07 | -0.81 | 0.19 | -0.7 | 0.3 | 68.36 | 32.23
2019-09-04 | 11:10 | 53.5586 | 0.05 | 1.05 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 33.2
2019-09-04 | 11:10 | 53.6602 | 0.09 | 1.09 | -0.83 | 0.17 | -0.72 | 0.28 | 69.34 | 33.2
2019-09-04 | 11:10 | 53.7578 | 0.07 | 1.07 | -0.82 | 0.18 | -0.7 | 0.3 | 66.41 | 34.18
2019-09-04 | 11:10 | 53.8711 | 0.06 | 1.06 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 53.9688 | -0.03 | 0.97 | -0.73 | 0.27 | -0.7 | 0.3 | 68.36 | 33.2
2019-09-04 | 11:10 | 54.0703 | -0.1 | 0.9 | -0.68 | 0.32 | -0.69 | 0.31 | 68.36 | 33.2
2019-09-04 | 11:10 | 54.1797 | -0.12 | 0.88 | -0.65 | 0.35 | -0.69 | 0.31 | 68.36 | 34.18
2019-09-04 | 11:10 | 54.2773 | 0.04 | 1.04 | -0.75 | 0.25 | -0.67 | 0.33 | 67.38 | 34.18
2019-09-04 | 11:10 | 54.3789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 66.41 | 32.23
2019-09-04 | 11:10 | 54.4805 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 68.36 | 32.23
2019-09-04 | 11:10 | 54.5898 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 67.38 | 33.2
2019-09-04 | 11:10 | 54.6875 | 0.07 | 1.07 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 34.18
2019-09-04 | 11:10 | 54.7891 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 67.38 | 32.23
2019-09-04 | 11:10 | 54.8906 | 0.07 | 1.07 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 33.2
2019-09-04 | 11:10 | 55 | 0.06 | 1.06 | -0.81 | 0.19 | -0.7 | 0.3 | 66.41 | 33.2
2019-09-04 | 11:10 | 55.0977 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 67.38 | 32.23
2019-09-04 | 11:10 | 55.1992 | 0.07 | 1.07 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 55.3008 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 34.18
2019-09-04 | 11:10 | 55.4102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 33.2
2019-09-04 | 11:10 | 55.5078 | -0.06 | 0.94 | -0.7 | 0.3 | -0.69 | 0.31 | 69.34 | 33.2
2019-09-04 | 11:10 | 55.6094 | -0.1 | 0.9 | -0.67 | 0.33 | -0.67 | 0.33 | 68.36 | 33.2
2019-09-04 | 11:10 | 55.7188 | -0.1 | 0.9 | -0.65 | 0.35 | -0.66 | 0.34 | 68.36 | 35.16
2019-09-04 | 11:10 | 55.8203 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 68.36 | 33.2
2019-09-04 | 11:10 | 55.918 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 67.38 | 33.2
2019-09-04 | 11:10 | 56.0195 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 68.36 | 35.16
2019-09-04 | 11:10 | 56.1289 | 0.07 | 1.07 | -0.81 | 0.19 | -0.7 | 0.3 | 68.36 | 33.2
2019-09-04 | 11:10 | 56.2305 | 0.08 | 1.08 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 56.3281 | 0.07 | 1.07 | -0.81 | 0.19 | -0.7 | 0.3 | 67.38 | 32.23
2019-09-04 | 11:10 | 56.4297 | 0.06 | 1.06 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 32.23
2019-09-04 | 11:10 | 56.5391 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 68.36 | 33.2
2019-09-04 | 11:10 | 56.6406 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 68.36 | 32.23
2019-09-04 | 11:10 | 56.7383 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 67.38 | 33.2
2019-09-04 | 11:10 | 56.8398 | 0.07 | 1.07 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 56.9492 | -0.03 | 0.97 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 33.2
2019-09-04 | 11:10 | 57.0508 | -0.08 | 0.92 | -0.68 | 0.32 | -0.68 | 0.32 | 69.34 | 33.2
2019-09-04 | 11:10 | 57.1484 | -0.11 | 0.89 | -0.67 | 0.33 | -0.68 | 0.32 | 68.36 | 33.2
2019-09-04 | 11:10 | 57.2578 | -0.12 | 0.88 | -0.65 | 0.35 | -0.67 | 0.33 | 69.34 | 33.2
2019-09-04 | 11:10 | 57.3594 | 0.06 | 1.06 | -0.8 | 0.2 | -0.67 | 0.33 | 68.36 | 32.23
2019-09-04 | 11:10 | 57.4609 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 68.36 | 31.25
2019-09-04 | 11:10 | 57.5586 | 0.08 | 1.08 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 33.2
2019-09-04 | 11:10 | 57.668 | 0.07 | 1.07 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:10 | 57.7695 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 32.23
2019-09-04 | 11:10 | 57.8711 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 34.18
2019-09-04 | 11:10 | 57.9688 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 68.36 | 32.23
2019-09-04 | 11:10 | 58.0781 | 0.07 | 1.07 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 33.2
2019-09-04 | 11:10 | 58.1797 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 32.23
2019-09-04 | 11:10 | 58.2891 | 0.08 | 1.08 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 58.3906 | 0.07 | 1.07 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 34.18
2019-09-04 | 11:10 | 58.4883 | -0.05 | 0.95 | -0.72 | 0.28 | -0.69 | 0.31 | 68.36 | 32.23
2019-09-04 | 11:10 | 58.5898 | -0.11 | 0.89 | -0.68 | 0.32 | -0.68 | 0.32 | 68.36 | 32.23
2019-09-04 | 11:10 | 58.6875 | -0.11 | 0.89 | -0.65 | 0.35 | -0.69 | 0.31 | 68.36 | 32.23
2019-09-04 | 11:10 | 58.8008 | 0.02 | 1.02 | -0.77 | 0.23 | -0.68 | 0.32 | 69.34 | 33.2
2019-09-04 | 11:10 | 58.8984 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 68.36 | 31.25
2019-09-04 | 11:10 | 59 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 34.18
2019-09-04 | 11:10 | 59.0977 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 11:10 | 59.2109 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 33.2
2019-09-04 | 11:10 | 59.3086 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 33.2
2019-09-04 | 11:10 | 59.418 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 59.5195 | 0.09 | 1.09 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 33.2
2019-09-04 | 11:10 | 59.6211 | 0.07 | 1.07 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 33.2
2019-09-04 | 11:10 | 59.7188 | 0.07 | 1.07 | -0.85 | 0.15 | -0.71 | 0.29 | 68.36 | 32.23
2019-09-04 | 11:10 | 59.8281 | 0.07 | 1.07 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 59.9297 | 0 | 1 | -0.77 | 0.23 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:10 | 60.0273 | -0.08 | 0.92 | -0.7 | 0.3 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 11:10 | 60.1289 | -0.11 | 0.89 | -0.67 | 0.33 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 11:10 | 60.2383 | -0.12 | 0.88 | -0.64 | 0.36 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 11:10 | 60.3398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 32.23
2019-09-04 | 11:10 | 60.4375 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 33.2
2019-09-04 | 11:10 | 60.5508 | 0.06 | 1.06 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 60.6484 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:10 | 60.75 | 0.06 | 1.06 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 32.23
2019-09-04 | 11:10 | 60.8477 | 0.07 | 1.07 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:10 | 60.9609 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 11:10 | 61.0586 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:10 | 61.1602 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:10 | 61.2578 | 0.09 | 1.09 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:10 | 61.3711 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:10 | 61.4688 | -0.05 | 0.95 | -0.75 | 0.25 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 61.5703 | -0.09 | 0.91 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 32.23
2019-09-04 | 11:10 | 61.6797 | -0.11 | 0.89 | -0.67 | 0.33 | -0.67 | 0.33 | 69.34 | 32.23
2019-09-04 | 11:10 | 61.7773 | -0.02 | 0.98 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 61.8789 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 68.36 | 31.25
2019-09-04 | 11:10 | 61.9805 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:10 | 62.0898 | 0.06 | 1.06 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:10 | 62.1875 | 0.07 | 1.07 | -0.82 | 0.18 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:10 | 62.2891 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 11:10 | 62.3906 | 0.07 | 1.07 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 32.23
2019-09-04 | 11:10 | 62.5 | 0.07 | 1.07 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 62.5977 | 0.08 | 1.08 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 32.23
2019-09-04 | 11:10 | 62.6992 | 0.08 | 1.08 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:10 | 62.8086 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:10 | 62.9102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:10 | 63.0078 | -0.08 | 0.92 | -0.72 | 0.28 | -0.71 | 0.29 | 69.34 | 33.2
2019-09-04 | 11:10 | 63.1094 | -0.1 | 0.9 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 32.23
2019-09-04 | 11:10 | 63.2188 | -0.11 | 0.89 | -0.67 | 0.33 | -0.68 | 0.32 | 68.36 | 32.23
2019-09-04 | 11:10 | 63.3203 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 11:10 | 63.418 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 63.5195 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:10 | 63.6289 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 32.23
2019-09-04 | 11:10 | 63.7305 | 0.08 | 1.08 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:10 | 63.8281 | 0.07 | 1.07 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:10 | 63.9297 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 11:10 | 64.0391 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:10 | 64.1406 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 32.23
2019-09-04 | 11:10 | 64.25 | 0.08 | 1.08 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 34.18
2019-09-04 | 11:10 | 64.3477 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:10 | 64.4492 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 64.5508 | -0.09 | 0.91 | -0.7 | 0.3 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 64.6484 | -0.09 | 0.91 | -0.7 | 0.3 | -0.69 | 0.31 | 68.36 | 32.23
2019-09-04 | 11:10 | 64.7578 | -0.12 | 0.88 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 32.23
2019-09-04 | 11:10 | 64.8594 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:10 | 64.9609 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:10 | 65.0586 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 68.36 | 31.25
2019-09-04 | 11:10 | 65.168 | 0.05 | 1.05 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 65.2695 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:10 | 65.3789 | 0.07 | 1.07 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 65.4805 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 65.5781 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:10 | 65.6797 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:10 | 65.7891 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:10 | 65.8906 | 0.09 | 1.09 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 65.9883 | -0.04 | 0.96 | -0.75 | 0.25 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 66.0898 | -0.09 | 0.91 | -0.69 | 0.31 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 66.1992 | -0.11 | 0.89 | -0.68 | 0.32 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:10 | 66.3008 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:10 | 66.3984 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 68.36 | 32.23
2019-09-04 | 11:10 | 66.5078 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:10 | 66.6094 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 11:10 | 66.7109 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 34.18
2019-09-04 | 11:10 | 66.8203 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:10 | 66.918 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:10 | 67.0195 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:10 | 67.1289 | 0.07 | 1.07 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 67.2305 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 67.3281 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 11:10 | 67.4297 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 67.5273 | -0.05 | 0.95 | -0.72 | 0.28 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 67.6406 | -0.12 | 0.88 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:10 | 67.7383 | -0.13 | 0.87 | -0.64 | 0.36 | -0.68 | 0.32 | 70.31 | 32.23
2019-09-04 | 11:10 | 67.8398 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:10 | 67.9375 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:10 | 68.0508 | 0.05 | 1.05 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:10 | 68.1484 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:10 | 68.25 | 0.08 | 1.08 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:10 | 68.3477 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 68.4609 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:10 | 68.5586 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:10 | 68.6602 | 0.08 | 1.08 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:10 | 68.7578 | 0.07 | 1.07 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:10 | 68.8711 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:10 | 68.9688 | -0.03 | 0.97 | -0.77 | 0.23 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:10 | 69.0703 | -0.08 | 0.92 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:10 | 69.1797 | -0.1 | 0.9 | -0.68 | 0.32 | -0.67 | 0.33 | 69.34 | 33.2
2019-09-04 | 11:10 | 69.2773 | -0.03 | 0.97 | -0.7 | 0.3 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:10 | 69.3789 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:10 | 69.4805 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 32.23
2019-09-04 | 11:11 | 69.5898 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 32.23
2019-09-04 | 11:11 | 69.6875 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:11 | 69.7891 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:11 | 69.8906 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 70 | 0.06 | 1.06 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 70.0977 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:11 | 70.2109 | 0.06 | 1.06 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:11 | 70.3086 | 0.09 | 1.09 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 70.4102 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:11 | 70.5078 | -0.05 | 0.95 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:11 | 70.6094 | -0.08 | 0.92 | -0.71 | 0.29 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:11 | 70.7188 | -0.11 | 0.89 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:11 | 70.8203 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:11 | 70.918 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 71.0195 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 71.1289 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 71.2305 | 0.07 | 1.07 | -0.82 | 0.18 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:11 | 71.3398 | 0.09 | 1.09 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:11 | 71.4375 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:11 | 71.5391 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 32.23
2019-09-04 | 11:11 | 71.6406 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 11:11 | 71.75 | 0.07 | 1.07 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:11 | 71.8477 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:11 | 71.9492 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:11 | 72.0508 | -0.07 | 0.93 | -0.71 | 0.29 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:11 | 72.1484 | -0.11 | 0.89 | -0.68 | 0.32 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 11:11 | 72.2578 | -0.12 | 0.88 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:11 | 72.3594 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 11:11 | 72.4609 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:11 | 72.5703 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 72.668 | 0.06 | 1.06 | -0.82 | 0.18 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 11:11 | 72.7695 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 11:11 | 72.8789 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 72.9805 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 73.0781 | 0.06 | 1.06 | -0.83 | 0.17 | -0.72 | 0.28 | 69.34 | 31.25
2019-09-04 | 11:11 | 73.1797 | 0.07 | 1.07 | -0.85 | 0.15 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 11:11 | 73.2891 | 0.08 | 1.08 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 33.2
2019-09-04 | 11:11 | 73.3906 | 0.05 | 1.05 | -0.85 | 0.15 | -0.73 | 0.27 | 70.31 | 32.23
2019-09-04 | 11:11 | 73.4883 | -0.03 | 0.97 | -0.75 | 0.25 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:11 | 73.5977 | -0.09 | 0.91 | -0.69 | 0.31 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:11 | 73.6992 | -0.13 | 0.87 | -0.67 | 0.33 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:11 | 73.8008 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 73.8984 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 74.0078 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 74.1094 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 74.2109 | 0.07 | 1.07 | -0.82 | 0.18 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 74.3086 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 74.418 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 74.5195 | 0.07 | 1.07 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:11 | 74.6211 | 0.09 | 1.09 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 74.7188 | 0.07 | 1.07 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 74.8281 | 0.08 | 1.08 | -0.84 | 0.16 | -0.72 | 0.28 | 71.29 | 31.25
2019-09-04 | 11:11 | 74.9297 | 0.05 | 1.05 | -0.83 | 0.17 | -0.72 | 0.28 | 69.34 | 30.27
2019-09-04 | 11:11 | 75.0273 | -0.04 | 0.96 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 75.1406 | -0.09 | 0.91 | -0.69 | 0.31 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 75.2383 | -0.1 | 0.9 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 75.3398 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 75.4492 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 75.5508 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:11 | 75.6484 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 75.75 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 75.8477 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 75.9609 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 76.0586 | 0.07 | 1.07 | -0.83 | 0.17 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 11:11 | 76.1602 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:11 | 76.2695 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 76.3711 | 0.07 | 1.07 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 76.4805 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 76.5703 | -0.07 | 0.93 | -0.72 | 0.28 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 76.6797 | -0.1 | 0.9 | -0.67 | 0.33 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 76.7773 | -0.12 | 0.88 | -0.66 | 0.34 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 76.8789 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:11 | 76.9805 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 77.0898 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 77.1875 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 77.2891 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 77.3984 | 0.06 | 1.06 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 77.5 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 77.5977 | 0.08 | 1.08 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 77.7109 | 0.1 | 1.1 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:11 | 77.8086 | 0.07 | 1.07 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 77.9102 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:11 | 78.0078 | -0.05 | 0.95 | -0.74 | 0.26 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 78.1211 | -0.11 | 0.89 | -0.67 | 0.33 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 78.2188 | -0.12 | 0.88 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 78.3203 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 78.418 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 78.5273 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 78.6289 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 78.7305 | 0.06 | 1.06 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 78.8398 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 78.9375 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 79.0391 | 0.08 | 1.08 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 79.1484 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 79.25 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 11:11 | 79.3477 | 0.07 | 1.07 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:11 | 79.4492 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 79.5586 | -0.08 | 0.92 | -0.68 | 0.32 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 79.6602 | -0.12 | 0.88 | -0.67 | 0.33 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 79.7578 | -0.12 | 0.88 | -0.65 | 0.35 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:11 | 79.8594 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 79.9688 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 80.0703 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 80.168 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 11:11 | 80.2695 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 80.3789 | 0.06 | 1.06 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 80.4805 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 80.5781 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 80.6797 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 80.7891 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 11:11 | 80.8906 | 0.05 | 1.05 | -0.84 | 0.16 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 11:11 | 80.9883 | -0.02 | 0.98 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 81.0977 | -0.1 | 0.9 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 81.1992 | -0.11 | 0.89 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 81.3008 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 68.36 | 29.3
2019-09-04 | 11:11 | 81.3984 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 81.5078 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 81.6094 | 0.07 | 1.07 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 81.7109 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 81.8086 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 81.918 | 0.07 | 1.07 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 82.0195 | 0.07 | 1.07 | -0.84 | 0.16 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 11:11 | 82.1211 | 0.05 | 1.05 | -0.84 | 0.16 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 11:11 | 82.2305 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 82.3281 | 0.08 | 1.08 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 82.4297 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:11 | 82.5273 | -0.06 | 0.94 | -0.72 | 0.28 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 82.6406 | -0.1 | 0.9 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 82.7383 | -0.11 | 0.89 | -0.65 | 0.35 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 11:11 | 82.8398 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 82.9375 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 83.0508 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 83.1484 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 83.25 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 83.3477 | 0.07 | 1.07 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 83.4609 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 83.5586 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 11:11 | 83.668 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:11 | 83.7695 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 11:11 | 83.8711 | 0.06 | 1.06 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:11 | 83.9688 | 0 | 1 | -0.77 | 0.23 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:11 | 84.0703 | -0.06 | 0.94 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 84.1797 | -0.1 | 0.9 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:11 | 84.2773 | -0.14 | 0.86 | -0.65 | 0.35 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 84.3789 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 84.4805 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 84.5898 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 84.6875 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 11:11 | 84.8008 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 84.8984 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 11:11 | 85 | 0.07 | 1.07 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 85.0977 | 0.06 | 1.06 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 85.2109 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 85.3086 | 0.07 | 1.07 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 85.4102 | 0.06 | 1.06 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 85.5195 | -0.05 | 0.95 | -0.73 | 0.27 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 85.6211 | -0.11 | 0.89 | -0.68 | 0.32 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 85.7188 | -0.12 | 0.88 | -0.65 | 0.35 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 85.8203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 68.36 | 29.3
2019-09-04 | 11:11 | 85.9297 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 86.0273 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 86.1289 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 86.2305 | 0.05 | 1.05 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 86.3398 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 86.4375 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 86.5391 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 11:11 | 86.6484 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 86.75 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 86.8477 | 0.09 | 1.09 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:11 | 86.9492 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 87.0586 | -0.09 | 0.91 | -0.71 | 0.29 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 87.1602 | -0.1 | 0.9 | -0.68 | 0.32 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:11 | 87.2578 | -0.12 | 0.88 | -0.65 | 0.35 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 87.3594 | 0.03 | 1.03 | -0.8 | 0.2 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 87.4688 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 87.5703 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 87.668 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 87.7695 | 0.05 | 1.05 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 87.8789 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 87.9805 | 0.05 | 1.05 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 88.0781 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 88.1797 | 0.08 | 1.08 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:11 | 88.2891 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 88.3906 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 88.4883 | -0.02 | 0.98 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 88.5977 | -0.09 | 0.91 | -0.7 | 0.3 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 88.6992 | -0.12 | 0.88 | -0.67 | 0.33 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 88.8086 | 0 | 1 | -0.74 | 0.26 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 88.8984 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 89.0078 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 89.1094 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 89.2109 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 89.3086 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 89.418 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 89.5195 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 89.6289 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 89.7305 | 0.07 | 1.07 | -0.83 | 0.17 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 11:11 | 89.8281 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 89.9297 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 90.0391 | -0.06 | 0.94 | -0.74 | 0.26 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:11 | 90.1406 | -0.1 | 0.9 | -0.68 | 0.32 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 90.2383 | -0.12 | 0.88 | -0.66 | 0.34 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 90.3398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 90.4492 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 90.5508 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 90.6484 | 0.06 | 1.06 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 90.7578 | 0.05 | 1.05 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 11:11 | 90.8594 | 0.07 | 1.07 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 90.9609 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 91.0586 | 0.05 | 1.05 | -0.84 | 0.16 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 91.168 | 0.06 | 1.06 | -0.84 | 0.16 | -0.72 | 0.28 | 70.31 | 30.27
2019-09-04 | 11:11 | 91.2695 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 91.3711 | 0.07 | 1.07 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 91.4688 | -0.01 | 0.99 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 91.5781 | -0.08 | 0.92 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 91.6797 | -0.11 | 0.89 | -0.65 | 0.35 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 91.7773 | -0.13 | 0.87 | -0.65 | 0.35 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 91.8906 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 91.9883 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 92.0898 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 92.1875 | 0.05 | 1.05 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 92.3008 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 92.3984 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 92.5 | 0.07 | 1.07 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 92.5977 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 92.7109 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 11:11 | 92.8086 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 92.9102 | 0.06 | 1.06 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:11 | 93.0195 | -0.06 | 0.94 | -0.74 | 0.26 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 93.1211 | -0.13 | 0.87 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 93.2188 | -0.11 | 0.89 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 32.23
2019-09-04 | 11:11 | 93.3203 | 0.01 | 1.01 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:11 | 93.4297 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:11 | 93.5273 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 93.6289 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 93.7305 | 0.05 | 1.05 | -0.81 | 0.19 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 11:11 | 93.8398 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 93.9375 | 0.08 | 1.08 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 94.0391 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 94.1406 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 94.25 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 94.3477 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 94.4609 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 94.5586 | -0.08 | 0.92 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 94.6602 | -0.11 | 0.89 | -0.67 | 0.33 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 94.7578 | -0.13 | 0.87 | -0.65 | 0.35 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 94.8594 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 94.9688 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 95.0703 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 95.168 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 95.2695 | 0.06 | 1.06 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 95.3789 | 0.06 | 1.06 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 95.4805 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:11 | 95.5781 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 95.6875 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 95.7891 | 0.05 | 1.05 | -0.83 | 0.17 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 11:11 | 95.8906 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 95.9883 | -0.05 | 0.95 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:11 | 96.0977 | -0.12 | 0.88 | -0.68 | 0.32 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 96.1992 | -0.14 | 0.86 | -0.66 | 0.34 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 96.3008 | -0.05 | 0.95 | -0.71 | 0.29 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 96.3984 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:11 | 96.5078 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 96.6094 | 0.06 | 1.06 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 96.7188 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 96.8203 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 96.918 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 97.0195 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 97.1289 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 97.2305 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 97.3281 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 97.4297 | 0.05 | 1.05 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 97.5391 | -0.07 | 0.93 | -0.71 | 0.29 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 97.6406 | -0.11 | 0.89 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 97.7383 | -0.13 | 0.87 | -0.66 | 0.34 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 97.8398 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 97.9492 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:11 | 98.0508 | 0.03 | 1.03 | -0.81 | 0.19 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 98.1484 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 98.2578 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 98.3594 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 98.4609 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 98.5586 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 98.668 | 0.06 | 1.06 | -0.82 | 0.18 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 11:11 | 98.7695 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:11 | 98.8711 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 98.9805 | -0.02 | 0.98 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:11 | 99.0781 | -0.13 | 0.87 | -0.69 | 0.31 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 11:11 | 99.1797 | -0.13 | 0.87 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 99.2773 | -0.15 | 0.85 | -0.65 | 0.35 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 99.3906 | 0.01 | 1.01 | -0.79 | 0.21 | -0.65 | 0.35 | 69.34 | 30.27
2019-09-04 | 11:11 | 99.4883 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 99.5898 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 68.36 | 29.3
2019-09-04 | 11:11 | 99.6875 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 99.8008 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 99.8984 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 100 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 100.0977 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 100.2109 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 100.3086 | 0.05 | 1.05 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 100.4102 | 0.03 | 1.03 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 100.5195 | -0.07 | 0.93 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 11:11 | 100.6211 | -0.13 | 0.87 | -0.66 | 0.34 | -0.67 | 0.33 | 70.31 | 31.25
2019-09-04 | 11:11 | 100.7188 | -0.11 | 0.89 | -0.67 | 0.33 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 100.8203 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 100.9297 | 0.03 | 1.03 | -0.8 | 0.2 | -0.67 | 0.33 | 69.34 | 31.25
2019-09-04 | 11:11 | 101.0273 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 101.1289 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 101.2305 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 101.3398 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 101.4375 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 101.5391 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 101.6484 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 101.75 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 101.8477 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 101.9609 | -0.02 | 0.98 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 102.0586 | -0.12 | 0.88 | -0.69 | 0.31 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 102.1602 | -0.12 | 0.88 | -0.66 | 0.34 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:11 | 102.2578 | -0.14 | 0.86 | -0.64 | 0.36 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 102.3594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 102.4688 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 102.5703 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 102.668 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 102.7773 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 102.8789 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 102.9805 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 103.0781 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 103.1875 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 103.2891 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 103.3906 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 103.5 | -0.03 | 0.97 | -0.76 | 0.24 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 103.5977 | -0.12 | 0.88 | -0.67 | 0.33 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 103.6992 | -0.13 | 0.87 | -0.65 | 0.35 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 103.8086 | -0.09 | 0.91 | -0.67 | 0.33 | -0.66 | 0.34 | 70.31 | 30.27
2019-09-04 | 11:11 | 103.8984 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 11:11 | 104.0078 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 104.1094 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 104.2188 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 104.3203 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 104.418 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 104.5195 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 104.6289 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 104.7305 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:11 | 104.8281 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 104.9297 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 70.31 | 32.23
2019-09-04 | 11:11 | 105.0391 | -0.05 | 0.95 | -0.73 | 0.27 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 105.1406 | -0.14 | 0.86 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 11:11 | 105.2383 | -0.16 | 0.84 | -0.64 | 0.36 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 105.3477 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 105.4492 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 105.5508 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 105.6484 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 105.7578 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 105.8594 | 0.02 | 1.02 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 105.9609 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 106.0586 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 106.168 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:11 | 106.2695 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 106.3711 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 11:11 | 106.4805 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 106.5781 | -0.08 | 0.92 | -0.72 | 0.28 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 106.6797 | -0.15 | 0.85 | -0.67 | 0.33 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 106.7773 | -0.13 | 0.87 | -0.65 | 0.35 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:11 | 106.8906 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 106.9883 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 107.0898 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 107.1875 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 107.3008 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 107.3984 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 107.5 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 107.6094 | 0.03 | 1.03 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 107.7109 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 107.8086 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 107.918 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 108.0195 | -0.06 | 0.94 | -0.76 | 0.24 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 108.1211 | -0.16 | 0.84 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 108.2188 | -0.16 | 0.84 | -0.65 | 0.35 | -0.67 | 0.33 | 69.34 | 30.27
2019-09-04 | 11:11 | 108.3203 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 11:11 | 108.4297 | 0.01 | 1.01 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:11 | 108.5273 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 108.6289 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 108.7383 | 0.02 | 1.02 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 108.8398 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 108.9375 | 0.02 | 1.02 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 11:11 | 109.0508 | 0.02 | 1.02 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 109.1484 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:11 | 109.25 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 109.3477 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 11:11 | 109.4609 | -0.01 | 0.99 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 109.5586 | -0.1 | 0.9 | -0.7 | 0.3 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 109.6602 | -0.13 | 0.87 | -0.66 | 0.34 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 109.7695 | -0.15 | 0.85 | -0.64 | 0.36 | -0.66 | 0.34 | 70.31 | 30.27
2019-09-04 | 11:11 | 109.8711 | 0 | 1 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 11:11 | 109.9688 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 110.0703 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 110.1797 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 110.2773 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:11 | 110.3789 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 110.4805 | 0.03 | 1.03 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 110.5898 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 110.6875 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 110.7891 | 0.02 | 1.02 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 32.23
2019-09-04 | 11:11 | 110.8906 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 11:11 | 111 | -0.05 | 0.95 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 111.0977 | -0.12 | 0.88 | -0.68 | 0.32 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:11 | 111.1992 | -0.15 | 0.85 | -0.65 | 0.35 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:11 | 111.3086 | -0.15 | 0.85 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:11 | 111.4102 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:11 | 111.5078 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 111.6094 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 11:11 | 111.7188 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 111.8203 | 0.02 | 1.02 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 111.918 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 112.0195 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:11 | 112.1289 | 0.02 | 1.02 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 112.2305 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 112.3281 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:11 | 112.4375 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:11 | 112.5391 | -0.06 | 0.94 | -0.72 | 0.28 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 11:11 | 112.6406 | -0.14 | 0.86 | -0.66 | 0.34 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 112.7383 | -0.11 | 0.89 | -0.65 | 0.35 | -0.66 | 0.34 | 69.34 | 29.3
2019-09-04 | 11:11 | 112.8477 | 0 | 1 | -0.77 | 0.23 | -0.67 | 0.33 | 70.31 | 31.25
2019-09-04 | 11:11 | 112.9492 | 0.02 | 1.02 | -0.8 | 0.2 | -0.67 | 0.33 | 69.34 | 30.27
2019-09-04 | 11:11 | 113.0508 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 113.1484 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 113.2578 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 113.3594 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 113.4609 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 113.5586 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 113.668 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 113.7695 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 113.8711 | 0.06 | 1.06 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 113.9805 | -0.01 | 0.99 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 114.0781 | -0.12 | 0.88 | -0.69 | 0.31 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 114.1797 | -0.13 | 0.87 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:11 | 114.2773 | -0.15 | 0.85 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:11 | 114.3906 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 114.4883 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 114.5898 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 114.6875 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 114.8008 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 114.8984 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 115.0078 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:11 | 115.1094 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 115.2109 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 115.3086 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 115.4102 | 0.03 | 1.03 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 115.5195 | -0.06 | 0.94 | -0.75 | 0.25 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 115.6211 | -0.12 | 0.88 | -0.68 | 0.32 | -0.68 | 0.32 | 68.36 | 29.3
2019-09-04 | 11:11 | 115.7305 | -0.11 | 0.89 | -0.65 | 0.35 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 115.8281 | -0.04 | 0.96 | -0.74 | 0.26 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 115.9297 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:11 | 116.0273 | 0.01 | 1.01 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:11 | 116.1406 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 116.2383 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 116.3398 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 116.4492 | 0.02 | 1.02 | -0.81 | 0.19 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 116.5508 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 116.6484 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 116.75 | 0.03 | 1.03 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 116.8477 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 11:11 | 116.9609 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 117.0586 | -0.06 | 0.94 | -0.73 | 0.27 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 117.1602 | -0.13 | 0.87 | -0.67 | 0.33 | -0.67 | 0.33 | 69.34 | 30.27
2019-09-04 | 11:11 | 117.2695 | -0.15 | 0.85 | -0.65 | 0.35 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:11 | 117.3711 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 117.4688 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:11 | 117.5703 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 117.6797 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 117.7773 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 117.8789 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 117.9805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 118.0898 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:11 | 118.1875 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 118.2891 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 118.3984 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 31.25
2019-09-04 | 11:11 | 118.5 | -0.03 | 0.97 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 118.5977 | -0.11 | 0.89 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 118.6992 | -0.15 | 0.85 | -0.65 | 0.35 | -0.67 | 0.33 | 71.29 | 31.25
2019-09-04 | 11:11 | 118.8086 | -0.18 | 0.82 | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 118.9102 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 119.0078 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:11 | 119.1094 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 119.2188 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 11:11 | 119.3203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 119.418 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:11 | 119.5195 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:11 | 119.6289 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 119.7305 | 0.03 | 1.03 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 119.8281 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 119.9375 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:11 | 120.0391 | -0.06 | 0.94 | -0.73 | 0.27 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 120.1484 | -0.13 | 0.87 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 120.2383 | -0.15 | 0.85 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 11:11 | 120.3477 | -0.03 | 0.97 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 120.4492 | 0.01 | 1.01 | -0.86 | 0.14 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 120.5508 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 120.6484 | 0.01 | 1.01 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 120.7578 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:11 | 120.8594 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 120.9688 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 121.0703 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 121.168 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:11 | 121.2695 | 0.03 | 1.03 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 121.3711 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 121.4805 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 121.5781 | -0.12 | 0.88 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 121.6875 | -0.12 | 0.88 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:11 | 121.7891 | -0.14 | 0.86 | -0.66 | 0.34 | -0.66 | 0.34 | 70.31 | 30.27
2019-09-04 | 11:11 | 121.8906 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 121.9883 | 0.02 | 1.02 | -0.8 | 0.2 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:11 | 122.0977 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:11 | 122.1992 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 122.3008 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 122.3984 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 122.5 | 0.01 | 1.01 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:11 | 122.6094 | 0.03 | 1.03 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 122.7109 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:11 | 122.8086 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:11 | 122.9102 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:11 | 123.0195 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 123.1211 | -0.11 | 0.89 | -0.69 | 0.31 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:11 | 123.2305 | -0.12 | 0.88 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 123.3281 | -0.06 | 0.94 | -0.74 | 0.26 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:11 | 123.4297 | 0.03 | 1.03 | -0.81 | 0.19 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 123.5273 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 123.6406 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:11 | 123.7383 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 123.8398 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 123.9375 | 0.02 | 1.02 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 124.0508 | 0.03 | 1.03 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 124.1484 | 0.05 | 1.05 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:11 | 124.25 | 0.03 | 1.03 | -0.83 | 0.17 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:11 | 124.3477 | 0.02 | 1.02 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:11 | 124.4609 | 0.02 | 1.02 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:11 | 124.5586 | -0.08 | 0.92 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:11 | 124.6602 | -0.15 | 0.85 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 124.7695 | -0.16 | 0.84 | -0.64 | 0.36 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:11 | 124.8711 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:11 | 124.9688 | 0.02 | 1.02 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 125.0703 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 125.1797 | 0.02 | 1.02 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 125.2773 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:11 | 125.3789 | 0.02 | 1.02 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 125.4805 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 125.5898 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 125.6875 | 0.03 | 1.03 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 125.7891 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 125.8984 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 126 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:11 | 126.0977 | -0.1 | 0.9 | -0.71 | 0.29 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:11 | 126.1992 | -0.13 | 0.87 | -0.67 | 0.33 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:11 | 126.3086 | -0.15 | 0.85 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:11 | 126.4102 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 126.5078 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:11 | 126.6094 | 0.03 | 1.03 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:11 | 126.7188 | 0.02 | 1.02 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:11 | 126.8203 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 126.9297 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:11 | 127.0273 | 0.03 | 1.03 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:11 | 127.1289 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:11 | 127.2383 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:11 | 127.3398 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:11 | 127.4375 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:11 | 127.5391 | -0.07 | 0.93 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:11 | 127.6406 | -0.12 | 0.88 | -0.68 | 0.32 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:11 | 127.75 | -0.13 | 0.87 | -0.66 | 0.34 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:11 | 127.8477 | -0.02 | 0.98 | -0.77 | 0.23 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:11 | 127.9492 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:11 | 128.0586 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:11 | 128.1602 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:11 | 128.2578 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:11 | 128.3594 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:11 | 128.4688 | 0.03 | 1.03 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:12 | 128.5703 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 128.668 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 128.7695 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 128.8711 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:12 | 128.9805 | 0.02 | 1.02 | -0.81 | 0.19 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:12 | 129.0781 | -0.08 | 0.92 | -0.72 | 0.28 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 129.1875 | -0.15 | 0.85 | -0.67 | 0.33 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 129.2891 | -0.16 | 0.84 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 129.3906 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 129.4883 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 129.5977 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 129.6992 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 129.8008 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 129.8984 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 130.0078 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 130.1094 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 130.2109 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 130.3086 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 130.418 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:12 | 130.5195 | -0.03 | 0.97 | -0.75 | 0.25 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 130.6211 | -0.12 | 0.88 | -0.68 | 0.32 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 130.7305 | -0.15 | 0.85 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 130.8281 | -0.08 | 0.92 | -0.68 | 0.32 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 130.9297 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 11:12 | 131.0273 | 0.01 | 1.01 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 131.1406 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 131.2383 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 131.3398 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:12 | 131.4375 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:12 | 131.5508 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 131.6484 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 131.75 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 131.8594 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 131.9609 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 132.0586 | -0.08 | 0.92 | -0.71 | 0.29 | -0.67 | 0.33 | 68.36 | 28.32
2019-09-04 | 11:12 | 132.1602 | -0.13 | 0.87 | -0.64 | 0.36 | -0.67 | 0.33 | 68.36 | 29.3
2019-09-04 | 11:12 | 132.2695 | -0.14 | 0.86 | -0.64 | 0.36 | -0.65 | 0.35 | 70.31 | 30.27
2019-09-04 | 11:12 | 132.3711 | -0.02 | 0.98 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 132.4688 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 132.5703 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 132.6797 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 132.7773 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 132.8906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 132.9883 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:12 | 133.0898 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 133.1875 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 133.2891 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 133.3984 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 133.5 | 0 | 1 | -0.76 | 0.24 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 133.5977 | -0.07 | 0.93 | -0.69 | 0.31 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 11:12 | 133.7109 | -0.15 | 0.85 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 133.8086 | -0.14 | 0.86 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 133.9102 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 134.0195 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 134.1211 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 134.2188 | 0.02 | 1.02 | -0.8 | 0.2 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 134.3203 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 134.4297 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 134.5273 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 134.6289 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 134.7305 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 134.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 134.9375 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 135.0391 | -0.04 | 0.96 | -0.73 | 0.27 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 135.1484 | -0.13 | 0.87 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 135.25 | -0.14 | 0.86 | -0.63 | 0.37 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 11:12 | 135.3477 | -0.01 | 0.99 | -0.76 | 0.24 | -0.66 | 0.34 | 70.31 | 30.27
2019-09-04 | 11:12 | 135.4609 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 135.5586 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 11:12 | 135.6602 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 135.7578 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 135.8594 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 135.9609 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 136.0703 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 136.168 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 136.2695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:12 | 136.3711 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 136.4883 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 136.5781 | -0.08 | 0.92 | -0.71 | 0.29 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 136.6875 | -0.12 | 0.88 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 136.7891 | -0.15 | 0.85 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:12 | 136.8906 | 0 | 1 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 136.9883 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 137.0977 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 137.1992 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 137.3008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 137.3984 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 137.5078 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 137.6094 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 137.7109 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:12 | 137.8203 | 0.03 | 1.03 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 137.918 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 138.0195 | -0.04 | 0.96 | -0.74 | 0.26 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 138.1211 | -0.12 | 0.88 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 11:12 | 138.2305 | -0.15 | 0.85 | -0.64 | 0.36 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 138.3281 | -0.11 | 0.89 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 138.4297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:12 | 138.5273 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 11:12 | 138.6406 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 138.7383 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 138.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 138.9492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 139.0508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 139.1484 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 139.25 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 139.3594 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 139.4609 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 139.5586 | -0.05 | 0.95 | -0.73 | 0.27 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 139.6602 | -0.1 | 0.9 | -0.66 | 0.34 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 139.7695 | -0.14 | 0.86 | -0.63 | 0.37 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:12 | 139.8711 | -0.01 | 0.99 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 139.9688 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 140.0781 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 140.1797 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 140.2773 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 140.3906 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 140.4883 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 140.5898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 140.6875 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 140.7891 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:12 | 140.8984 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 141 | -0.01 | 0.99 | -0.74 | 0.26 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 141.1094 | -0.1 | 0.9 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 141.2109 | -0.14 | 0.86 | -0.65 | 0.35 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:12 | 141.3086 | -0.16 | 0.84 | -0.62 | 0.38 | -0.65 | 0.35 | 71.29 | 31.25
2019-09-04 | 11:12 | 141.4102 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 141.5195 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 141.6211 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 141.7188 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 141.8203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 141.9297 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 142.0273 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 142.1289 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:12 | 142.2305 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 142.3398 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 142.4375 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 142.5391 | -0.05 | 0.95 | -0.73 | 0.27 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 142.6484 | -0.13 | 0.87 | -0.65 | 0.35 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 142.75 | -0.14 | 0.86 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 142.8477 | -0.02 | 0.98 | -0.74 | 0.26 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 142.9492 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:12 | 143.0586 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 143.1602 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 143.2578 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 143.3594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 143.4688 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 143.5703 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 143.6797 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 143.7773 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 143.8789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 143.9805 | -0.01 | 0.99 | -0.77 | 0.23 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 144.0781 | -0.09 | 0.91 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 144.1875 | -0.15 | 0.85 | -0.64 | 0.36 | -0.66 | 0.34 | 72.27 | 30.27
2019-09-04 | 11:12 | 144.2891 | -0.16 | 0.84 | -0.62 | 0.38 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 11:12 | 144.3906 | -0.01 | 0.99 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 144.4883 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 11:12 | 144.5977 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:12 | 144.6992 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 144.8086 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 144.9102 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 145.0078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 145.1094 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:12 | 145.2109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 145.3203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 145.418 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 11:12 | 145.5195 | 0 | 1 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 145.6211 | -0.08 | 0.92 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 145.7305 | -0.14 | 0.86 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 145.8281 | -0.14 | 0.86 | -0.64 | 0.36 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 145.9297 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:12 | 146.0391 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 146.1406 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 146.2383 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:12 | 146.3477 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 146.4492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 146.5508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 146.6484 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 146.75 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 146.8594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 146.9609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 147.0703 | -0.04 | 0.96 | -0.73 | 0.27 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 147.168 | -0.12 | 0.88 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:12 | 147.2695 | -0.15 | 0.85 | -0.63 | 0.37 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:12 | 147.3711 | 0 | 1 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 147.4805 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 147.5781 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 147.6797 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 147.7773 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 147.8789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 147.9883 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 148.0898 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 148.1875 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 148.2891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:12 | 148.3984 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 148.5 | 0.01 | 1.01 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:12 | 148.6094 | -0.1 | 0.9 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 11:12 | 148.7109 | -0.15 | 0.85 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 148.8086 | -0.15 | 0.85 | -0.61 | 0.39 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 148.9102 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 149.0195 | 0.01 | 1.01 | -0.78 | 0.22 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 149.1211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 149.2188 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 149.3203 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 149.4297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 11:12 | 149.5273 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 149.6406 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 149.7383 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 149.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 149.9375 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 150.0391 | -0.02 | 0.98 | -0.74 | 0.26 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 150.1484 | -0.08 | 0.92 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:12 | 150.25 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 150.3477 | -0.01 | 0.99 | -0.72 | 0.28 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:12 | 150.4492 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 150.5586 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 150.6602 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 150.7578 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 150.8711 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 150.9688 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 151.0703 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 151.168 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 151.2773 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:12 | 151.3789 | 0.05 | 1.05 | -0.8 | 0.2 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:12 | 151.4805 | 0.02 | 1.02 | -0.76 | 0.24 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:12 | 151.5781 | -0.1 | 0.9 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 151.6875 | -0.14 | 0.86 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 151.7891 | -0.15 | 0.85 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 151.8906 | 0 | 1 | -0.76 | 0.24 | -0.66 | 0.34 | 69.34 | 29.3
2019-09-04 | 11:12 | 152 | 0.01 | 1.01 | -0.79 | 0.21 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 152.0977 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 152.1992 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 152.3086 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 152.4102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 152.5078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 152.6094 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 152.7109 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 152.8203 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 152.918 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 153.0273 | -0.04 | 0.96 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 153.1289 | -0.09 | 0.91 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 153.2305 | -0.14 | 0.86 | -0.62 | 0.38 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 153.3281 | -0.16 | 0.84 | -0.62 | 0.38 | -0.66 | 0.34 | 72.27 | 30.27
2019-09-04 | 11:12 | 153.4375 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 153.5391 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 153.6406 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 153.7383 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 153.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 153.9492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 154.0508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 154.1484 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 154.25 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 154.3594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 154.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 154.5703 | -0.04 | 0.96 | -0.71 | 0.29 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 154.668 | -0.11 | 0.89 | -0.66 | 0.34 | -0.67 | 0.33 | 70.31 | 31.25
2019-09-04 | 11:12 | 154.7695 | -0.13 | 0.87 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 154.8711 | 0 | 1 | -0.76 | 0.24 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:12 | 154.9805 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 155.0781 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 155.1797 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 155.2773 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 155.3906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 155.4883 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:12 | 155.5898 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 155.6992 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 155.8008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 70.31 | 29.3
2019-09-04 | 11:12 | 155.8984 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 156 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 156.1094 | -0.07 | 0.93 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 156.2109 | -0.15 | 0.85 | -0.64 | 0.36 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 11:12 | 156.3086 | -0.14 | 0.86 | -0.62 | 0.38 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 11:12 | 156.4102 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 156.5195 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 156.6211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 156.7188 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 156.8281 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 156.9297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 157.0273 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 11:12 | 157.1289 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 157.2383 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 11:12 | 157.3398 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 157.4375 | 0.02 | 1.02 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 157.5391 | -0.03 | 0.97 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:12 | 157.6484 | -0.13 | 0.87 | -0.66 | 0.34 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 157.75 | -0.13 | 0.87 | -0.63 | 0.37 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 157.8594 | -0.05 | 0.95 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:12 | 157.9492 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 158.0586 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 158.1602 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 158.2695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 158.3711 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 158.4688 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 158.5703 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 158.668 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 158.7773 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 158.8789 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 158.9805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 159.0898 | -0.02 | 0.98 | -0.73 | 0.27 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 159.1875 | -0.12 | 0.88 | -0.65 | 0.35 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 159.2891 | -0.15 | 0.85 | -0.64 | 0.36 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 159.3984 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 159.5 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 11:12 | 159.5977 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 159.6992 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 159.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 159.9102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 160.0078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 160.1094 | 0.05 | 1.05 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 160.2109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 160.3203 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 160.418 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 160.5273 | -0.01 | 0.99 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:12 | 160.6289 | -0.11 | 0.89 | -0.67 | 0.33 | -0.66 | 0.34 | 71.29 | 30.27
2019-09-04 | 11:12 | 160.7305 | -0.13 | 0.87 | -0.63 | 0.37 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:12 | 160.8281 | -0.14 | 0.86 | -0.62 | 0.38 | -0.66 | 0.34 | 71.29 | 30.27
2019-09-04 | 11:12 | 160.9375 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 161.0391 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 161.1406 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 161.2383 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:12 | 161.3477 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 161.4492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 161.5508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:12 | 161.6602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 161.7578 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 161.8594 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 161.9688 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 162.0703 | -0.02 | 0.98 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:12 | 162.168 | -0.1 | 0.9 | -0.68 | 0.32 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 162.2695 | -0.14 | 0.86 | -0.65 | 0.35 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 162.3711 | -0.01 | 0.99 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 162.4805 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 162.5781 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 162.6797 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 162.7773 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 162.8906 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 162.9883 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 163.0898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 163.1992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 163.3008 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 163.3984 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 163.5 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 163.6094 | -0.11 | 0.89 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 163.7109 | -0.14 | 0.86 | -0.65 | 0.35 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 163.8203 | -0.15 | 0.85 | -0.62 | 0.38 | -0.66 | 0.34 | 70.31 | 28.32
2019-09-04 | 11:12 | 163.9102 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 164.0195 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 164.1211 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:12 | 164.2188 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 164.3281 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 164.4297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 164.5273 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 164.6289 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 164.7383 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 164.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 164.9375 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 165.0508 | -0.01 | 0.99 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 165.1484 | -0.1 | 0.9 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 165.25 | -0.13 | 0.87 | -0.63 | 0.37 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 165.3594 | -0.06 | 0.94 | -0.68 | 0.32 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 165.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 165.5586 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 11:12 | 165.6602 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 165.7695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 165.8711 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 165.9688 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 166.0703 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:12 | 166.168 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:12 | 166.2773 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 166.3789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 166.4883 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:12 | 166.5898 | -0.05 | 0.95 | -0.72 | 0.28 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 166.6875 | -0.12 | 0.88 | -0.65 | 0.35 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 166.7891 | -0.12 | 0.88 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 166.8984 | 0.01 | 1.01 | -0.76 | 0.24 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 167 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:12 | 167.0977 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 167.1992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:12 | 167.3086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 167.4102 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 167.5078 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 167.6211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 167.7188 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 167.8203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 167.918 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 168.0273 | 0.02 | 1.02 | -0.77 | 0.23 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 168.1289 | -0.08 | 0.92 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 168.2305 | -0.12 | 0.88 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:12 | 168.3281 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 168.4375 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 168.5391 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 168.6406 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 168.75 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 168.8477 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 168.9492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 169.0508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 169.1602 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 169.2578 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:12 | 169.3594 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 169.4688 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 169.5703 | -0.02 | 0.98 | -0.74 | 0.26 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 169.668 | -0.11 | 0.89 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:12 | 169.7773 | -0.12 | 0.88 | -0.65 | 0.35 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 169.8711 | 0.01 | 1.01 | -0.74 | 0.26 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 169.9805 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 170.0781 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 170.1797 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 170.2891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 170.3906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 170.4883 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 170.5898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 170.6992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 11:12 | 170.8008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 11:12 | 170.8984 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 171 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:12 | 171.1094 | -0.04 | 0.96 | -0.72 | 0.28 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 171.2109 | -0.13 | 0.87 | -0.65 | 0.35 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 171.3086 | -0.13 | 0.87 | -0.63 | 0.37 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:12 | 171.418 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 171.5195 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 171.6211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:12 | 171.7305 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 171.8281 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 171.9297 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:12 | 172.0273 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 172.1289 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 172.2383 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:12 | 172.3398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 70.31 | 28.32
2019-09-04 | 11:12 | 172.4492 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 172.5508 | 0.01 | 1.01 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:12 | 172.6484 | -0.07 | 0.93 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 172.75 | -0.13 | 0.87 | -0.63 | 0.37 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 172.8594 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 172.9609 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 173.0586 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 173.1602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:12 | 173.2695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 173.3711 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:12 | 173.4688 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 173.5781 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 173.6797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 173.7773 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 173.8789 | 0.05 | 1.05 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 11:12 | 173.9883 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 174.0898 | -0.05 | 0.95 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 174.1875 | -0.12 | 0.88 | -0.64 | 0.36 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 174.2891 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 174.3984 | -0.01 | 0.99 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 174.5 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 174.5977 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 174.6992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 174.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 174.9102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 175.0078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 11:12 | 175.1211 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 175.2188 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 175.3203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 175.418 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 175.5273 | 0 | 1 | -0.75 | 0.25 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:12 | 175.6289 | -0.11 | 0.89 | -0.66 | 0.34 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:12 | 175.7383 | -0.14 | 0.86 | -0.64 | 0.36 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 175.8398 | -0.15 | 0.85 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 31.25
2019-09-04 | 11:12 | 175.9375 | 0.02 | 1.02 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 176.0391 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 176.1406 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 176.25 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 176.3477 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 176.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 176.5508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 176.6602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 176.7578 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 176.8594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:12 | 176.9609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 177.0703 | -0.05 | 0.95 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:12 | 177.168 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 177.2773 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 177.3789 | -0.02 | 0.98 | -0.72 | 0.28 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 177.4805 | 0.03 | 1.03 | -0.77 | 0.23 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 177.5781 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:12 | 177.6875 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 177.7891 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 177.8906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 177.9883 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 178.0898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:12 | 178.1992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:12 | 178.3008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 178.4102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 178.5078 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 178.6094 | -0.06 | 0.94 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 178.7188 | -0.12 | 0.88 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 178.8203 | -0.14 | 0.86 | -0.61 | 0.39 | -0.67 | 0.33 | 71.29 | 31.25
2019-09-04 | 11:12 | 178.918 | 0.01 | 1.01 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 179.0195 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 179.1211 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:12 | 179.2305 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 179.3281 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:12 | 179.4297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 179.5391 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 179.6406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 179.7383 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 179.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 179.9492 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 180.0508 | -0.03 | 0.97 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 180.1484 | -0.12 | 0.88 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 180.25 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 180.3594 | -0.14 | 0.86 | -0.6 | 0.4 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 180.4609 | 0.01 | 1.01 | -0.76 | 0.24 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 180.5586 | 0.02 | 1.02 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 180.6602 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 180.7695 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 180.8711 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:12 | 180.9688 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:12 | 181.0781 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 181.1797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 181.2773 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 181.3789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 181.4883 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 181.5898 | -0.05 | 0.95 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 181.6992 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:12 | 181.8008 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 181.8984 | 0 | 1 | -0.74 | 0.26 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 182 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 182.0977 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:12 | 182.2109 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 182.3086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:12 | 182.4102 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 182.5078 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:12 | 182.6211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:12 | 182.7188 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 182.8203 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 182.918 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:12 | 183.0273 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:12 | 183.1289 | -0.08 | 0.92 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 183.2383 | -0.11 | 0.89 | -0.64 | 0.36 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:12 | 183.3398 | -0.16 | 0.84 | -0.63 | 0.37 | -0.66 | 0.34 | 70.31 | 30.27
2019-09-04 | 11:12 | 183.4375 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 183.5391 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:12 | 183.6484 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 183.75 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 183.8477 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:12 | 183.9492 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 184.0508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 184.1602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:12 | 184.2578 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:12 | 184.3711 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 184.4688 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 184.5703 | -0.02 | 0.98 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:12 | 184.668 | -0.11 | 0.89 | -0.66 | 0.34 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 184.7773 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 184.8789 | -0.03 | 0.97 | -0.71 | 0.29 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 184.9805 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 185.0781 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:12 | 185.1797 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 185.2891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:12 | 185.3906 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 185.5 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:12 | 185.5977 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 185.6992 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:12 | 185.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 185.9102 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 186.0078 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:12 | 186.1094 | -0.06 | 0.94 | -0.7 | 0.3 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:12 | 186.2109 | -0.12 | 0.88 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 186.3203 | -0.12 | 0.88 | -0.61 | 0.39 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:12 | 186.418 | 0.01 | 1.01 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:12 | 186.5195 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 186.6211 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 186.7305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 186.8281 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 186.9297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 187.0391 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:12 | 187.1406 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 11:12 | 187.2383 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:12 | 187.3398 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:12 | 187.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:12 | 187.5508 | 0 | 1 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 187.6602 | -0.1 | 0.9 | -0.66 | 0.34 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 187.7578 | -0.13 | 0.87 | -0.63 | 0.37 | -0.67 | 0.33 | 69.34 | 29.3
2019-09-04 | 11:12 | 187.8594 | -0.12 | 0.88 | -0.61 | 0.39 | -0.66 | 0.34 | 70.31 | 28.32
2019-09-04 | 11:12 | 187.9609 | 0.04 | 1.04 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:12 | 188.0586 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:12 | 188.168 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:12 | 188.2695 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:12 | 188.3711 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:12 | 188.4688 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:12 | 188.5781 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 188.6797 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:12 | 188.7773 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:12 | 188.8789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 11:12 | 188.9883 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:12 | 189.0898 | -0.01 | 0.99 | -0.73 | 0.27 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 189.1992 | -0.08 | 0.92 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:12 | 189.3008 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:12 | 189.3984 | 0 | 1 | -0.74 | 0.26 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:13 | 189.5 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:13 | 189.5977 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 189.7109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 189.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 189.9102 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 11:13 | 190.0078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 190.1211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 190.2188 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 190.3281 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 190.4297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 190.5273 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 190.6289 | -0.06 | 0.94 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 190.7383 | -0.1 | 0.9 | -0.64 | 0.36 | -0.67 | 0.33 | 72.27 | 30.27
2019-09-04 | 11:13 | 190.8398 | -0.14 | 0.86 | -0.61 | 0.39 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:13 | 190.9375 | 0.03 | 1.03 | -0.77 | 0.23 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 191.0391 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 191.1484 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 191.25 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 191.3477 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 191.4492 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 191.5586 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 191.6602 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 191.7578 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 191.8711 | 0.05 | 1.05 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 191.9688 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 70.31 | 28.32
2019-09-04 | 11:13 | 192.0703 | 0.02 | 1.02 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 192.168 | -0.09 | 0.91 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 192.2773 | -0.12 | 0.88 | -0.64 | 0.36 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 192.3789 | -0.07 | 0.93 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 192.4805 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 192.5781 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 192.6875 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 192.7891 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 192.8906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 193 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 193.0977 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 193.1992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 193.3008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:13 | 193.4102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 193.5078 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 193.6094 | -0.06 | 0.94 | -0.68 | 0.32 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 193.7188 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 193.8203 | -0.13 | 0.87 | -0.62 | 0.38 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 11:13 | 193.918 | 0.01 | 1.01 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 194.0195 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 194.1289 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 11:13 | 194.2305 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 194.3281 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 194.4297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 194.5391 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 194.6406 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 194.7383 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 194.8398 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 194.9492 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 195.0508 | 0 | 1 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:13 | 195.1484 | -0.11 | 0.89 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 195.2578 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 195.3594 | -0.14 | 0.86 | -0.6 | 0.4 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 11:13 | 195.4609 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 195.5586 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 195.668 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 195.7695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 195.8711 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 195.9688 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 196.0781 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 11:13 | 196.1797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 11:13 | 196.2891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 196.3906 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 196.4883 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 196.5898 | -0.03 | 0.97 | -0.73 | 0.27 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 196.6875 | -0.12 | 0.88 | -0.66 | 0.34 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 196.8008 | -0.13 | 0.87 | -0.63 | 0.37 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 196.8984 | 0.01 | 1.01 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:13 | 197 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:13 | 197.1094 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 197.2109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 197.3086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 197.4102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 197.5195 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:13 | 197.6211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 197.7188 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 197.8281 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 197.9297 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 198.0273 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 198.1289 | -0.09 | 0.91 | -0.67 | 0.33 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 198.2383 | -0.13 | 0.87 | -0.64 | 0.36 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 198.3398 | -0.16 | 0.84 | -0.61 | 0.39 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:13 | 198.4375 | 0.01 | 1.01 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 11:13 | 198.5391 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 198.6484 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 198.7578 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 198.8477 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 198.9609 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 199.0586 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 199.1602 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 199.2578 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 199.3711 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:13 | 199.4688 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 199.5703 | -0.03 | 0.97 | -0.72 | 0.28 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 199.6797 | -0.12 | 0.88 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 199.7773 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 199.8789 | -0.07 | 0.93 | -0.65 | 0.35 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 11:13 | 199.9805 | 0.04 | 1.04 | -0.76 | 0.24 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 200.0898 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 200.1875 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 200.2891 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 200.3906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 200.5 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 200.5977 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 200.6992 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 200.8086 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:13 | 200.9102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 201.0078 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 201.1094 | 0 | 1 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:13 | 201.2188 | -0.09 | 0.91 | -0.66 | 0.34 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 201.3203 | -0.13 | 0.87 | -0.63 | 0.37 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 11:13 | 201.418 | 0 | 1 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 201.5273 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 201.6289 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 11:13 | 201.7305 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 201.8281 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 201.9297 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 202.0391 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:13 | 202.1406 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:13 | 202.25 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 202.3477 | 0.08 | 1.08 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 202.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 202.5508 | 0 | 1 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 202.6602 | -0.07 | 0.93 | -0.66 | 0.34 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:13 | 202.7578 | -0.13 | 0.87 | -0.63 | 0.37 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 202.8594 | -0.13 | 0.87 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 202.9609 | 0.02 | 1.02 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 203.0586 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:13 | 203.168 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 203.2695 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:13 | 203.3711 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 203.4805 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 203.5781 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 203.6797 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 203.7891 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 203.8906 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 203.9883 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 204.0898 | -0.04 | 0.96 | -0.71 | 0.29 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 11:13 | 204.1992 | -0.1 | 0.9 | -0.65 | 0.35 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 204.3008 | -0.12 | 0.88 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 204.3984 | -0.01 | 0.99 | -0.73 | 0.27 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 204.5 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:13 | 204.6094 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 204.7109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:13 | 204.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 204.918 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 205.0195 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 205.1211 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 205.2188 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 205.3281 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 205.4297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 205.5273 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 205.6406 | -0.04 | 0.96 | -0.7 | 0.3 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 205.7383 | -0.11 | 0.89 | -0.64 | 0.36 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 205.8398 | -0.13 | 0.87 | -0.63 | 0.37 | -0.66 | 0.34 | 70.31 | 28.32
2019-09-04 | 11:13 | 205.9375 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 206.0508 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 206.1484 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 206.25 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 206.3477 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 206.4688 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 206.5586 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 206.6602 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 206.7578 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 206.8711 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 206.9688 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 207.0703 | -0.01 | 0.99 | -0.72 | 0.28 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 207.1797 | -0.12 | 0.88 | -0.63 | 0.37 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 11:13 | 207.2773 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 11:13 | 207.3789 | -0.13 | 0.87 | -0.61 | 0.39 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:13 | 207.4805 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 207.5898 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 207.6875 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 11:13 | 207.7891 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 207.8906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 208 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 208.0977 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 208.2109 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 208.3086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 208.4102 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 208.5078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 11:13 | 208.6211 | -0.05 | 0.95 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:13 | 208.7188 | -0.13 | 0.87 | -0.64 | 0.36 | -0.67 | 0.33 | 71.29 | 28.32
2019-09-04 | 11:13 | 208.8203 | -0.13 | 0.87 | -0.61 | 0.39 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 208.918 | 0.01 | 1.01 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 30.27
2019-09-04 | 11:13 | 209.0273 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 209.1289 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 209.2305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 209.3281 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 209.4375 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 209.5391 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 209.6406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 209.75 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 209.8477 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:13 | 209.9492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 210.0508 | -0.01 | 0.99 | -0.73 | 0.27 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 210.1602 | -0.08 | 0.92 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 210.2578 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 210.3594 | -0.14 | 0.86 | -0.6 | 0.4 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 210.4609 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 210.5586 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 210.668 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 210.7695 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 210.8789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 210.9805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 211.0781 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 211.1797 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 211.2891 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 211.3906 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 211.4883 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 11:13 | 211.5977 | -0.02 | 0.98 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 211.6992 | -0.09 | 0.91 | -0.65 | 0.35 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 211.8086 | -0.13 | 0.87 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 211.8984 | 0 | 1 | -0.71 | 0.29 | -0.66 | 0.34 | 72.27 | 31.25
2019-09-04 | 11:13 | 212.0078 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 212.1094 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 212.2109 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 212.3086 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 212.418 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 212.5195 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 212.6211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 212.7188 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 212.8281 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 212.9297 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 213.0391 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 213.1406 | -0.1 | 0.9 | -0.66 | 0.34 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 213.2383 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:13 | 213.3398 | -0.13 | 0.87 | -0.61 | 0.39 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 11:13 | 213.4492 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 213.5508 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 213.6484 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 213.75 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:13 | 213.8477 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 213.9609 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 214.0586 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 214.168 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 214.2695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 214.3711 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 214.4688 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 214.5781 | -0.01 | 0.99 | -0.72 | 0.28 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 214.6797 | -0.1 | 0.9 | -0.66 | 0.34 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 214.7773 | -0.13 | 0.87 | -0.62 | 0.38 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:13 | 214.8789 | -0.13 | 0.87 | -0.61 | 0.39 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:13 | 214.9883 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 215.0898 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 215.1875 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 215.2891 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 215.3984 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 215.5 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 11:13 | 215.5977 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 215.7109 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:13 | 215.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 215.9102 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 216.0078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 216.1211 | -0.04 | 0.96 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 216.2188 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:13 | 216.3203 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:13 | 216.418 | 0.01 | 1.01 | -0.74 | 0.26 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:13 | 216.5195 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 216.6289 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 216.7305 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 216.8398 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 216.9375 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:13 | 217.0391 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 217.1406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 217.25 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:13 | 217.3477 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:13 | 217.4492 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:13 | 217.5508 | 0.02 | 1.02 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 217.6602 | -0.08 | 0.92 | -0.66 | 0.34 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 217.7578 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 217.8594 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 217.9688 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:13 | 218.0703 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 218.168 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 218.2695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 218.3789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 218.4805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 218.5781 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 218.6797 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 218.7891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 218.8906 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 218.9883 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 219.0977 | -0.01 | 0.99 | -0.73 | 0.27 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 219.1992 | -0.09 | 0.91 | -0.66 | 0.34 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 219.3008 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:13 | 219.3984 | -0.03 | 0.97 | -0.7 | 0.3 | -0.67 | 0.33 | 71.29 | 28.32
2019-09-04 | 11:13 | 219.5078 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 219.6094 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 219.7109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 219.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 219.918 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 220.0195 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 220.1211 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 220.2305 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 220.3281 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 11:13 | 220.4297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 220.5391 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:13 | 220.6406 | -0.02 | 0.98 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 220.7383 | -0.11 | 0.89 | -0.64 | 0.36 | -0.68 | 0.32 | 73.24 | 29.3
2019-09-04 | 11:13 | 220.8398 | -0.13 | 0.87 | -0.61 | 0.39 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 220.9375 | 0.01 | 1.01 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 221.0508 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 221.1484 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:13 | 221.25 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 221.3594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:13 | 221.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 221.5586 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 221.668 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:13 | 221.7695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 221.8711 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 221.9688 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 222.0781 | 0 | 1 | -0.74 | 0.26 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 222.1797 | -0.1 | 0.9 | -0.66 | 0.34 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 222.2773 | -0.13 | 0.87 | -0.63 | 0.37 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:13 | 222.3906 | -0.14 | 0.86 | -0.63 | 0.37 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 222.4805 | 0.01 | 1.01 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 222.5898 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 222.6875 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 222.8008 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 222.8984 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 223 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 223.0977 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 223.2109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 223.3086 | 0.05 | 1.05 | -0.79 | 0.21 | -0.72 | 0.28 | 70.31 | 28.32
2019-09-04 | 11:13 | 223.4102 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 223.5078 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:13 | 223.6211 | -0.01 | 0.99 | -0.72 | 0.28 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 223.7188 | -0.11 | 0.89 | -0.64 | 0.36 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 223.8281 | -0.13 | 0.87 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 223.9297 | 0.02 | 1.02 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 224.0273 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 11:13 | 224.1289 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 224.2305 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 224.3398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 224.4375 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 11:13 | 224.5391 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 224.6406 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 224.75 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 224.8477 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:13 | 224.9609 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 29.3
2019-09-04 | 11:13 | 225.0586 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 225.1602 | -0.07 | 0.93 | -0.69 | 0.31 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 225.2578 | -0.13 | 0.87 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 225.3594 | -0.14 | 0.86 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 225.4688 | 0.02 | 1.02 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 225.5703 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 225.668 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:13 | 225.7695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 225.8789 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 225.9805 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 226.0781 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 226.1875 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:13 | 226.2891 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 226.3906 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 226.5 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:13 | 226.5977 | 0 | 1 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 226.6992 | -0.09 | 0.91 | -0.65 | 0.35 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 226.8008 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:13 | 226.8984 | -0.08 | 0.92 | -0.67 | 0.33 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:13 | 227.0078 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:13 | 227.1094 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 227.2109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 227.3203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 227.418 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 227.5195 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 227.6289 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 227.7305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:13 | 227.8281 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 227.9297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 228.0391 | 0.07 | 1.07 | -0.79 | 0.21 | -0.72 | 0.28 | 71.29 | 30.27
2019-09-04 | 11:13 | 228.1406 | -0.04 | 0.96 | -0.72 | 0.28 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 228.2383 | -0.09 | 0.91 | -0.65 | 0.35 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 228.3477 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 228.4492 | 0 | 1 | -0.74 | 0.26 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 228.5508 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 228.6484 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 228.7578 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 228.8594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 228.9609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 229.0586 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 229.168 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 229.2695 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 229.3711 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 229.4688 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 229.5781 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:13 | 229.6797 | -0.07 | 0.93 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 229.7773 | -0.12 | 0.88 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 229.8906 | -0.14 | 0.86 | -0.61 | 0.39 | -0.67 | 0.33 | 73.24 | 30.27
2019-09-04 | 11:13 | 229.9883 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 230.0898 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 11:13 | 230.1875 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 230.3008 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 230.3984 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 230.5 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 230.5977 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:13 | 230.7109 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 30.27
2019-09-04 | 11:13 | 230.8086 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:13 | 230.9102 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 231.0195 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 70.31 | 29.3
2019-09-04 | 11:13 | 231.1211 | -0.01 | 0.99 | -0.73 | 0.27 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 231.2188 | -0.08 | 0.92 | -0.65 | 0.35 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 231.3203 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 231.4297 | 0 | 1 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 231.5273 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 231.6289 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 231.7305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 231.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 231.9375 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 232.0508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 232.1484 | 0.05 | 1.05 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 232.25 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 11:13 | 232.3477 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 11:13 | 232.4609 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 232.5586 | 0.04 | 1.04 | -0.76 | 0.24 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 11:13 | 232.6602 | -0.07 | 0.93 | -0.68 | 0.32 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:13 | 232.7578 | -0.09 | 0.91 | -0.63 | 0.37 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:13 | 232.8711 | -0.11 | 0.89 | -0.61 | 0.39 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:13 | 232.9688 | 0.01 | 1.01 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 233.0703 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 233.168 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 233.2773 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 233.3789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:13 | 233.4805 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:13 | 233.5898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 233.6875 | 0.05 | 1.05 | -0.79 | 0.21 | -0.72 | 0.28 | 71.29 | 31.25
2019-09-04 | 11:13 | 233.7891 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 233.8906 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:13 | 233.9883 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 234.0977 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 234.1992 | -0.04 | 0.96 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:13 | 234.3086 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 234.4102 | -0.11 | 0.89 | -0.65 | 0.35 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 234.5078 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 234.6211 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 234.7188 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:13 | 234.8203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 234.918 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 235.0195 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:13 | 235.1289 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 235.2305 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 235.3281 | 0.05 | 1.05 | -0.79 | 0.21 | -0.73 | 0.27 | 70.31 | 29.3
2019-09-04 | 11:13 | 235.4297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 29.3
2019-09-04 | 11:13 | 235.5273 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 235.6406 | -0.04 | 0.96 | -0.7 | 0.3 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 235.7383 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 235.8477 | -0.13 | 0.87 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 30.27
2019-09-04 | 11:13 | 235.9492 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 11:13 | 236.0508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 236.1484 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 236.2578 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 236.3594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 236.4688 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:13 | 236.5586 | 0.05 | 1.05 | -0.79 | 0.21 | -0.72 | 0.28 | 71.29 | 29.3
2019-09-04 | 11:13 | 236.668 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 236.7695 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 11:13 | 236.8711 | 0.08 | 1.08 | -0.79 | 0.21 | -0.72 | 0.28 | 71.29 | 29.3
2019-09-04 | 11:13 | 236.9805 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:13 | 237.0781 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:13 | 237.1797 | -0.07 | 0.93 | -0.68 | 0.32 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 237.2773 | -0.12 | 0.88 | -0.63 | 0.37 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 237.3906 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 237.4883 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 237.5898 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 237.6875 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:13 | 237.8008 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 237.8984 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 238.0078 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 238.1094 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 238.2109 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 238.3086 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 238.4102 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 238.5195 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 30.27
2019-09-04 | 11:13 | 238.6211 | -0.02 | 0.98 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 238.7305 | -0.11 | 0.89 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:13 | 238.8203 | -0.13 | 0.87 | -0.62 | 0.38 | -0.66 | 0.34 | 71.29 | 30.27
2019-09-04 | 11:13 | 238.9297 | -0.01 | 0.99 | -0.73 | 0.27 | -0.67 | 0.33 | 71.29 | 28.32
2019-09-04 | 11:13 | 239.0273 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 239.1289 | 0.04 | 1.04 | -0.77 | 0.23 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 239.2383 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 239.3398 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 239.4375 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:13 | 239.5508 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 11:13 | 239.6484 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 239.75 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 239.8477 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 239.9609 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:13 | 240.0586 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 240.1602 | -0.07 | 0.93 | -0.69 | 0.31 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:13 | 240.2695 | -0.11 | 0.89 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 240.3711 | -0.13 | 0.87 | -0.63 | 0.37 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 240.4688 | 0.01 | 1.01 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 240.5703 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 240.6797 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 240.7773 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:13 | 240.8789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 240.9805 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:13 | 241.0898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 241.1875 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 241.2891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 241.3906 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 11:13 | 241.5 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 29.3
2019-09-04 | 11:13 | 241.5977 | 0.02 | 1.02 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 241.6992 | -0.08 | 0.92 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:13 | 241.8086 | -0.13 | 0.87 | -0.63 | 0.37 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:13 | 241.9102 | -0.11 | 0.89 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:13 | 242.0078 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 242.1094 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 242.2188 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 242.3203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 242.418 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 242.5195 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 242.6289 | 0.06 | 1.06 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 242.7305 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 242.8281 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 242.9375 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 243.0391 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:13 | 243.1406 | -0.01 | 0.99 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:13 | 243.2383 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:13 | 243.3477 | -0.15 | 0.85 | -0.61 | 0.39 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:13 | 243.4609 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 243.5508 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:13 | 243.6484 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 243.7578 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:13 | 243.8594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 243.9609 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 244.0703 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 244.168 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:13 | 244.2695 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 244.3711 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 244.4805 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 244.5781 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:13 | 244.6797 | -0.04 | 0.96 | -0.71 | 0.29 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 244.7773 | -0.11 | 0.89 | -0.65 | 0.35 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 11:13 | 244.8906 | -0.13 | 0.87 | -0.62 | 0.38 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:13 | 244.9883 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 245.0898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 245.1992 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 245.3008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 245.3984 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 245.5078 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:13 | 245.6094 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 245.7109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:13 | 245.8086 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 245.9102 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 29.3
2019-09-04 | 11:13 | 246.0195 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:13 | 246.1211 | -0.02 | 0.98 | -0.7 | 0.3 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 246.2305 | -0.1 | 0.9 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:13 | 246.3281 | -0.14 | 0.86 | -0.61 | 0.39 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:13 | 246.4297 | 0 | 1 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:13 | 246.5273 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 246.6406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 246.7383 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:13 | 246.8398 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:13 | 246.9375 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:13 | 247.0391 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 247.1484 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:13 | 247.25 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:13 | 247.3477 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:13 | 247.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:13 | 247.5586 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:13 | 247.6602 | 0 | 1 | -0.72 | 0.28 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 247.7695 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:13 | 247.8789 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:13 | 247.9688 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:13 | 248.0703 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:13 | 248.1797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:13 | 248.2773 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:13 | 248.3789 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:13 | 248.4805 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 248.5898 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:14 | 248.6875 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 248.7891 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:14 | 248.8984 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:14 | 249 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 11:14 | 249.0977 | 0.03 | 1.03 | -0.75 | 0.25 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 249.1992 | -0.08 | 0.92 | -0.65 | 0.35 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 249.3086 | -0.11 | 0.89 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:14 | 249.4102 | -0.22 |  | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 28.32 | anomalous boiler pressure removed from analysis
2019-09-04 | 11:14 | 249.5078 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:14 | 249.6094 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 249.7188 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 249.8203 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 249.918 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 11:14 | 250.0273 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 250.1289 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 250.2305 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 250.3281 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 250.4375 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:14 | 250.5391 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 250.6406 | -0.04 | 0.96 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 250.7383 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 30.27
2019-09-04 | 11:14 | 250.8477 | -0.14 | 0.86 | -0.6 | 0.4 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:14 | 250.9492 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:14 | 251.0508 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 251.1484 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 251.2578 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 11:14 | 251.3594 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 251.4688 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 251.5703 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 251.668 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 251.7695 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 251.8711 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 251.9805 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:14 | 252.0781 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 252.1875 | -0.05 | 0.95 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 252.2891 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 11:14 | 252.3906 | -0.12 | 0.88 | -0.61 | 0.39 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:14 | 252.4883 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 252.5977 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 252.6992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 11:14 | 252.8008 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 252.8984 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:14 | 253.0078 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 253.1094 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 253.2109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 253.3086 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 253.418 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:14 | 253.5195 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 253.6211 | 0 | 1 | -0.73 | 0.27 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 253.7305 | -0.1 | 0.9 | -0.65 | 0.35 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 253.8281 | -0.12 | 0.88 | -0.61 | 0.39 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:14 | 253.9297 | -0.02 | 0.98 | -0.68 | 0.32 | -0.66 | 0.34 | 73.24 | 30.27
2019-09-04 | 11:14 | 254.0273 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 254.1406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 254.2383 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 254.3398 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 254.4375 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 254.5508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 254.6484 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 254.75 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 254.8594 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 254.9609 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 255.0586 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 255.1602 | -0.03 | 0.97 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 255.2695 | -0.12 | 0.88 | -0.65 | 0.35 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 255.3711 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:14 | 255.4688 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 255.5703 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 255.6797 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 255.7773 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 255.8789 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 255.9883 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 256.0898 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 256.1875 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:14 | 256.2891 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 256.3984 | 0.04 | 1.04 | -0.78 | 0.22 | -0.72 | 0.28 | 70.31 | 30.27
2019-09-04 | 11:14 | 256.5 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:14 | 256.5977 | 0.01 | 1.01 | -0.73 | 0.27 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 256.6992 | -0.07 | 0.93 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 256.8086 | -0.12 | 0.88 | -0.62 | 0.38 | -0.66 | 0.34 | 72.27 | 31.25
2019-09-04 | 11:14 | 256.9102 | -0.15 | 0.85 | -0.59 | 0.41 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:14 | 257.0078 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 257.1094 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 257.2188 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 257.3203 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 257.4297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 257.5273 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 257.6289 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 257.7305 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 257.8398 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 257.9375 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 258.0391 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 258.1484 | -0.02 | 0.98 | -0.71 | 0.29 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 258.25 | -0.09 | 0.91 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 258.3477 | -0.13 | 0.87 | -0.62 | 0.38 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:14 | 258.4492 | 0.01 | 1.01 | -0.73 | 0.27 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:14 | 258.5586 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 258.6602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 258.7578 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 258.8594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:14 | 258.9609 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 259.0703 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 259.168 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 259.2695 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:14 | 259.3711 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 259.4805 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 259.5781 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 259.6875 | -0.06 | 0.94 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 11:14 | 259.7891 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 11:14 | 259.8906 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:14 | 259.9883 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:14 | 260.0977 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 260.1992 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 260.3008 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 260.3984 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 11:14 | 260.5078 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 260.6094 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 260.7109 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:14 | 260.8203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:14 | 260.918 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:14 | 261.0195 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:14 | 261.1211 | 0.02 | 1.02 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 261.2305 | -0.06 | 0.94 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 261.3281 | -0.13 | 0.87 | -0.61 | 0.39 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:14 | 261.4297 | -0.04 | 0.96 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 261.5273 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 261.6406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 11:14 | 261.7383 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 261.8398 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 261.9492 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 262.0508 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:14 | 262.1484 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 262.25 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 262.3594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 262.4609 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 262.5586 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 262.6602 | -0.03 | 0.97 | -0.71 | 0.29 | -0.68 | 0.32 | 73.24 | 29.3
2019-09-04 | 11:14 | 262.7695 | -0.09 | 0.91 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 262.8711 | -0.1 | 0.9 | -0.61 | 0.39 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:14 | 262.9688 | 0.02 | 1.02 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 263.0703 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 263.1797 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 263.2773 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 263.3789 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 263.4883 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 263.5898 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 29.3
2019-09-04 | 11:14 | 263.6875 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 263.7891 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 11:14 | 263.8984 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:14 | 264 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 264.0977 | 0.01 | 1.01 | -0.73 | 0.27 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 264.2109 | -0.1 | 0.9 | -0.66 | 0.34 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 264.3086 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:14 | 264.4102 | -0.14 | 0.86 | -0.62 | 0.38 | -0.67 | 0.33 | 69.34 | 28.32
2019-09-04 | 11:14 | 264.5195 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:14 | 264.6211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 264.7188 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 11:14 | 264.8203 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 264.9297 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:14 | 265.0273 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 265.1289 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 265.2305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 265.3281 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 265.4375 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 265.5508 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:14 | 265.6484 | -0.01 | 0.99 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 265.75 | -0.09 | 0.91 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 265.8477 | -0.13 | 0.87 | -0.61 | 0.39 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 11:14 | 265.9492 | 0.02 | 1.02 | -0.73 | 0.27 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 266.0586 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 266.1602 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 266.2578 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 266.3594 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 266.4805 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:14 | 266.5703 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 266.668 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 266.7773 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 11:14 | 266.8789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 266.9805 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 267.0781 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 267.1875 | -0.02 | 0.98 | -0.69 | 0.31 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 267.2891 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 11:14 | 267.3906 | -0.12 | 0.88 | -0.61 | 0.39 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:14 | 267.4883 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 267.5977 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 267.6992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 11:14 | 267.8008 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 267.9102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 268.0078 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 268.1094 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 268.2188 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 268.3203 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 268.418 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 29.3
2019-09-04 | 11:14 | 268.5195 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:14 | 268.6211 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 268.7383 | -0.06 | 0.94 | -0.67 | 0.33 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:14 | 268.8281 | -0.11 | 0.89 | -0.63 | 0.37 | -0.67 | 0.33 | 72.27 | 30.27
2019-09-04 | 11:14 | 268.9375 | -0.12 | 0.88 | -0.62 | 0.38 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:14 | 269.0273 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 269.1406 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 269.2383 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 269.3477 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 269.4492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 269.5508 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 269.6484 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 269.75 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 269.8594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 269.9609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:14 | 270.0586 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 270.1602 | 0.01 | 1.01 | -0.74 | 0.26 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 270.2695 | -0.07 | 0.93 | -0.66 | 0.34 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 270.3711 | -0.13 | 0.87 | -0.63 | 0.37 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 270.4805 | 0.02 | 1.02 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 270.5781 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 270.6797 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:14 | 270.7773 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 270.8906 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 270.9883 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 271.0898 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 271.1875 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 271.3008 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:14 | 271.3984 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 271.5 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:14 | 271.6094 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:14 | 271.7109 | -0.02 | 0.98 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 271.8086 | -0.1 | 0.9 | -0.63 | 0.37 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 271.9102 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 272.0195 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 272.1211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 272.2188 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 272.3203 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 272.4297 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 272.5273 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 272.6289 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 272.7383 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:14 | 272.8398 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 11:14 | 272.9375 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 11:14 | 273.0508 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 11:14 | 273.1484 | 0.02 | 1.02 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 273.25 | -0.07 | 0.93 | -0.65 | 0.35 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 273.3477 | -0.11 | 0.89 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 29.3
2019-09-04 | 11:14 | 273.4609 | 0 | 1 | -0.72 | 0.28 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 273.5586 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 273.6602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 11:14 | 273.7578 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 273.8711 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 273.9688 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 274.0703 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 274.168 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 274.2773 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:14 | 274.3789 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 274.4805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:14 | 274.5781 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:14 | 274.6875 | 0 | 1 | -0.73 | 0.27 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 274.7891 | -0.12 | 0.88 | -0.65 | 0.35 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 274.8906 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 11:14 | 274.9883 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 275.0977 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:14 | 275.1992 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 275.3008 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 275.4102 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 275.5078 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 275.6094 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 275.7109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:14 | 275.8203 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 275.918 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 276.0195 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 276.1211 | 0.01 | 1.01 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 276.2305 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 276.3281 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 276.4375 | -0.13 | 0.87 | -0.6 | 0.4 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 276.5391 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:14 | 276.6406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 276.7383 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 11:14 | 276.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 276.9492 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 277.0508 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 277.1484 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 277.25 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 277.3594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 277.4688 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 277.5703 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 277.668 | 0 | 1 | -0.74 | 0.26 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 11:14 | 277.7695 | -0.1 | 0.9 | -0.65 | 0.35 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 277.8711 | -0.12 | 0.88 | -0.63 | 0.37 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 277.9805 | 0.02 | 1.02 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 278.0781 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 278.1797 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 278.2773 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 278.3789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 278.4883 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 278.5898 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 278.6992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 11:14 | 278.8008 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:14 | 278.8984 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 279 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 11:14 | 279.1094 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 279.2109 | -0.06 | 0.94 | -0.69 | 0.31 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 279.3086 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:14 | 279.4102 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 279.5195 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 279.6211 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 279.7188 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 279.8203 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 279.9297 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 280.0273 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 280.1289 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:14 | 280.2383 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 280.3398 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 11:14 | 280.4375 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:14 | 280.5391 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 11:14 | 280.6484 | 0 | 1 | -0.73 | 0.27 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 280.75 | -0.07 | 0.93 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 280.8594 | -0.1 | 0.9 | -0.63 | 0.37 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:14 | 280.9492 | 0.01 | 1.01 | -0.72 | 0.28 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 281.0586 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:14 | 281.1602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 281.2578 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 281.3711 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 281.4688 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 281.5703 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:14 | 281.668 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 281.7773 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 281.8789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 281.9805 | 0.08 | 1.08 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:14 | 282.0781 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 282.1875 | -0.03 | 0.97 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 282.2891 | -0.11 | 0.89 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:14 | 282.3984 | -0.13 | 0.87 | -0.59 | 0.41 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:14 | 282.5 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 282.5977 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 282.6992 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 11:14 | 282.8086 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 282.9102 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 283.0078 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 283.1094 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 283.2109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 283.3203 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 283.418 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 283.5273 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 283.6289 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 283.7305 | -0.05 | 0.95 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 283.8281 | -0.11 | 0.89 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 283.9375 | -0.12 | 0.88 | -0.61 | 0.39 | -0.66 | 0.34 | 70.31 | 28.32
2019-09-04 | 11:14 | 284.0391 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 284.1406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 284.2383 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 284.3477 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 284.4492 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 284.5508 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 284.6602 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 284.7578 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 284.8594 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 284.9609 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 285.0703 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 11:14 | 285.168 | -0.01 | 0.99 | -0.71 | 0.29 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 285.2695 | -0.11 | 0.89 | -0.63 | 0.37 | -0.67 | 0.33 | 71.29 | 28.32
2019-09-04 | 11:14 | 285.3711 | -0.12 | 0.88 | -0.6 | 0.4 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 285.4805 | 0.02 | 1.02 | -0.73 | 0.27 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:14 | 285.5781 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 285.6797 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:14 | 285.7773 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 32.23
2019-09-04 | 11:14 | 285.8906 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 285.9883 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 286.0898 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 11:14 | 286.1992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 286.3008 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 286.3984 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 286.5078 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 11:14 | 286.6094 | 0.02 | 1.02 | -0.72 | 0.28 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 286.7109 | -0.1 | 0.9 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 286.8203 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 11:14 | 286.918 | -0.11 | 0.89 | -0.6 | 0.4 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:14 | 287.0195 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:14 | 287.1211 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 287.2188 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 287.3281 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 287.4297 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 287.5273 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 287.6289 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 287.7383 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 287.8398 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 287.9375 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 288.0508 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 11:14 | 288.1484 | 0 | 1 | -0.71 | 0.29 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 11:14 | 288.25 | -0.07 | 0.93 | -0.63 | 0.37 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:14 | 288.3594 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 29.3
2019-09-04 | 11:14 | 288.4609 | -0.06 | 0.94 | -0.67 | 0.33 | -0.66 | 0.34 | 71.29 | 30.27
2019-09-04 | 11:14 | 288.5586 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 288.6602 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 288.7695 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 288.8711 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 288.9688 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 289.0703 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 289.168 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 289.2773 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 289.3789 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 289.4883 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 289.5898 | 0.04 | 1.04 | -0.78 | 0.22 | -0.72 | 0.28 | 70.31 | 29.3
2019-09-04 | 11:14 | 289.6875 | -0.03 | 0.97 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 289.7891 | -0.1 | 0.9 | -0.64 | 0.36 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 11:14 | 289.8984 | -0.12 | 0.88 | -0.61 | 0.39 | -0.67 | 0.33 | 70.31 | 30.27
2019-09-04 | 11:14 | 290 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 290.0977 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:14 | 290.1992 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 30.27
2019-09-04 | 11:14 | 290.3086 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 290.4102 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 290.5078 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 11:14 | 290.6211 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 290.7188 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 290.8203 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 290.918 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 11:14 | 291.0273 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 291.1289 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 291.2305 | -0.05 | 0.95 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 291.3281 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 291.4375 | -0.12 | 0.88 | -0.59 | 0.41 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 11:14 | 291.5391 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 291.6406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 291.75 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 291.8477 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 291.9492 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 292.0508 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 292.1602 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 11:14 | 292.2578 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:14 | 292.3594 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 292.4688 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 292.5703 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 11:14 | 292.668 | 0 | 1 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 292.7695 | -0.07 | 0.93 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 292.8789 | -0.08 | 0.92 | -0.63 | 0.37 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:14 | 292.9805 | 0.01 | 1.01 | -0.73 | 0.27 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 293.0781 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 293.1875 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:14 | 293.2891 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 293.3906 | 0.05 | 1.05 | -0.76 | 0.24 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:14 | 293.4883 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 293.5977 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 293.6992 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 293.8008 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 293.8984 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 11:14 | 294 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 294.1094 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 11:14 | 294.2109 | -0.04 | 0.96 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 294.3203 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 294.418 | -0.1 | 0.9 | -0.59 | 0.41 | -0.66 | 0.34 | 73.24 | 30.27
2019-09-04 | 11:14 | 294.5195 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:14 | 294.6211 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 294.7188 | 0.06 | 1.06 | -0.75 | 0.25 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:14 | 294.8281 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 294.9297 | 0.06 | 1.06 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 11:14 | 295.0273 | 0.07 | 1.07 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 295.1406 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 295.2383 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 11:14 | 295.3398 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 295.4492 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 295.5508 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 11:14 | 295.6484 | 0.04 | 1.04 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 11:14 | 295.75 | -0.07 | 0.93 | -0.65 | 0.35 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 295.8594 | -0.1 | 0.9 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 31.25
2019-09-04 | 11:14 | 295.9609 | -0.05 | 0.95 | -0.65 | 0.35 | -0.66 | 0.34 | 70.31 | 29.3
2019-09-04 | 11:14 | 296.0586 | 0.04 | 1.04 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 29.3
2019-09-04 | 11:14 | 296.1602 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 296.2695 | 0.05 | 1.05 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 296.3711 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 296.4688 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 296.5781 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 296.6797 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 11:14 | 296.7773 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 11:14 | 296.8789 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 296.9883 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 297.0898 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 297.1875 | -0.06 | 0.94 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 11:14 | 297.2891 | -0.11 | 0.89 | -0.6 | 0.4 | -0.66 | 0.34 | 72.27 | 30.27
2019-09-04 | 11:14 | 297.3984 | -0.13 | 0.87 | -0.59 | 0.41 | -0.67 | 0.33 | 72.27 | 30.27
2019-09-04 | 11:14 | 297.5 | 0.02 | 1.02 | -0.74 | 0.26 | -0.66 | 0.34 | 71.29 | 28.32
2019-09-04 | 11:14 | 297.5977 | 0.04 | 1.04 | -0.76 | 0.24 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:14 | 297.6992 | 0.07 | 1.07 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:14 | 297.8086 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 297.9102 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 298.0078 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 298.1211 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 11:14 | 298.2188 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 11:14 | 298.3203 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 298.418 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 298.5273 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 298.6289 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 11:14 | 298.75 | -0.06 | 0.94 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 298.8398 | -0.1 | 0.9 | -0.63 | 0.37 | -0.67 | 0.33 | 71.29 | 30.27
2019-09-04 | 11:14 | 298.9375 | -0.13 | 0.87 | -0.6 | 0.4 | -0.66 | 0.34 | 72.27 | 30.27
2019-09-04 | 11:14 | 299.0391 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 11:14 | 299.1484 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 299.25 | 0.06 | 1.06 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 11:14 | 299.3477 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 11:14 | 299.4609 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 299.5508 | 0.07 | 1.07 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 11:14 | 299.6602 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 11:14 | 299.7578 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 299.8594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 299.9609 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 11:14 | 300.0703 | 0.07 | 1.07 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 11:14 | 300.168 | 0.02 | 1.02 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 11:14 | 300.2773 | -0.07 | 0.93 | -0.65 | 0.35 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 11:14 | 300.3789 | -0.1 | 0.9 | -0.62 | 0.38 | -0.67 | 0.33 | 70.31 | 29.3
2019-09-04 | 11:14 | 300.4805 | 0 | 1 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 30.27
2019-09-04 | 11:14 | 300.5781 | 0.05 | 1.05 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 11:14 | 300.6875 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 11:14 | 300.7891 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27

## 14.7mL s
|  |  | BoilerPressure |  | HEPressure |  | SCPressure
Date | Clock | Timer | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | HETemperature | SCTemperature
2019-09-04 | 13:10 | 1.0703 | 0.04 | 1.04 | -0.32 | 0.68 | -0.24 | 0.76 | 24.41 | 24.41 |  | Flow
2019-09-04 | 13:10 | 1.1797 | 0.03 | 1.03 | -0.31 | 0.69 | -0.25 | 0.75 | 23.44 | 25.39 |  | mL | seconds | flow
2019-09-04 | 13:10 | 1.2812 | -0.04 | 0.96 | -0.28 | 0.72 | -0.25 | 0.75 | 24.41 | 25.39 |  | 100 | 7 | 14.3 | start
2019-09-04 | 13:10 | 1.3789 | -0.02 | 0.98 | -0.28 | 0.72 | -0.24 | 0.76 | 24.41 | 25.39 |  | 100 | 6 | 16.7
2019-09-04 | 13:10 | 1.4805 | -0.05 | 0.95 | -0.26 | 0.74 | -0.23 | 0.77 | 24.41 | 24.41 |  | 100 | 7 | 14.3
2019-09-04 | 13:10 | 1.5898 | -0.06 | 0.94 | -0.26 | 0.74 | -0.22 | 0.78 | 24.41 | 24.41
2019-09-04 | 13:10 | 1.6914 | 0.04 | 1.04 | -0.29 | 0.71 | -0.23 | 0.77 | 24.41 | 25.39 |  | 100 | 7 | 14.3 | end
2019-09-04 | 13:10 | 1.7891 | 0.02 | 1.02 | -0.3 | 0.7 | -0.23 | 0.77 | 23.44 | 25.39 |  | 100 | 7 | 14.3
2019-09-04 | 13:10 | 1.8906 | 0.03 | 1.03 | -0.31 | 0.69 | -0.23 | 0.77 | 24.41 | 24.41 |  | 100 | 7 | 14.3
2019-09-04 | 13:10 | 2 | 0.04 | 1.04 | -0.31 | 0.69 | -0.25 | 0.75 | 24.41 | 24.41
2019-09-04 | 13:10 | 2.1016 | 0.04 | 1.04 | -0.3 | 0.7 | -0.25 | 0.75 | 24.41 | 25.39 |  |  |  | 14.7 | average
2019-09-04 | 13:10 | 2.1992 | 0.04 | 1.04 | -0.31 | 0.69 | -0.25 | 0.75 | 23.44 | 24.41
2019-09-04 | 13:10 | 2.3008 | 0.04 | 1.04 | -0.31 | 0.69 | -0.25 | 0.75 | 24.41 | 26.37
2019-09-04 | 13:10 | 2.4102 | 0.07 | 1.07 | -0.31 | 0.69 | -0.25 | 0.75 | 24.41 | 24.41
2019-09-04 | 13:10 | 2.5117 | 0.07 | 1.07 | -0.32 | 0.68 | -0.25 | 0.75 | 24.41 | 26.37
2019-09-04 | 13:10 | 2.6094 | 0.04 | 1.04 | -0.33 | 0.67 | -0.24 | 0.76 | 24.41 | 24.41
2019-09-04 | 13:10 | 2.7227 | -0.01 | 0.99 | -0.3 | 0.7 | -0.25 | 0.75 | 23.44 | 24.41
2019-09-04 | 13:10 | 2.8203 | -0.01 | 0.99 | -0.28 | 0.72 | -0.23 | 0.77 | 24.41 | 24.41
2019-09-04 | 13:10 | 2.9219 | -0.01 | 0.99 | -0.28 | 0.72 | -0.22 | 0.78 | 25.39 | 25.39
2019-09-04 | 13:10 | 3.0195 | -0.06 | 0.94 | -0.28 | 0.72 | -0.23 | 0.77 | 25.39 | 25.39
2019-09-04 | 13:10 | 3.1289 | -0.03 | 0.97 | -0.27 | 0.73 | -0.23 | 0.77 | 25.39 | 23.44
2019-09-04 | 13:10 | 3.2305 | 0.03 | 1.03 | -0.3 | 0.7 | -0.24 | 0.76 | 23.44 | 24.41
2019-09-04 | 13:10 | 3.332 | 0.04 | 1.04 | -0.3 | 0.7 | -0.23 | 0.77 | 23.44 | 25.39
2019-09-04 | 13:10 | 3.4297 | 0.04 | 1.04 | -0.3 | 0.7 | -0.23 | 0.77 | 24.41 | 25.39
2019-09-04 | 13:10 | 3.5391 | 0.04 | 1.04 | -0.32 | 0.68 | -0.24 | 0.76 | 24.41 | 25.39
2019-09-04 | 13:10 | 3.6406 | 0.03 | 1.03 | -0.3 | 0.7 | -0.23 | 0.77 | 24.41 | 25.39
2019-09-04 | 13:10 | 3.7422 | 0.04 | 1.04 | -0.31 | 0.69 | -0.25 | 0.75 | 24.41 | 25.39
2019-09-04 | 13:10 | 3.8516 | 0.06 | 1.06 | -0.31 | 0.69 | -0.24 | 0.76 | 24.41 | 25.39
2019-09-04 | 13:10 | 3.9492 | 0.03 | 1.03 | -0.33 | 0.67 | -0.24 | 0.76 | 25.39 | 26.37
2019-09-04 | 13:10 | 4.0508 | 0.02 | 1.02 | -0.33 | 0.67 | -0.25 | 0.75 | 24.41 | 24.41
2019-09-04 | 13:10 | 4.1523 | 0.04 | 1.04 | -0.31 | 0.69 | -0.26 | 0.74 | 23.44 | 25.39
2019-09-04 | 13:10 | 4.2617 | -0.02 | 0.98 | -0.29 | 0.71 | -0.23 | 0.77 | 23.44 | 25.39
2019-09-04 | 13:10 | 4.3594 | -0.03 | 0.97 | -0.27 | 0.73 | -0.24 | 0.76 | 23.44 | 24.41
2019-09-04 | 13:10 | 4.4727 | -0.03 | 0.97 | -0.26 | 0.74 | -0.22 | 0.78 | 25.39 | 27.34
2019-09-04 | 13:10 | 4.5703 | -0.02 | 0.98 | -0.27 | 0.73 | -0.23 | 0.77 | 24.41 | 26.37
2019-09-04 | 13:10 | 4.6719 | 0.02 | 1.02 | -0.29 | 0.71 | -0.21 | 0.79 | 24.41 | 25.39 |  | Take equilibrium pressures between 100 and 175 seconds
2019-09-04 | 13:10 | 4.7695 | 0.04 | 1.04 | -0.29 | 0.71 | -0.23 | 0.77 | 26.37 | 26.37
2019-09-04 | 13:10 | 4.8711 | 0.02 | 1.02 | -0.3 | 0.7 | -0.23 | 0.77 | 23.44 | 27.34 |  | minimum boiler pressure between 100 and 175 seconds is: | [6 empty] | 0.83 | average Pb |  | 1.0001
2019-09-04 | 13:10 | 4.9805 | 0.03 | 1.03 | -0.31 | 0.69 | -0.24 | 0.76 | 25.39 | 25.39 |  | maximum boiler pressure between 100 and 175 seconds is: | [6 empty] | 1.07
2019-09-04 | 13:10 | 5.082 | 0.03 | 1.03 | -0.31 | 0.69 | -0.23 | 0.77 | 24.41 | 26.37
2019-09-04 | 13:10 | 5.1797 | 0.05 | 1.05 | -0.3 | 0.7 | -0.24 | 0.76 | 23.44 | 27.34 |  | minimum heat exchanger pressure between 100 and 175 seconds is: | [6 empty] | 0.12 | average Phe |  | 0.17776
2019-09-04 | 13:10 | 5.2812 | 0.05 | 1.05 | -0.31 | 0.69 | -0.25 | 0.75 | 23.44 | 26.37 |  | maximum heat exchanger pressure between 100 and 175 seconds is: | [6 empty] | 0.32
2019-09-04 | 13:10 | 5.3906 | 0.03 | 1.03 | -0.32 | 0.68 | -0.25 | 0.75 | 24.41 | 27.34
2019-09-04 | 13:10 | 5.4922 | 0.04 | 1.04 | -0.31 | 0.69 | -0.25 | 0.75 | 24.41 | 26.37
2019-09-04 | 13:10 | 5.5898 | 0.04 | 1.04 | -0.32 | 0.68 | -0.25 | 0.75 | 26.37 | 28.32
2019-09-04 | 13:10 | 5.6992 | 0 | 1 | -0.29 | 0.71 | -0.24 | 0.76 | 24.41 | 27.34
2019-09-04 | 13:10 | 5.8008 | -0.03 | 0.97 | -0.27 | 0.73 | -0.25 | 0.75 | 24.41 | 28.32
2019-09-04 | 13:10 | 5.9023 | -0.02 | 0.98 | -0.28 | 0.72 | -0.24 | 0.76 | 23.44 | 26.37
2019-09-04 | 13:10 | 6.0117 | -0.02 | 0.98 | -0.27 | 0.73 | -0.23 | 0.77 | 25.39 | 27.34
2019-09-04 | 13:10 | 6.1094 | -0.01 | 0.99 | -0.26 | 0.74 | -0.22 | 0.78 | 24.41 | 26.37
2019-09-04 | 13:10 | 6.2109 | 0.02 | 1.02 | -0.31 | 0.69 | -0.24 | 0.76 | 24.41 | 28.32
2019-09-04 | 13:10 | 6.3125 | 0.04 | 1.04 | -0.3 | 0.7 | -0.25 | 0.75 | 24.41 | 27.34
2019-09-04 | 13:10 | 6.4102 | 0.04 | 1.04 | -0.32 | 0.68 | -0.24 | 0.76 | 23.44 | 29.3
2019-09-04 | 13:10 | 6.5195 | 0.03 | 1.03 | -0.3 | 0.7 | -0.26 | 0.74 | 25.39 | 29.3
2019-09-04 | 13:10 | 6.6211 | 0.04 | 1.04 | -0.33 | 0.67 | -0.25 | 0.75 | 24.41 | 29.3
2019-09-04 | 13:10 | 6.7227 | 0.05 | 1.05 | -0.34 | 0.66 | -0.26 | 0.74 | 24.41 | 28.32
2019-09-04 | 13:10 | 6.8203 | 0.04 | 1.04 | -0.33 | 0.67 | -0.27 | 0.73 | 24.41 | 27.34
2019-09-04 | 13:10 | 6.9297 | 0.04 | 1.04 | -0.36 | 0.64 | -0.29 | 0.71 | 25.39 | 29.3
2019-09-04 | 13:10 | 7.0312 | 0.04 | 1.04 | -0.36 | 0.64 | -0.29 | 0.71 | 26.37 | 29.3
2019-09-04 | 13:10 | 7.1289 | 0.05 | 1.05 | -0.37 | 0.63 | -0.3 | 0.7 | 27.34 | 28.32
2019-09-04 | 13:10 | 7.2422 | -0.01 | 0.99 | -0.31 | 0.69 | -0.28 | 0.72 | 28.32 | 29.3
2019-09-04 | 13:10 | 7.3398 | -0.02 | 0.98 | -0.32 | 0.68 | -0.29 | 0.71 | 30.27 | 31.25
2019-09-04 | 13:10 | 7.4414 | -0.03 | 0.97 | -0.32 | 0.68 | -0.3 | 0.7 | 32.23 | 31.25
2019-09-04 | 13:10 | 7.5508 | -0.04 | 0.96 | -0.34 | 0.66 | -0.3 | 0.7 | 34.18 | 30.27
2019-09-04 | 13:10 | 7.6523 | -0.01 | 0.99 | -0.36 | 0.64 | -0.3 | 0.7 | 35.16 | 28.32
2019-09-04 | 13:10 | 7.75 | 0.04 | 1.04 | -0.38 | 0.62 | -0.33 | 0.67 | 39.06 | 29.3
2019-09-04 | 13:10 | 7.8516 | 0.03 | 1.03 | -0.41 | 0.59 | -0.35 | 0.65 | 41.02 | 29.3
2019-09-04 | 13:10 | 7.9609 | 0.03 | 1.03 | -0.42 | 0.58 | -0.36 | 0.64 | 42.97 | 30.27
2019-09-04 | 13:10 | 8.0625 | 0.03 | 1.03 | -0.42 | 0.58 | -0.37 | 0.63 | 45.9 | 30.27
2019-09-04 | 13:10 | 8.1602 | 0.04 | 1.04 | -0.44 | 0.56 | -0.37 | 0.63 | 47.85 | 30.27
2019-09-04 | 13:10 | 8.2617 | 0.05 | 1.05 | -0.46 | 0.54 | -0.38 | 0.62 | 49.8 | 30.27
2019-09-04 | 13:10 | 8.3594 | 0.05 | 1.05 | -0.46 | 0.54 | -0.39 | 0.61 | 51.76 | 28.32
2019-09-04 | 13:10 | 8.4727 | 0.04 | 1.04 | -0.47 | 0.53 | -0.4 | 0.6 | 53.71 | 30.27
2019-09-04 | 13:10 | 8.5703 | 0.04 | 1.04 | -0.48 | 0.52 | -0.41 | 0.59 | 55.66 | 30.27
2019-09-04 | 13:10 | 8.6797 | 0.02 | 1.02 | -0.47 | 0.53 | -0.41 | 0.59 | 58.59 | 33.2
2019-09-04 | 13:10 | 8.7812 | -0.04 | 0.96 | -0.4 | 0.6 | -0.38 | 0.62 | 60.55 | 32.23 |  | temperature equilibrium from 125 seconds
2019-09-04 | 13:10 | 8.8789 | -0.04 | 0.96 | -0.39 | 0.61 | -0.38 | 0.62 | 60.55 | 31.25
2019-09-04 | 13:10 | 8.9805 | -0.05 | 0.95 | -0.39 | 0.61 | -0.37 | 0.63 | 61.52 | 31.25 |  | minimum heat exchanger outlet temperature is: |  |  |  |  | 69.34 |  | average SC bath temp |  | 26.7998
2019-09-04 | 13:10 | 9.0898 | -0.07 | 0.93 | -0.4 | 0.6 | -0.39 | 0.61 | 63.48 | 31.25 |  | maximum heat exchanger outlet temperature is: |  |  |  |  | 75.2
2019-09-04 | 13:10 | 9.1914 | 0.02 | 1.02 | -0.48 | 0.52 | -0.4 | 0.6 | 63.48 | 31.25
2019-09-04 | 13:10 | 9.2891 | 0.02 | 1.02 | -0.5 | 0.5 | -0.41 | 0.59 | 65.43 | 32.23 |  | average HE outlet temperature is: |  |  |  | 70.7671
2019-09-04 | 13:10 | 9.3906 | 0.03 | 1.03 | -0.49 | 0.51 | -0.43 | 0.57 | 65.43 | 31.25
2019-09-04 | 13:10 | 9.4922 | 0.04 | 1.04 | -0.5 | 0.5 | -0.44 | 0.56 | 65.43 | 32.23 |  | number of temperature points measured is: |  |  |  | 1714 |  | STDEV | 0.85568
2019-09-04 | 13:10 | 9.6016 | 0.04 | 1.04 | -0.51 | 0.49 | -0.44 | 0.56 | 66.41 | 34.18
2019-09-04 | 13:10 | 9.6992 | 0.04 | 1.04 | -0.52 | 0.48 | -0.45 | 0.55 | 67.38 | 33.2
2019-09-04 | 13:10 | 9.8125 | 0.05 | 1.05 | -0.51 | 0.49 | -0.45 | 0.55 | 67.38 | 33.2
2019-09-04 | 13:10 | 9.9102 | 0.04 | 1.04 | -0.53 | 0.47 | -0.46 | 0.54 | 67.38 | 32.23
2019-09-04 | 13:10 | 10.0117 | 0.05 | 1.05 | -0.54 | 0.46 | -0.47 | 0.53 | 66.41 | 34.18
2019-09-04 | 13:10 | 10.1094 | 0.04 | 1.04 | -0.53 | 0.47 | -0.47 | 0.53 | 66.41 | 32.23
2019-09-04 | 13:10 | 10.2227 | 0.01 | 1.01 | -0.5 | 0.5 | -0.45 | 0.55 | 66.41 | 33.2
2019-09-04 | 13:10 | 10.3203 | -0.03 | 0.97 | -0.45 | 0.55 | -0.46 | 0.54 | 67.38 | 33.2
2019-09-04 | 13:10 | 10.4219 | -0.06 | 0.94 | -0.42 | 0.58 | -0.44 | 0.56 | 66.41 | 33.2
2019-09-04 | 13:10 | 10.5195 | -0.07 | 0.93 | -0.43 | 0.57 | -0.42 | 0.58 | 66.41 | 33.2
2019-09-04 | 13:10 | 10.6289 | -0.08 | 0.92 | -0.43 | 0.57 | -0.43 | 0.57 | 65.43 | 31.25
2019-09-04 | 13:10 | 10.7305 | 0.03 | 1.03 | -0.52 | 0.48 | -0.46 | 0.54 | 65.43 | 32.23
2019-09-04 | 13:10 | 10.832 | 0.04 | 1.04 | -0.53 | 0.47 | -0.46 | 0.54 | 66.41 | 34.18
2019-09-04 | 13:10 | 10.9414 | 0.04 | 1.04 | -0.53 | 0.47 | -0.46 | 0.54 | 66.41 | 34.18
2019-09-04 | 13:10 | 11.0391 | 0.03 | 1.03 | -0.53 | 0.47 | -0.47 | 0.53 | 66.41 | 34.18
2019-09-04 | 13:10 | 11.1406 | 0.04 | 1.04 | -0.54 | 0.46 | -0.47 | 0.53 | 65.43 | 34.18
2019-09-04 | 13:10 | 11.2422 | 0.03 | 1.03 | -0.54 | 0.46 | -0.48 | 0.52 | 65.43 | 33.2
2019-09-04 | 13:10 | 11.3516 | 0.05 | 1.05 | -0.55 | 0.45 | -0.48 | 0.52 | 64.45 | 33.2
2019-09-04 | 13:10 | 11.4492 | 0.04 | 1.04 | -0.56 | 0.44 | -0.5 | 0.5 | 64.45 | 33.2
2019-09-04 | 13:10 | 11.5508 | 0.04 | 1.04 | -0.56 | 0.44 | -0.49 | 0.51 | 65.43 | 33.2
2019-09-04 | 13:10 | 11.6523 | 0.04 | 1.04 | -0.56 | 0.44 | -0.5 | 0.5 | 66.41 | 35.16
2019-09-04 | 13:10 | 11.7617 | -0.03 | 0.97 | -0.47 | 0.53 | -0.47 | 0.53 | 65.43 | 35.16
2019-09-04 | 13:10 | 11.8594 | -0.07 | 0.93 | -0.45 | 0.55 | -0.47 | 0.53 | 66.41 | 33.2
2019-09-04 | 13:10 | 11.9727 | -0.08 | 0.92 | -0.45 | 0.55 | -0.46 | 0.54 | 65.43 | 34.18
2019-09-04 | 13:10 | 12.0703 | -0.09 | 0.91 | -0.44 | 0.56 | -0.46 | 0.54 | 66.41 | 36.13
2019-09-04 | 13:10 | 12.1719 | 0.01 | 1.01 | -0.53 | 0.47 | -0.48 | 0.52 | 65.43 | 33.2
2019-09-04 | 13:10 | 12.2695 | 0.02 | 1.02 | -0.55 | 0.45 | -0.5 | 0.5 | 65.43 | 34.18
2019-09-04 | 13:10 | 12.3711 | 0.02 | 1.02 | -0.58 | 0.42 | -0.5 | 0.5 | 65.43 | 34.18
2019-09-04 | 13:10 | 12.4805 | 0.04 | 1.04 | -0.57 | 0.43 | -0.51 | 0.49 | 65.43 | 34.18
2019-09-04 | 13:10 | 12.582 | 0.04 | 1.04 | -0.57 | 0.43 | -0.51 | 0.49 | 64.45 | 36.13
2019-09-04 | 13:10 | 12.6797 | 0.04 | 1.04 | -0.57 | 0.43 | -0.51 | 0.49 | 65.43 | 34.18
2019-09-04 | 13:10 | 12.7812 | 0.04 | 1.04 | -0.57 | 0.43 | -0.51 | 0.49 | 65.43 | 36.13
2019-09-04 | 13:10 | 12.8906 | 0.04 | 1.04 | -0.57 | 0.43 | -0.5 | 0.5 | 65.43 | 32.23
2019-09-04 | 13:10 | 12.9922 | 0.05 | 1.05 | -0.57 | 0.43 | -0.52 | 0.48 | 65.43 | 36.13
2019-09-04 | 13:10 | 13.0898 | 0.05 | 1.05 | -0.58 | 0.42 | -0.52 | 0.48 | 64.45 | 34.18
2019-09-04 | 13:10 | 13.1914 | 0.04 | 1.04 | -0.59 | 0.41 | -0.52 | 0.48 | 66.41 | 35.16
2019-09-04 | 13:10 | 13.3008 | -0.01 | 0.99 | -0.49 | 0.51 | -0.49 | 0.51 | 65.43 | 35.16
2019-09-04 | 13:10 | 13.4023 | -0.07 | 0.93 | -0.47 | 0.53 | -0.5 | 0.5 | 67.38 | 37.11
2019-09-04 | 13:10 | 13.5117 | -0.09 | 0.91 | -0.46 | 0.54 | -0.49 | 0.51 | 65.43 | 35.16
2019-09-04 | 13:10 | 13.6094 | -0.08 | 0.92 | -0.46 | 0.54 | -0.49 | 0.51 | 67.38 | 36.13
2019-09-04 | 13:10 | 13.7109 | 0.01 | 1.01 | -0.58 | 0.42 | -0.51 | 0.49 | 67.38 | 35.16
2019-09-04 | 13:10 | 13.8125 | 0.04 | 1.04 | -0.59 | 0.41 | -0.51 | 0.49 | 67.38 | 36.13
2019-09-04 | 13:10 | 13.9219 | 0.03 | 1.03 | -0.58 | 0.42 | -0.53 | 0.47 | 65.43 | 34.18
2019-09-04 | 13:10 | 14.0195 | 0.06 | 1.06 | -0.59 | 0.41 | -0.53 | 0.47 | 65.43 | 36.13
2019-09-04 | 13:10 | 14.1211 | 0.03 | 1.03 | -0.6 | 0.4 | -0.53 | 0.47 | 66.41 | 36.13
2019-09-04 | 13:10 | 14.2227 | 0.04 | 1.04 | -0.6 | 0.4 | -0.53 | 0.47 | 66.41 | 35.16
2019-09-04 | 13:10 | 14.3203 | 0.06 | 1.06 | -0.61 | 0.39 | -0.54 | 0.46 | 65.43 | 35.16
2019-09-04 | 13:10 | 14.4297 | 0.04 | 1.04 | -0.62 | 0.38 | -0.55 | 0.45 | 66.41 | 33.2
2019-09-04 | 13:10 | 14.5312 | 0.04 | 1.04 | -0.61 | 0.39 | -0.54 | 0.46 | 66.41 | 35.16
2019-09-04 | 13:10 | 14.6406 | 0.04 | 1.04 | -0.62 | 0.38 | -0.55 | 0.45 | 65.43 | 36.13
2019-09-04 | 13:10 | 14.7422 | 0 | 1 | -0.58 | 0.42 | -0.54 | 0.46 | 67.38 | 36.13
2019-09-04 | 13:10 | 14.8398 | -0.07 | 0.93 | -0.49 | 0.51 | -0.53 | 0.47 | 65.43 | 35.16
2019-09-04 | 13:10 | 14.9414 | -0.1 | 0.9 | -0.48 | 0.52 | -0.53 | 0.47 | 66.41 | 36.13
2019-09-04 | 13:10 | 15.0508 | -0.11 | 0.89 | -0.49 | 0.51 | -0.52 | 0.48 | 67.38 | 36.13
2019-09-04 | 13:10 | 15.1523 | -0.02 | 0.98 | -0.54 | 0.46 | -0.53 | 0.47 | 67.38 | 35.16
2019-09-04 | 13:10 | 15.25 | 0.03 | 1.03 | -0.61 | 0.39 | -0.54 | 0.46 | 65.43 | 36.13
2019-09-04 | 13:10 | 15.3516 | 0.03 | 1.03 | -0.61 | 0.39 | -0.54 | 0.46 | 65.43 | 37.11
2019-09-04 | 13:10 | 15.4492 | 0.03 | 1.03 | -0.62 | 0.38 | -0.56 | 0.44 | 67.38 | 35.16
2019-09-04 | 13:10 | 15.5625 | 0.04 | 1.04 | -0.62 | 0.38 | -0.56 | 0.44 | 65.43 | 35.16
2019-09-04 | 13:10 | 15.6602 | 0.04 | 1.04 | -0.63 | 0.37 | -0.56 | 0.44 | 65.43 | 36.13
2019-09-04 | 13:10 | 15.7695 | 0.03 | 1.03 | -0.62 | 0.38 | -0.55 | 0.45 | 66.41 | 36.13
2019-09-04 | 13:10 | 15.8711 | 0.04 | 1.04 | -0.63 | 0.37 | -0.57 | 0.43 | 67.38 | 35.16
2019-09-04 | 13:10 | 15.9727 | 0.04 | 1.04 | -0.63 | 0.37 | -0.56 | 0.44 | 67.38 | 34.18
2019-09-04 | 13:10 | 16.082 | 0.04 | 1.04 | -0.64 | 0.36 | -0.56 | 0.44 | 66.41 | 35.16
2019-09-04 | 13:10 | 16.1797 | 0.04 | 1.04 | -0.64 | 0.36 | -0.58 | 0.42 | 67.38 | 36.13
2019-09-04 | 13:10 | 16.2812 | -0.02 | 0.98 | -0.54 | 0.46 | -0.56 | 0.44 | 66.41 | 35.16
2019-09-04 | 13:10 | 16.3789 | -0.07 | 0.93 | -0.53 | 0.47 | -0.55 | 0.45 | 65.43 | 34.18
2019-09-04 | 13:10 | 16.4805 | -0.11 | 0.89 | -0.49 | 0.51 | -0.55 | 0.45 | 65.43 | 37.11
2019-09-04 | 13:10 | 16.5898 | -0.13 | 0.87 | -0.49 | 0.51 | -0.55 | 0.45 | 67.38 | 37.11
2019-09-04 | 13:10 | 16.6914 | 0.01 | 1.01 | -0.62 | 0.38 | -0.56 | 0.44 | 66.41 | 35.16
2019-09-04 | 13:10 | 16.7891 | 0.04 | 1.04 | -0.63 | 0.37 | -0.58 | 0.42 | 65.43 | 36.13
2019-09-04 | 13:10 | 16.9023 | 0.04 | 1.04 | -0.64 | 0.36 | -0.57 | 0.43 | 66.41 | 36.13
2019-09-04 | 13:10 | 17 | 0.03 | 1.03 | -0.64 | 0.36 | -0.58 | 0.42 | 65.43 | 37.11
2019-09-04 | 13:10 | 17.1016 | 0.04 | 1.04 | -0.64 | 0.36 | -0.57 | 0.43 | 65.43 | 37.11
2019-09-04 | 13:10 | 17.1992 | 0.01 | 1.01 | -0.65 | 0.35 | -0.58 | 0.42 | 66.41 | 37.11
2019-09-04 | 13:10 | 17.3125 | 0.04 | 1.04 | -0.66 | 0.34 | -0.59 | 0.41 | 65.43 | 36.13
2019-09-04 | 13:10 | 17.4102 | 0.04 | 1.04 | -0.66 | 0.34 | -0.6 | 0.4 | 65.43 | 34.18
2019-09-04 | 13:10 | 17.5117 | 0.04 | 1.04 | -0.66 | 0.34 | -0.58 | 0.42 | 67.38 | 35.16
2019-09-04 | 13:10 | 17.6094 | 0.04 | 1.04 | -0.66 | 0.34 | -0.59 | 0.41 | 66.41 | 37.11
2019-09-04 | 13:10 | 17.7227 | 0.04 | 1.04 | -0.65 | 0.35 | -0.59 | 0.41 | 66.41 | 36.13
2019-09-04 | 13:10 | 17.8203 | -0.07 | 0.93 | -0.54 | 0.46 | -0.58 | 0.42 | 67.38 | 38.09
2019-09-04 | 13:10 | 17.9219 | -0.11 | 0.89 | -0.52 | 0.48 | -0.56 | 0.44 | 68.36 | 37.11
2019-09-04 | 13:10 | 18.0312 | -0.11 | 0.89 | -0.5 | 0.5 | -0.56 | 0.44 | 66.41 | 36.13
2019-09-04 | 13:10 | 18.1289 | -0.11 | 0.89 | -0.5 | 0.5 | -0.54 | 0.46 | 66.41 | 35.16
2019-09-04 | 13:10 | 18.2305 | 0.03 | 1.03 | -0.64 | 0.36 | -0.58 | 0.42 | 67.38 | 36.13
2019-09-04 | 13:10 | 18.3398 | 0 | 1 | -0.65 | 0.35 | -0.59 | 0.41 | 66.41 | 37.11
2019-09-04 | 13:10 | 18.4414 | 0.03 | 1.03 | -0.66 | 0.34 | -0.59 | 0.41 | 65.43 | 36.13
2019-09-04 | 13:10 | 18.5391 | 0.04 | 1.04 | -0.67 | 0.33 | -0.59 | 0.41 | 67.38 | 38.09
2019-09-04 | 13:10 | 18.6406 | 0.03 | 1.03 | -0.66 | 0.34 | -0.59 | 0.41 | 66.41 | 36.13
2019-09-04 | 13:10 | 18.75 | 0.04 | 1.04 | -0.66 | 0.34 | -0.6 | 0.4 | 68.36 | 37.11
2019-09-04 | 13:10 | 18.8516 | 0.04 | 1.04 | -0.65 | 0.35 | -0.6 | 0.4 | 65.43 | 36.13
2019-09-04 | 13:10 | 18.9492 | 0.04 | 1.04 | -0.67 | 0.33 | -0.6 | 0.4 | 65.43 | 34.18
2019-09-04 | 13:10 | 19.0508 | 0.04 | 1.04 | -0.67 | 0.33 | -0.6 | 0.4 | 66.41 | 36.13
2019-09-04 | 13:10 | 19.1523 | 0.04 | 1.04 | -0.68 | 0.32 | -0.59 | 0.41 | 65.43 | 37.11
2019-09-04 | 13:10 | 19.2617 | -0.01 | 0.99 | -0.61 | 0.39 | -0.58 | 0.42 | 65.43 | 36.13
2019-09-04 | 13:10 | 19.3594 | -0.07 | 0.93 | -0.55 | 0.45 | -0.57 | 0.43 | 66.41 | 36.13
2019-09-04 | 13:10 | 19.4609 | -0.08 | 0.92 | -0.52 | 0.48 | -0.57 | 0.43 | 66.41 | 37.11
2019-09-04 | 13:10 | 19.5703 | -0.1 | 0.9 | -0.52 | 0.48 | -0.55 | 0.45 | 65.43 | 35.16
2019-09-04 | 13:10 | 19.6719 | 0 | 1 | -0.61 | 0.39 | -0.56 | 0.44 | 67.38 | 35.16
2019-09-04 | 13:10 | 19.7695 | 0.02 | 1.02 | -0.64 | 0.36 | -0.59 | 0.41 | 66.41 | 36.13
2019-09-04 | 13:10 | 19.8711 | 0.03 | 1.03 | -0.66 | 0.34 | -0.58 | 0.42 | 65.43 | 35.16
2019-09-04 | 13:10 | 19.9805 | 0.02 | 1.02 | -0.65 | 0.35 | -0.58 | 0.42 | 66.41 | 36.13
2019-09-04 | 13:10 | 20.082 | 0.04 | 1.04 | -0.65 | 0.35 | -0.59 | 0.41 | 66.41 | 36.13
2019-09-04 | 13:10 | 20.1797 | 0.04 | 1.04 | -0.66 | 0.34 | -0.59 | 0.41 | 65.43 | 35.16
2019-09-04 | 13:10 | 20.2812 | 0.04 | 1.04 | -0.67 | 0.33 | -0.59 | 0.41 | 65.43 | 35.16
2019-09-04 | 13:10 | 20.3906 | 0.04 | 1.04 | -0.67 | 0.33 | -0.6 | 0.4 | 67.38 | 33.2
2019-09-04 | 13:10 | 20.4922 | 0.04 | 1.04 | -0.67 | 0.33 | -0.6 | 0.4 | 65.43 | 34.18
2019-09-04 | 13:10 | 20.6016 | 0.05 | 1.05 | -0.66 | 0.34 | -0.59 | 0.41 | 66.41 | 36.13
2019-09-04 | 13:10 | 20.6992 | 0.04 | 1.04 | -0.66 | 0.34 | -0.61 | 0.39 | 66.41 | 36.13
2019-09-04 | 13:10 | 20.8008 | -0.05 | 0.95 | -0.56 | 0.44 | -0.59 | 0.41 | 65.43 | 34.18
2019-09-04 | 13:10 | 20.9023 | -0.09 | 0.91 | -0.52 | 0.48 | -0.58 | 0.42 | 67.38 | 35.16
2019-09-04 | 13:10 | 21.0117 | -0.09 | 0.91 | -0.53 | 0.47 | -0.56 | 0.44 | 65.43 | 35.16
2019-09-04 | 13:10 | 21.1094 | -0.12 | 0.88 | -0.51 | 0.49 | -0.57 | 0.43 | 65.43 | 37.11
2019-09-04 | 13:10 | 21.2109 | 0.01 | 1.01 | -0.65 | 0.35 | -0.61 | 0.39 | 66.41 | 33.2
2019-09-04 | 13:10 | 21.3125 | 0.03 | 1.03 | -0.65 | 0.35 | -0.61 | 0.39 | 64.45 | 36.13
2019-09-04 | 13:10 | 21.4102 | 0.04 | 1.04 | -0.68 | 0.32 | -0.61 | 0.39 | 64.45 | 34.18
2019-09-04 | 13:10 | 21.5195 | 0.02 | 1.02 | -0.68 | 0.32 | -0.61 | 0.39 | 65.43 | 34.18
2019-09-04 | 13:10 | 21.6211 | 0.04 | 1.04 | -0.67 | 0.33 | -0.62 | 0.38 | 66.41 | 36.13
2019-09-04 | 13:10 | 21.7305 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 65.43 | 36.13
2019-09-04 | 13:10 | 21.832 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 66.41 | 35.16
2019-09-04 | 13:10 | 21.9297 | 0.05 | 1.05 | -0.69 | 0.31 | -0.62 | 0.38 | 66.41 | 33.2
2019-09-04 | 13:10 | 22.0312 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 65.43 | 33.2
2019-09-04 | 13:10 | 22.1406 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 65.43 | 34.18
2019-09-04 | 13:10 | 22.2422 | 0.04 | 1.04 | -0.66 | 0.34 | -0.64 | 0.36 | 64.45 | 34.18
2019-09-04 | 13:10 | 22.3398 | -0.07 | 0.93 | -0.58 | 0.42 | -0.62 | 0.38 | 64.45 | 34.18
2019-09-04 | 13:10 | 22.4414 | -0.1 | 0.9 | -0.55 | 0.45 | -0.61 | 0.39 | 65.43 | 35.16
2019-09-04 | 13:10 | 22.5508 | -0.12 | 0.88 | -0.54 | 0.46 | -0.61 | 0.39 | 66.41 | 34.18
2019-09-04 | 13:10 | 22.6523 | -0.07 | 0.93 | -0.58 | 0.42 | -0.59 | 0.41 | 64.45 | 33.2
2019-09-04 | 13:10 | 22.75 | 0.02 | 1.02 | -0.67 | 0.33 | -0.63 | 0.37 | 64.45 | 33.2
2019-09-04 | 13:10 | 22.8594 | 0.02 | 1.02 | -0.7 | 0.3 | -0.63 | 0.37 | 64.45 | 34.18
2019-09-04 | 13:10 | 22.9609 | 0.02 | 1.02 | -0.69 | 0.31 | -0.63 | 0.37 | 65.43 | 35.16
2019-09-04 | 13:10 | 23.0625 | 0.03 | 1.03 | -0.7 | 0.3 | -0.63 | 0.37 | 66.41 | 35.16
2019-09-04 | 13:10 | 23.1602 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 65.43 | 34.18
2019-09-04 | 13:10 | 23.2695 | 0.05 | 1.05 | -0.7 | 0.3 | -0.63 | 0.37 | 65.43 | 34.18
2019-09-04 | 13:10 | 23.3711 | 0.04 | 1.04 | -0.7 | 0.3 | -0.63 | 0.37 | 65.43 | 33.2
2019-09-04 | 13:10 | 23.4727 | 0.03 | 1.03 | -0.71 | 0.29 | -0.64 | 0.36 | 66.41 | 33.2
2019-09-04 | 13:10 | 23.5703 | 0.04 | 1.04 | -0.7 | 0.3 | -0.64 | 0.36 | 65.43 | 34.18
2019-09-04 | 13:10 | 23.6797 | 0.04 | 1.04 | -0.7 | 0.3 | -0.63 | 0.37 | 66.41 | 35.16
2019-09-04 | 13:10 | 23.7812 | -0.01 | 0.99 | -0.62 | 0.38 | -0.61 | 0.39 | 66.41 | 34.18
2019-09-04 | 13:10 | 23.8789 | -0.07 | 0.93 | -0.56 | 0.44 | -0.6 | 0.4 | 66.41 | 35.16
2019-09-04 | 13:10 | 23.9922 | -0.11 | 0.89 | -0.54 | 0.46 | -0.59 | 0.41 | 65.43 | 33.2
2019-09-04 | 13:10 | 24.0898 | -0.13 | 0.87 | -0.54 | 0.46 | -0.58 | 0.42 | 65.43 | 34.18
2019-09-04 | 13:10 | 24.1914 | 0.01 | 1.01 | -0.65 | 0.35 | -0.6 | 0.4 | 65.43 | 32.23
2019-09-04 | 13:10 | 24.2891 | 0.03 | 1.03 | -0.67 | 0.33 | -0.61 | 0.39 | 65.43 | 34.18
2019-09-04 | 13:10 | 24.4023 | 0.03 | 1.03 | -0.67 | 0.33 | -0.61 | 0.39 | 66.41 | 34.18
2019-09-04 | 13:10 | 24.5 | 0.03 | 1.03 | -0.66 | 0.34 | -0.61 | 0.39 | 66.41 | 33.2
2019-09-04 | 13:10 | 24.6016 | 0.03 | 1.03 | -0.66 | 0.34 | -0.61 | 0.39 | 65.43 | 33.2
2019-09-04 | 13:10 | 24.6992 | 0.03 | 1.03 | -0.67 | 0.33 | -0.6 | 0.4 | 65.43 | 32.23
2019-09-04 | 13:10 | 24.8125 | 0.05 | 1.05 | -0.68 | 0.32 | -0.61 | 0.39 | 65.43 | 34.18
2019-09-04 | 13:10 | 24.9102 | 0.04 | 1.04 | -0.67 | 0.33 | -0.61 | 0.39 | 66.41 | 32.23
2019-09-04 | 13:10 | 25.0117 | 0.04 | 1.04 | -0.67 | 0.33 | -0.6 | 0.4 | 65.43 | 32.23
2019-09-04 | 13:10 | 25.1094 | 0.05 | 1.05 | -0.68 | 0.32 | -0.59 | 0.41 | 65.43 | 32.23
2019-09-04 | 13:10 | 25.2227 | 0.04 | 1.04 | -0.67 | 0.33 | -0.61 | 0.39 | 64.45 | 33.2
2019-09-04 | 13:10 | 25.3203 | -0.06 | 0.94 | -0.57 | 0.43 | -0.6 | 0.4 | 65.43 | 32.23
2019-09-04 | 13:10 | 25.4219 | -0.1 | 0.9 | -0.55 | 0.45 | -0.57 | 0.43 | 65.43 | 33.2
2019-09-04 | 13:10 | 25.5312 | -0.11 | 0.89 | -0.53 | 0.47 | -0.57 | 0.43 | 65.43 | 33.2
2019-09-04 | 13:10 | 25.6289 | -0.13 | 0.87 | -0.52 | 0.48 | -0.57 | 0.43 | 65.43 | 34.18
2019-09-04 | 13:10 | 25.7305 | 0 | 1 | -0.67 | 0.33 | -0.61 | 0.39 | 66.41 | 31.25
2019-09-04 | 13:10 | 25.832 | 0.03 | 1.03 | -0.68 | 0.32 | -0.62 | 0.38 | 65.43 | 32.23
2019-09-04 | 13:10 | 25.9414 | 0.02 | 1.02 | -0.69 | 0.31 | -0.63 | 0.37 | 65.43 | 31.25
2019-09-04 | 13:10 | 26.0391 | 0.04 | 1.04 | -0.7 | 0.3 | -0.62 | 0.38 | 65.43 | 31.25
2019-09-04 | 13:10 | 26.1406 | 0.04 | 1.04 | -0.71 | 0.29 | -0.64 | 0.36 | 66.41 | 32.23
2019-09-04 | 13:10 | 26.2422 | 0.04 | 1.04 | -0.7 | 0.3 | -0.65 | 0.35 | 65.43 | 32.23
2019-09-04 | 13:10 | 26.3516 | 0.04 | 1.04 | -0.71 | 0.29 | -0.65 | 0.35 | 65.43 | 32.23
2019-09-04 | 13:10 | 26.4492 | 0.04 | 1.04 | -0.73 | 0.27 | -0.67 | 0.33 | 65.43 | 31.25
2019-09-04 | 13:10 | 26.5625 | 0.04 | 1.04 | -0.72 | 0.28 | -0.67 | 0.33 | 65.43 | 31.25
2019-09-04 | 13:10 | 26.6602 | 0.04 | 1.04 | -0.72 | 0.28 | -0.66 | 0.34 | 65.43 | 32.23
2019-09-04 | 13:10 | 26.7617 | 0.04 | 1.04 | -0.71 | 0.29 | -0.66 | 0.34 | 66.41 | 32.23
2019-09-04 | 13:10 | 26.8594 | -0.07 | 0.93 | -0.6 | 0.4 | -0.64 | 0.36 | 65.43 | 32.23
2019-09-04 | 13:10 | 26.9727 | -0.07 | 0.93 | -0.58 | 0.42 | -0.63 | 0.37 | 65.43 | 33.2
2019-09-04 | 13:10 | 27.0703 | -0.11 | 0.89 | -0.56 | 0.44 | -0.63 | 0.37 | 66.41 | 33.2
2019-09-04 | 13:10 | 27.1719 | -0.01 | 0.99 | -0.67 | 0.33 | -0.63 | 0.37 | 66.41 | 30.27
2019-09-04 | 13:10 | 27.2695 | 0.02 | 1.02 | -0.71 | 0.29 | -0.64 | 0.36 | 68.36 | 32.23
2019-09-04 | 13:10 | 27.3789 | 0.04 | 1.04 | -0.71 | 0.29 | -0.65 | 0.35 | 66.41 | 34.18
2019-09-04 | 13:10 | 27.4805 | 0.03 | 1.03 | -0.72 | 0.28 | -0.65 | 0.35 | 68.36 | 33.2
2019-09-04 | 13:10 | 27.582 | 0.04 | 1.04 | -0.73 | 0.27 | -0.66 | 0.34 | 67.38 | 33.2
2019-09-04 | 13:10 | 27.6914 | 0.05 | 1.05 | -0.72 | 0.28 | -0.66 | 0.34 | 68.36 | 32.23
2019-09-04 | 13:10 | 27.7891 | 0.04 | 1.04 | -0.72 | 0.28 | -0.66 | 0.34 | 68.36 | 34.18
2019-09-04 | 13:10 | 27.8906 | 0.03 | 1.03 | -0.75 | 0.25 | -0.67 | 0.33 | 66.41 | 29.3
2019-09-04 | 13:10 | 27.9922 | 0.04 | 1.04 | -0.74 | 0.26 | -0.68 | 0.32 | 68.36 | 31.25
2019-09-04 | 13:10 | 28.1016 | 0.04 | 1.04 | -0.72 | 0.28 | -0.67 | 0.33 | 67.38 | 31.25
2019-09-04 | 13:10 | 28.1992 | 0.05 | 1.05 | -0.75 | 0.25 | -0.67 | 0.33 | 67.38 | 33.2
2019-09-04 | 13:10 | 28.3008 | 0 | 1 | -0.69 | 0.31 | -0.68 | 0.32 | 67.38 | 31.25
2019-09-04 | 13:10 | 28.4023 | -0.08 | 0.92 | -0.61 | 0.39 | -0.66 | 0.34 | 68.36 | 32.23
2019-09-04 | 13:10 | 28.5117 | -0.12 | 0.88 | -0.56 | 0.44 | -0.64 | 0.36 | 68.36 | 31.25
2019-09-04 | 13:10 | 28.6094 | -0.11 | 0.89 | -0.56 | 0.44 | -0.65 | 0.35 | 67.38 | 31.25
2019-09-04 | 13:10 | 28.7109 | 0.02 | 1.02 | -0.71 | 0.29 | -0.64 | 0.36 | 67.38 | 31.25
2019-09-04 | 13:10 | 28.8203 | 0.02 | 1.02 | -0.72 | 0.28 | -0.65 | 0.35 | 69.34 | 31.25
2019-09-04 | 13:10 | 28.9219 | 0.04 | 1.04 | -0.73 | 0.27 | -0.66 | 0.34 | 67.38 | 31.25
2019-09-04 | 13:10 | 29.0195 | 0.03 | 1.03 | -0.73 | 0.27 | -0.67 | 0.33 | 68.36 | 32.23
2019-09-04 | 13:10 | 29.1211 | 0.04 | 1.04 | -0.74 | 0.26 | -0.67 | 0.33 | 70.31 | 31.25
2019-09-04 | 13:10 | 29.2305 | 0.03 | 1.03 | -0.74 | 0.26 | -0.67 | 0.33 | 70.31 | 32.23
2019-09-04 | 13:10 | 29.332 | 0.05 | 1.05 | -0.73 | 0.27 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 13:10 | 29.4297 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 13:10 | 29.5312 | 0.04 | 1.04 | -0.75 | 0.25 | -0.67 | 0.33 | 68.36 | 30.27
2019-09-04 | 13:10 | 29.6406 | 0.05 | 1.05 | -0.74 | 0.26 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 13:10 | 29.7422 | 0.07 | 1.07 | -0.75 | 0.25 | -0.68 | 0.32 | 69.34 | 32.23
2019-09-04 | 13:10 | 29.8516 | -0.06 | 0.94 | -0.63 | 0.37 | -0.66 | 0.34 | 69.34 | 32.23
2019-09-04 | 13:10 | 29.9492 | -0.11 | 0.89 | -0.59 | 0.41 | -0.65 | 0.35 | 70.31 | 31.25
2019-09-04 | 13:10 | 30.0508 | -0.12 | 0.88 | -0.58 | 0.42 | -0.65 | 0.35 | 69.34 | 32.23
2019-09-04 | 13:10 | 30.1523 | -0.14 | 0.86 | -0.56 | 0.44 | -0.64 | 0.36 | 70.31 | 29.3
2019-09-04 | 13:10 | 30.25 | 0.02 | 1.02 | -0.73 | 0.27 | -0.65 | 0.35 | 69.34 | 31.25
2019-09-04 | 13:10 | 30.3594 | 0.03 | 1.03 | -0.74 | 0.26 | -0.66 | 0.34 | 69.34 | 33.2
2019-09-04 | 13:10 | 30.4609 | 0.04 | 1.04 | -0.74 | 0.26 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 13:10 | 30.5625 | 0.04 | 1.04 | -0.74 | 0.26 | -0.67 | 0.33 | 69.34 | 31.25
2019-09-04 | 13:10 | 30.6602 | 0.05 | 1.05 | -0.74 | 0.26 | -0.67 | 0.33 | 69.34 | 32.23
2019-09-04 | 13:10 | 30.7695 | 0.04 | 1.04 | -0.75 | 0.25 | -0.67 | 0.33 | 68.36 | 31.25
2019-09-04 | 13:10 | 30.8711 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 13:10 | 30.9727 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 13:10 | 31.0703 | 0.07 | 1.07 | -0.75 | 0.25 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 13:10 | 31.1797 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 13:10 | 31.2812 | 0.02 | 1.02 | -0.71 | 0.29 | -0.68 | 0.32 | 68.36 | 31.25
2019-09-04 | 13:10 | 31.3906 | -0.08 | 0.92 | -0.64 | 0.36 | -0.65 | 0.35 | 69.34 | 32.23
2019-09-04 | 13:10 | 31.4922 | -0.13 | 0.87 | -0.58 | 0.42 | -0.66 | 0.34 | 70.31 | 31.25
2019-09-04 | 13:10 | 31.5898 | -0.13 | 0.87 | -0.59 | 0.41 | -0.65 | 0.35 | 69.34 | 29.3
2019-09-04 | 13:10 | 31.6914 | 0 | 1 | -0.71 | 0.29 | -0.66 | 0.34 | 68.36 | 31.25
2019-09-04 | 13:10 | 31.7891 | 0.04 | 1.04 | -0.72 | 0.28 | -0.67 | 0.33 | 68.36 | 31.25
2019-09-04 | 13:10 | 31.9023 | 0.02 | 1.02 | -0.72 | 0.28 | -0.66 | 0.34 | 69.34 | 32.23
2019-09-04 | 13:10 | 32 | 0.04 | 1.04 | -0.73 | 0.27 | -0.68 | 0.32 | 68.36 | 32.23
2019-09-04 | 13:10 | 32.1016 | 0.04 | 1.04 | -0.74 | 0.26 | -0.69 | 0.31 | 68.36 | 31.25
2019-09-04 | 13:10 | 32.1992 | 0.03 | 1.03 | -0.73 | 0.27 | -0.68 | 0.32 | 69.34 | 31.25
2019-09-04 | 13:10 | 32.3125 | 0.04 | 1.04 | -0.73 | 0.27 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 13:10 | 32.4102 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 13:10 | 32.5195 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 69.34 | 32.23
2019-09-04 | 13:10 | 32.6211 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 13:10 | 32.7227 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 68.36 | 30.27
2019-09-04 | 13:10 | 32.8203 | -0.03 | 0.97 | -0.7 | 0.3 | -0.68 | 0.32 | 68.36 | 31.25
2019-09-04 | 13:10 | 32.9297 | -0.09 | 0.91 | -0.62 | 0.38 | -0.68 | 0.32 | 70.31 | 31.25
2019-09-04 | 13:10 | 33.0312 | -0.13 | 0.87 | -0.59 | 0.41 | -0.67 | 0.33 | 68.36 | 30.27
2019-09-04 | 13:10 | 33.1289 | -0.15 | 0.85 | -0.57 | 0.43 | -0.65 | 0.35 | 68.36 | 31.25
2019-09-04 | 13:10 | 33.2305 | 0.03 | 1.03 | -0.72 | 0.28 | -0.68 | 0.32 | 68.36 | 30.27
2019-09-04 | 13:10 | 33.332 | 0.04 | 1.04 | -0.74 | 0.26 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 13:10 | 33.4414 | 0.04 | 1.04 | -0.74 | 0.26 | -0.69 | 0.31 | 68.36 | 31.25
2019-09-04 | 13:10 | 33.5391 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 68.36 | 31.25
2019-09-04 | 13:10 | 33.6523 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 13:10 | 33.75 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 69.34 | 31.25
2019-09-04 | 13:10 | 33.8516 | 0.04 | 1.04 | -0.76 | 0.24 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 13:10 | 33.9609 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 13:10 | 34.0625 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 13:10 | 34.1602 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 13:10 | 34.2617 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 13:10 | 34.3594 | -0.07 | 0.93 | -0.66 | 0.34 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 13:10 | 34.4727 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 68.36 | 32.23
2019-09-04 | 13:10 | 34.5703 | -0.12 | 0.88 | -0.59 | 0.41 | -0.67 | 0.33 | 69.34 | 28.32
2019-09-04 | 13:10 | 34.6719 | -0.01 | 0.99 | -0.7 | 0.3 | -0.67 | 0.33 | 68.36 | 31.25
2019-09-04 | 13:10 | 34.7812 | -0.01 | 0.99 | -0.75 | 0.25 | -0.68 | 0.32 | 68.36 | 30.27
2019-09-04 | 13:10 | 34.8789 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 69.34 | 30.27
2019-09-04 | 13:10 | 34.9805 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 68.36 | 31.25
2019-09-04 | 13:10 | 35.082 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 31.25
2019-09-04 | 13:10 | 35.1914 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 13:10 | 35.2891 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 13:10 | 35.3906 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 35.4922 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 68.36 | 30.27
2019-09-04 | 13:10 | 35.6016 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 13:10 | 35.6992 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 13:10 | 35.8008 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 13:10 | 35.9102 | -0.07 | 0.93 | -0.66 | 0.34 | -0.68 | 0.32 | 68.36 | 34.18
2019-09-04 | 13:10 | 36.0117 | -0.1 | 0.9 | -0.62 | 0.38 | -0.68 | 0.32 | 68.36 | 31.25
2019-09-04 | 13:10 | 36.1094 | -0.14 | 0.86 | -0.59 | 0.41 | -0.66 | 0.34 | 69.34 | 29.3
2019-09-04 | 13:10 | 36.2109 | 0 | 1 | -0.73 | 0.27 | -0.67 | 0.33 | 68.36 | 30.27
2019-09-04 | 13:10 | 36.3203 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 13:10 | 36.4219 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 68.36 | 29.3
2019-09-04 | 13:10 | 36.5195 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 36.6211 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 13:10 | 36.7305 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 13:10 | 36.832 | 0.05 | 1.05 | -0.76 | 0.24 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 36.9297 | 0.03 | 1.03 | -0.77 | 0.23 | -0.71 | 0.29 | 67.38 | 29.3
2019-09-04 | 13:10 | 37.0312 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 70.31 | 30.27
2019-09-04 | 13:10 | 37.1406 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 13:10 | 37.2422 | 0.05 | 1.05 | -0.79 | 0.21 | -0.73 | 0.27 | 68.36 | 30.27
2019-09-04 | 13:10 | 37.3398 | 0.02 | 1.02 | -0.72 | 0.28 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 13:10 | 37.4492 | -0.07 | 0.93 | -0.66 | 0.34 | -0.7 | 0.3 | 70.31 | 31.25
2019-09-04 | 13:10 | 37.5508 | -0.1 | 0.9 | -0.61 | 0.39 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 37.6523 | -0.13 | 0.87 | -0.59 | 0.41 | -0.68 | 0.32 | 69.34 | 30.27
2019-09-04 | 13:10 | 37.75 | 0.01 | 1.01 | -0.75 | 0.25 | -0.69 | 0.31 | 68.36 | 31.25
2019-09-04 | 13:10 | 37.8594 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 68.36 | 29.3
2019-09-04 | 13:10 | 37.9609 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 38.0625 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 69.34 | 29.3
2019-09-04 | 13:10 | 38.1602 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 69.34 | 31.25
2019-09-04 | 13:10 | 38.2695 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 13:10 | 38.3711 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 13:10 | 38.4805 | 0.03 | 1.03 | -0.78 | 0.22 | -0.72 | 0.28 | 69.34 | 30.27
2019-09-04 | 13:10 | 38.582 | 0.04 | 1.04 | -0.78 | 0.22 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 38.6797 | 0.06 | 1.06 | -0.78 | 0.22 | -0.73 | 0.27 | 68.36 | 29.3
2019-09-04 | 13:10 | 38.7812 | 0.03 | 1.03 | -0.78 | 0.22 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 38.8906 | -0.07 | 0.93 | -0.66 | 0.34 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 13:10 | 38.9922 | -0.1 | 0.9 | -0.62 | 0.38 | -0.7 | 0.3 | 68.36 | 30.27
2019-09-04 | 13:10 | 39.0898 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 67.38 | 28.32
2019-09-04 | 13:10 | 39.1914 | 0 | 1 | -0.73 | 0.27 | -0.69 | 0.31 | 68.36 | 31.25
2019-09-04 | 13:10 | 39.2891 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:10 | 39.4023 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 39.5 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 39.6094 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 13:10 | 39.7109 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 39.8125 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 13:10 | 39.9102 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 67.38 | 30.27
2019-09-04 | 13:10 | 40.0195 | 0.07 | 1.07 | -0.79 | 0.21 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 40.1211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 40.2227 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 40.3203 | 0 | 1 | -0.73 | 0.27 | -0.71 | 0.29 | 67.38 | 29.3
2019-09-04 | 13:10 | 40.4336 | -0.05 | 0.95 | -0.66 | 0.34 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 13:10 | 40.5312 | -0.12 | 0.88 | -0.64 | 0.36 | -0.68 | 0.32 | 67.38 | 27.34
2019-09-04 | 13:10 | 40.6328 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 70.31 | 29.3
2019-09-04 | 13:10 | 40.7422 | 0 | 1 | -0.75 | 0.25 | -0.71 | 0.29 | 68.36 | 30.27
2019-09-04 | 13:10 | 40.8438 | 0.02 | 1.02 | -0.76 | 0.24 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 40.9414 | 0.01 | 1.01 | -0.79 | 0.21 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 13:10 | 41.043 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 41.1523 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 13:10 | 41.25 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 27.34
2019-09-04 | 13:10 | 41.3516 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 67.38 | 28.32
2019-09-04 | 13:10 | 41.4531 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 29.3
2019-09-04 | 13:10 | 41.5625 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 67.38 | 30.27
2019-09-04 | 13:10 | 41.6602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.73 | 0.27 | 68.36 | 28.32
2019-09-04 | 13:10 | 41.7617 | 0.04 | 1.04 | -0.78 | 0.22 | -0.73 | 0.27 | 68.36 | 29.3
2019-09-04 | 13:10 | 41.8711 | -0.03 | 0.97 | -0.69 | 0.31 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 13:10 | 41.9727 | -0.12 | 0.88 | -0.63 | 0.37 | -0.7 | 0.3 | 67.38 | 29.3
2019-09-04 | 13:10 | 42.0703 | -0.15 | 0.85 | -0.61 | 0.39 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 13:10 | 42.1719 | -0.04 | 0.96 | -0.68 | 0.32 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 13:10 | 42.2812 | 0.01 | 1.01 | -0.76 | 0.24 | -0.71 | 0.29 | 67.38 | 29.3
2019-09-04 | 13:10 | 42.3828 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 67.38 | 28.32
2019-09-04 | 13:10 | 42.4805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 13:10 | 42.582 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 67.38 | 29.3
2019-09-04 | 13:10 | 42.6914 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 28.32
2019-09-04 | 13:10 | 42.793 | 0.03 | 1.03 | -0.79 | 0.21 | -0.72 | 0.28 | 66.41 | 27.34
2019-09-04 | 13:10 | 42.8906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 42.9922 | 0.04 | 1.04 | -0.79 | 0.21 | -0.73 | 0.27 | 67.38 | 29.3
2019-09-04 | 13:10 | 43.1016 | 0.06 | 1.06 | -0.79 | 0.21 | -0.73 | 0.27 | 67.38 | 29.3
2019-09-04 | 13:10 | 43.2031 | 0.06 | 1.06 | -0.8 | 0.2 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 43.3008 | 0.02 | 1.02 | -0.79 | 0.21 | -0.74 | 0.26 | 67.38 | 29.3
2019-09-04 | 13:10 | 43.4102 | -0.09 | 0.91 | -0.67 | 0.33 | -0.7 | 0.3 | 67.38 | 28.32
2019-09-04 | 13:10 | 43.5117 | -0.09 | 0.91 | -0.67 | 0.33 | -0.7 | 0.3 | 67.38 | 29.3
2019-09-04 | 13:10 | 43.6133 | -0.14 | 0.86 | -0.63 | 0.37 | -0.7 | 0.3 | 69.34 | 30.27
2019-09-04 | 13:10 | 43.7109 | 0 | 1 | -0.76 | 0.24 | -0.7 | 0.3 | 67.38 | 29.3
2019-09-04 | 13:10 | 43.8203 | 0 | 1 | -0.78 | 0.22 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 43.9219 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 44.0234 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 44.1211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 67.38 | 30.27
2019-09-04 | 13:10 | 44.2305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 44.332 | 0.04 | 1.04 | -0.8 | 0.2 | -0.72 | 0.28 | 67.38 | 29.3
2019-09-04 | 13:10 | 44.4414 | 0.06 | 1.06 | -0.79 | 0.21 | -0.72 | 0.28 | 67.38 | 30.27
2019-09-04 | 13:10 | 44.543 | 0.05 | 1.05 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 44.6406 | 0.04 | 1.04 | -0.8 | 0.2 | -0.73 | 0.27 | 67.38 | 29.3
2019-09-04 | 13:10 | 44.7422 | 0.04 | 1.04 | -0.8 | 0.2 | -0.73 | 0.27 | 67.38 | 29.3
2019-09-04 | 13:10 | 44.8516 | -0.02 | 0.98 | -0.75 | 0.25 | -0.71 | 0.29 | 67.38 | 29.3
2019-09-04 | 13:10 | 44.9531 | -0.12 | 0.88 | -0.66 | 0.34 | -0.7 | 0.3 | 67.38 | 28.32
2019-09-04 | 13:10 | 45.0508 | -0.14 | 0.86 | -0.63 | 0.37 | -0.7 | 0.3 | 67.38 | 28.32
2019-09-04 | 13:10 | 45.1523 | -0.15 | 0.85 | -0.62 | 0.38 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 45.2617 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 45.3633 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 67.38 | 28.32
2019-09-04 | 13:10 | 45.4609 | 0.02 | 1.02 | -0.78 | 0.22 | -0.72 | 0.28 | 70.31 | 30.27
2019-09-04 | 13:10 | 45.5703 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 45.6719 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 13:10 | 45.7734 | 0.04 | 1.04 | -0.81 | 0.19 | -0.72 | 0.28 | 68.36 | 30.27
2019-09-04 | 13:10 | 45.8828 | 0.04 | 1.04 | -0.8 | 0.2 | -0.72 | 0.28 | 67.38 | 29.3
2019-09-04 | 13:10 | 45.9805 | 0.04 | 1.04 | -0.8 | 0.2 | -0.72 | 0.28 | 67.38 | 28.32
2019-09-04 | 13:10 | 46.082 | 0.04 | 1.04 | -0.8 | 0.2 | -0.72 | 0.28 | 67.38 | 29.3
2019-09-04 | 13:10 | 46.1836 | 0.04 | 1.04 | -0.8 | 0.2 | -0.73 | 0.27 | 67.38 | 28.32
2019-09-04 | 13:10 | 46.2812 | 0.03 | 1.03 | -0.8 | 0.2 | -0.73 | 0.27 | 69.34 | 29.3
2019-09-04 | 13:10 | 46.3906 | -0.08 | 0.92 | -0.7 | 0.3 | -0.71 | 0.29 | 67.38 | 28.32
2019-09-04 | 13:10 | 46.4922 | -0.13 | 0.87 | -0.65 | 0.35 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:10 | 46.5938 | -0.14 | 0.86 | -0.63 | 0.37 | -0.7 | 0.3 | 68.36 | 31.25
2019-09-04 | 13:10 | 46.7031 | -0.03 | 0.97 | -0.76 | 0.24 | -0.69 | 0.31 | 67.38 | 28.32
2019-09-04 | 13:10 | 46.8008 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 46.9023 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 31.25
2019-09-04 | 13:10 | 47 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 67.38 | 29.3
2019-09-04 | 13:10 | 47.1133 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 47.2109 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:10 | 47.3125 | 0.03 | 1.03 | -0.8 | 0.2 | -0.72 | 0.28 | 67.38 | 28.32
2019-09-04 | 13:10 | 47.4102 | 0.05 | 1.05 | -0.8 | 0.2 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 13:10 | 47.5234 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 47.6211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 67.38 | 28.32
2019-09-04 | 13:10 | 47.7227 | 0.05 | 1.05 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 30.27
2019-09-04 | 13:10 | 47.8203 | 0.04 | 1.04 | -0.76 | 0.24 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 47.9336 | -0.07 | 0.93 | -0.69 | 0.31 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 48.0312 | -0.14 | 0.86 | -0.64 | 0.36 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 48.1328 | -0.16 | 0.84 | -0.63 | 0.37 | -0.68 | 0.32 | 69.34 | 29.3
2019-09-04 | 13:10 | 48.2422 | -0.02 | 0.98 | -0.78 | 0.22 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 48.3438 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:10 | 48.4414 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 48.543 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 48.6523 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 67.38 | 27.34
2019-09-04 | 13:10 | 48.75 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 67.38 | 28.32
2019-09-04 | 13:10 | 48.8516 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 13:10 | 48.9609 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 67.38 | 28.32
2019-09-04 | 13:10 | 49.0625 | 0.06 | 1.06 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:10 | 49.1602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 67.38 | 30.27
2019-09-04 | 13:10 | 49.2734 | 0.06 | 1.06 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 30.27
2019-09-04 | 13:10 | 49.3711 | -0.04 | 0.96 | -0.72 | 0.28 | -0.72 | 0.28 | 67.38 | 28.32
2019-09-04 | 13:10 | 49.4727 | -0.11 | 0.89 | -0.66 | 0.34 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 49.5703 | -0.12 | 0.88 | -0.64 | 0.36 | -0.69 | 0.31 | 67.38 | 27.34
2019-09-04 | 13:10 | 49.6719 | -0.07 | 0.93 | -0.68 | 0.32 | -0.69 | 0.31 | 68.36 | 29.3
2019-09-04 | 13:10 | 49.7812 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 49.8828 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:10 | 49.9805 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 50.082 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 67.38 | 26.37
2019-09-04 | 13:10 | 50.1914 | 0.04 | 1.04 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 29.3
2019-09-04 | 13:10 | 50.293 | 0.06 | 1.06 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 50.4023 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:10 | 50.5 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:10 | 50.6016 | 0.08 | 1.08 | -0.8 | 0.2 | -0.72 | 0.28 | 68.36 | 29.3
2019-09-04 | 13:10 | 50.7031 | 0.05 | 1.05 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 50.8125 | 0.05 | 1.05 | -0.79 | 0.21 | -0.72 | 0.28 | 68.36 | 28.32
2019-09-04 | 13:10 | 50.9102 | -0.09 | 0.91 | -0.69 | 0.31 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 51.0117 | -0.15 | 0.85 | -0.66 | 0.34 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 51.1133 | -0.14 | 0.86 | -0.64 | 0.36 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:10 | 51.2227 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 67.38 | 27.34
2019-09-04 | 13:10 | 51.3203 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:10 | 51.4219 | 0.05 | 1.05 | -0.8 | 0.2 | -0.69 | 0.31 | 67.38 | 27.34
2019-09-04 | 13:10 | 51.5312 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 13:10 | 51.6328 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:10 | 51.7305 | 0.03 | 1.03 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:10 | 51.832 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:10 | 51.9414 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:10 | 52.043 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 52.1406 | 0.05 | 1.05 | -0.82 | 0.18 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:10 | 52.2422 | 0.03 | 1.03 | -0.82 | 0.18 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:10 | 52.3516 | -0.02 | 0.98 | -0.76 | 0.24 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:10 | 52.4531 | -0.1 | 0.9 | -0.7 | 0.3 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:10 | 52.5508 | -0.13 | 0.87 | -0.65 | 0.35 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 13:10 | 52.6602 | -0.14 | 0.86 | -0.64 | 0.36 | -0.69 | 0.31 | 68.36 | 30.27
2019-09-04 | 13:10 | 52.7617 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:10 | 52.8633 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 13:10 | 52.9727 | 0.03 | 1.03 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:10 | 53.0703 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:10 | 53.1719 | 0.04 | 1.04 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:10 | 53.2734 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:10 | 53.3711 | 0.05 | 1.05 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:10 | 53.4805 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:10 | 53.582 | 0.02 | 1.02 | -0.82 | 0.18 | -0.74 | 0.26 | 68.36 | 27.34
2019-09-04 | 13:10 | 53.6836 | 0.04 | 1.04 | -0.82 | 0.18 | -0.72 | 0.28 | 69.34 | 28.32
2019-09-04 | 13:10 | 53.7812 | 0.05 | 1.05 | -0.82 | 0.18 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:10 | 53.8906 | -0.07 | 0.93 | -0.71 | 0.29 | -0.71 | 0.29 | 68.36 | 31.25
2019-09-04 | 13:10 | 54 | -0.12 | 0.88 | -0.66 | 0.34 | -0.69 | 0.31 | 70.31 | 30.27
2019-09-04 | 13:10 | 54.0938 | -0.13 | 0.87 | -0.65 | 0.35 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:10 | 54.2031 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:10 | 54.3008 | 0.02 | 1.02 | -0.81 | 0.19 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 13:10 | 54.4023 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:10 | 54.5 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:10 | 54.6133 | 0.04 | 1.04 | -0.81 | 0.19 | -0.7 | 0.3 | 68.36 | 26.37
2019-09-04 | 13:10 | 54.7109 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:10 | 54.8125 | 0.05 | 1.05 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:10 | 54.9102 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 55.0234 | 0.05 | 1.05 | -0.82 | 0.18 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 55.1211 | 0.05 | 1.05 | -0.83 | 0.17 | -0.72 | 0.28 | 68.36 | 28.32
2019-09-04 | 13:10 | 55.2305 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:10 | 55.332 | 0.03 | 1.03 | -0.8 | 0.2 | -0.73 | 0.27 | 69.34 | 27.34
2019-09-04 | 13:10 | 55.4336 | -0.07 | 0.93 | -0.73 | 0.27 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 55.5312 | -0.13 | 0.87 | -0.69 | 0.31 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:10 | 55.6328 | -0.12 | 0.88 | -0.66 | 0.34 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:10 | 55.7422 | 0.01 | 1.01 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:10 | 55.8438 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:10 | 55.9414 | 0.02 | 1.02 | -0.81 | 0.19 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:10 | 56.043 | 0.03 | 1.03 | -0.82 | 0.18 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 13:10 | 56.1523 | 0.04 | 1.04 | -0.82 | 0.18 | -0.71 | 0.29 | 67.38 | 27.34
2019-09-04 | 13:10 | 56.25 | 0.04 | 1.04 | -0.82 | 0.18 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:10 | 56.3633 | 0.06 | 1.06 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:10 | 56.4609 | 0.04 | 1.04 | -0.84 | 0.16 | -0.72 | 0.28 | 71.29 | 28.32
2019-09-04 | 13:10 | 56.5625 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:10 | 56.6602 | 0.04 | 1.04 | -0.83 | 0.17 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:10 | 56.7617 | 0.05 | 1.05 | -0.83 | 0.17 | -0.72 | 0.28 | 68.36 | 26.37
2019-09-04 | 13:10 | 56.8711 | -0.03 | 0.97 | -0.77 | 0.23 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:10 | 56.9727 | -0.07 | 0.93 | -0.72 | 0.28 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:10 | 57.0703 | -0.12 | 0.88 | -0.68 | 0.32 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:10 | 57.1836 | -0.14 | 0.86 | -0.68 | 0.32 | -0.69 | 0.31 | 68.36 | 28.32
2019-09-04 | 13:10 | 57.2812 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 13:10 | 57.3828 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 57.4922 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 68.36 | 27.34
2019-09-04 | 13:11 | 57.5938 | 0.04 | 1.04 | -0.83 | 0.17 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 57.6914 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 13:11 | 57.793 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 57.9023 | 0.05 | 1.05 | -0.83 | 0.17 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:11 | 58 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 58.1016 | 0.04 | 1.04 | -0.83 | 0.17 | -0.72 | 0.28 | 68.36 | 26.37
2019-09-04 | 13:11 | 58.2031 | 0.05 | 1.05 | -0.83 | 0.17 | -0.72 | 0.28 | 70.31 | 28.32
2019-09-04 | 13:11 | 58.3008 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 58.4102 | -0.07 | 0.93 | -0.74 | 0.26 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 58.5117 | -0.11 | 0.89 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 58.6211 | -0.13 | 0.87 | -0.67 | 0.33 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 13:11 | 58.7227 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:11 | 58.8203 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 58.9219 | 0.02 | 1.02 | -0.83 | 0.17 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:11 | 59.0312 | 0.03 | 1.03 | -0.83 | 0.17 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 59.1328 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 59.2305 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 59.332 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 59.4414 | 0.05 | 1.05 | -0.84 | 0.16 | -0.72 | 0.28 | 68.36 | 28.32
2019-09-04 | 13:11 | 59.543 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:11 | 59.6406 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 59.7422 | 0.04 | 1.04 | -0.84 | 0.16 | -0.72 | 0.28 | 67.38 | 28.32
2019-09-04 | 13:11 | 59.8516 | 0 | 1 | -0.79 | 0.21 | -0.72 | 0.28 | 69.34 | 28.32
2019-09-04 | 13:11 | 59.9531 | -0.09 | 0.91 | -0.74 | 0.26 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:11 | 60.0508 | -0.12 | 0.88 | -0.7 | 0.3 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 60.1602 | -0.16 | 0.84 | -0.67 | 0.33 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 60.2617 | 0.01 | 1.01 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 60.3633 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 60.4609 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 60.5703 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:11 | 60.6719 | 0.03 | 1.03 | -0.85 | 0.15 | -0.73 | 0.27 | 69.34 | 27.34
2019-09-04 | 13:11 | 60.7734 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 60.8711 | 0.03 | 1.03 | -0.84 | 0.16 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 60.9805 | 0.04 | 1.04 | -0.84 | 0.16 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:11 | 61.082 | 0.05 | 1.05 | -0.86 | 0.14 | -0.73 | 0.27 | 68.36 | 27.34
2019-09-04 | 13:11 | 61.1836 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:11 | 61.293 | 0.03 | 1.03 | -0.85 | 0.15 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:11 | 61.3906 | -0.06 | 0.94 | -0.76 | 0.24 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 13:11 | 61.4922 | -0.12 | 0.88 | -0.71 | 0.29 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 13:11 | 61.5938 | -0.14 | 0.86 | -0.67 | 0.33 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 61.7031 | -0.02 | 0.98 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 61.8008 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:11 | 61.9023 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 62 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 62.1133 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 62.2109 | 0.04 | 1.04 | -0.84 | 0.16 | -0.72 | 0.28 | 69.34 | 29.3
2019-09-04 | 13:11 | 62.3125 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 62.4219 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:11 | 62.5234 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:11 | 62.6211 | 0.05 | 1.05 | -0.86 | 0.14 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 62.7227 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 62.832 | 0.02 | 1.02 | -0.83 | 0.17 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 62.9336 | -0.09 | 0.91 | -0.75 | 0.25 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 13:11 | 63.0312 | -0.12 | 0.88 | -0.71 | 0.29 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 63.1406 | -0.14 | 0.86 | -0.69 | 0.31 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 63.2422 | 0.02 | 1.02 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 63.3438 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 63.4531 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 13:11 | 63.5508 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 63.6523 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 13:11 | 63.75 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:11 | 63.8633 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 67.38 | 29.3
2019-09-04 | 13:11 | 63.9727 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:11 | 64.0625 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:11 | 64.1602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 64.2734 | 0.03 | 1.03 | -0.86 | 0.14 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:11 | 64.3711 | -0.03 | 0.97 | -0.79 | 0.21 | -0.72 | 0.28 | 69.34 | 28.32
2019-09-04 | 13:11 | 64.4727 | -0.09 | 0.91 | -0.74 | 0.26 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 64.582 | -0.14 | 0.86 | -0.71 | 0.29 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 64.6836 | -0.13 | 0.87 | -0.7 | 0.3 | -0.69 | 0.31 | 68.36 | 26.37
2019-09-04 | 13:11 | 64.7812 | 0.01 | 1.01 | -0.85 | 0.15 | -0.69 | 0.31 | 68.36 | 26.37
2019-09-04 | 13:11 | 64.8828 | 0.02 | 1.02 | -0.86 | 0.14 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 64.9922 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 65.0938 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 65.1914 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 65.293 | 0.05 | 1.05 | -0.87 | 0.13 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 65.4023 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:11 | 65.5 | 0.05 | 1.05 | -0.87 | 0.13 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 65.6016 | 0.05 | 1.05 | -0.87 | 0.13 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 65.7031 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 65.8125 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 68.36 | 27.34
2019-09-04 | 13:11 | 65.9102 | -0.05 | 0.95 | -0.77 | 0.23 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 13:11 | 66.0117 | -0.11 | 0.89 | -0.73 | 0.27 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 66.1211 | -0.13 | 0.87 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 66.2227 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 68.36 | 27.34
2019-09-04 | 13:11 | 66.3203 | 0.03 | 1.03 | -0.86 | 0.14 | -0.72 | 0.28 | 68.36 | 28.32
2019-09-04 | 13:11 | 66.4219 | 0.07 | 1.07 | -0.86 | 0.14 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 66.5312 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 66.6328 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 66.7305 | 0.03 | 1.03 | -0.86 | 0.14 | -0.73 | 0.27 | 69.34 | 26.37
2019-09-04 | 13:11 | 66.832 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 68.36 | 26.37
2019-09-04 | 13:11 | 66.9414 | 0.07 | 1.07 | -0.86 | 0.14 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:11 | 67.043 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 67.1406 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 68.36 | 27.34
2019-09-04 | 13:11 | 67.25 | 0.05 | 1.05 | -0.85 | 0.15 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 67.3516 | 0.02 | 1.02 | -0.82 | 0.18 | -0.72 | 0.28 | 68.36 | 28.32
2019-09-04 | 13:11 | 67.4531 | -0.09 | 0.91 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 67.5508 | -0.12 | 0.88 | -0.71 | 0.29 | -0.7 | 0.3 | 68.36 | 26.37
2019-09-04 | 13:11 | 67.6602 | -0.15 | 0.85 | -0.67 | 0.33 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 67.7617 | 0.01 | 1.01 | -0.84 | 0.16 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 67.8633 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 68.36 | 29.3
2019-09-04 | 13:11 | 67.9727 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 68.0703 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 68.1719 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 13:11 | 68.2734 | 0.05 | 1.05 | -0.86 | 0.14 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:11 | 68.3828 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:11 | 68.4805 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 68.36 | 27.34
2019-09-04 | 13:11 | 68.582 | 0.05 | 1.05 | -0.87 | 0.13 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 68.6836 | 0.05 | 1.05 | -0.86 | 0.14 | -0.73 | 0.27 | 69.34 | 29.3
2019-09-04 | 13:11 | 68.793 | 0.06 | 1.06 | -0.87 | 0.13 | -0.72 | 0.28 | 69.34 | 28.32
2019-09-04 | 13:11 | 68.8906 | -0.06 | 0.94 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 68.9922 | -0.11 | 0.89 | -0.74 | 0.26 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 69.1016 | -0.14 | 0.86 | -0.81 | 0.19 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 69.2031 | -0.03 | 0.97 | -0.92 | 0.08 | -0.68 | 0.32 | 68.36 | 27.34
2019-09-04 | 13:11 | 69.3008 | 0.02 | 1.02 | -0.96 | 0.04 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:11 | 69.4102 | 0.03 | 1.03 | -0.95 | 0.05 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 69.5117 | 0.04 | 1.04 | -0.94 | 0.06 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 69.6133 | 0.04 | 1.04 | -0.93 | 0.07 | -0.71 | 0.29 | 69.34 | 29.3
2019-09-04 | 13:11 | 69.7109 | 0.04 | 1.04 | -0.94 | 0.06 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 69.8203 | 0.05 | 1.05 | -0.95 | 0.05 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:11 | 69.9219 | 0.04 | 1.04 | -0.93 | 0.07 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 70.0234 | 0.04 | 1.04 | -0.92 | 0.08 | -0.73 | 0.27 | 69.34 | 27.34
2019-09-04 | 13:11 | 70.1211 | 0.04 | 1.04 | -0.92 | 0.08 | -0.71 | 0.29 | 68.36 | 27.34
2019-09-04 | 13:11 | 70.2227 | 0.04 | 1.04 | -0.93 | 0.07 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 70.332 | 0.03 | 1.03 | -0.92 | 0.08 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:11 | 70.4336 | -0.08 | 0.92 | -0.8 | 0.2 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 13:11 | 70.543 | -0.12 | 0.88 | -0.77 | 0.23 | -0.68 | 0.32 | 69.34 | 27.34
2019-09-04 | 13:11 | 70.6406 | -0.13 | 0.87 | -0.75 | 0.25 | -0.68 | 0.32 | 69.34 | 27.34
2019-09-04 | 13:11 | 70.7422 | 0 | 1 | -0.89 | 0.11 | -0.7 | 0.3 | 69.34 | 29.3
2019-09-04 | 13:11 | 70.8438 | 0.02 | 1.02 | -0.89 | 0.11 | -0.7 | 0.3 | 68.36 | 28.32
2019-09-04 | 13:11 | 70.9531 | 0.03 | 1.03 | -0.89 | 0.11 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 71.0508 | 0.04 | 1.04 | -0.88 | 0.12 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 71.1523 | 0.05 | 1.05 | -0.9 | 0.1 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 71.25 | 0.04 | 1.04 | -0.88 | 0.12 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:11 | 71.3633 | 0.04 | 1.04 | -0.89 | 0.11 | -0.71 | 0.29 | 68.36 | 28.32
2019-09-04 | 13:11 | 71.4609 | 0.05 | 1.05 | -0.89 | 0.11 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 71.5625 | 0.05 | 1.05 | -0.89 | 0.11 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 71.6602 | 0.04 | 1.04 | -0.9 | 0.1 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 71.7734 | 0.05 | 1.05 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 71.8711 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 71.9805 | -0.11 | 0.89 | -0.78 | 0.22 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 72.082 | -0.14 | 0.86 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 72.1836 | -0.13 | 0.87 | -0.73 | 0.27 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 13:11 | 72.2812 | 0.03 | 1.03 | -0.9 | 0.1 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:11 | 72.3828 | 0.03 | 1.03 | -0.9 | 0.1 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 72.4922 | 0.03 | 1.03 | -0.9 | 0.1 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 72.5938 | 0.04 | 1.04 | -0.9 | 0.1 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 72.6914 | 0.04 | 1.04 | -0.89 | 0.11 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 72.793 | 0.04 | 1.04 | -0.9 | 0.1 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 72.9023 | 0.04 | 1.04 | -0.91 | 0.09 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:11 | 73 | 0.04 | 1.04 | -0.89 | 0.11 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 73.1016 | 0.07 | 1.07 | -0.9 | 0.1 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 73.2109 | 0.05 | 1.05 | -0.9 | 0.1 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 73.3125 | 0.04 | 1.04 | -0.89 | 0.11 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 73.4102 | -0.07 | 0.93 | -0.8 | 0.2 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 73.5117 | -0.11 | 0.89 | -0.77 | 0.23 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 73.6211 | -0.15 | 0.85 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 13:11 | 73.7227 | 0.01 | 1.01 | -0.87 | 0.13 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 73.8203 | 0.03 | 1.03 | -0.9 | 0.1 | -0.68 | 0.32 | 68.36 | 27.34
2019-09-04 | 13:11 | 73.9219 | 0.04 | 1.04 | -0.89 | 0.11 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 74.0312 | 0.04 | 1.04 | -0.88 | 0.12 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 74.1328 | 0.03 | 1.03 | -0.88 | 0.12 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 74.2422 | 0.04 | 1.04 | -0.89 | 0.11 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:11 | 74.3438 | 0.04 | 1.04 | -0.89 | 0.11 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 74.4414 | 0.04 | 1.04 | -0.89 | 0.11 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 74.543 | 0.04 | 1.04 | -0.89 | 0.11 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:11 | 74.6406 | 0.05 | 1.05 | -0.89 | 0.11 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 74.75 | 0.05 | 1.05 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 74.8516 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 74.9531 | -0.08 | 0.92 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 75.0625 | -0.14 | 0.86 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 75.1602 | -0.15 | 0.85 | -0.73 | 0.27 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:11 | 75.2617 | 0 | 1 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 75.3711 | 0.02 | 1.02 | -0.88 | 0.12 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 75.4727 | 0.04 | 1.04 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:11 | 75.5703 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 75.6719 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 75.7812 | 0.04 | 1.04 | -0.88 | 0.12 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 75.8828 | 0.06 | 1.06 | -0.88 | 0.12 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 75.9805 | 0.04 | 1.04 | -0.89 | 0.11 | -0.7 | 0.3 | 68.36 | 27.34
2019-09-04 | 13:11 | 76.082 | 0.04 | 1.04 | -0.89 | 0.11 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 76.1914 | 0.05 | 1.05 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 76.293 | 0.05 | 1.05 | -0.9 | 0.1 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 76.3906 | -0.05 | 0.95 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 76.5 | -0.1 | 0.9 | -0.75 | 0.25 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 76.6016 | -0.14 | 0.86 | -0.74 | 0.26 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:11 | 76.7031 | -0.07 | 0.93 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 13:11 | 76.8008 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 76.9102 | 0.02 | 1.02 | -0.86 | 0.14 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 13:11 | 77.0117 | 0.03 | 1.03 | -0.87 | 0.13 | -0.69 | 0.31 | 68.36 | 27.34
2019-09-04 | 13:11 | 77.1133 | 0.04 | 1.04 | -0.87 | 0.13 | -0.69 | 0.31 | 69.34 | 25.39
2019-09-04 | 13:11 | 77.2109 | 0.04 | 1.04 | -0.88 | 0.12 | -0.69 | 0.31 | 68.36 | 25.39
2019-09-04 | 13:11 | 77.3203 | 0.04 | 1.04 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 77.4219 | 0.04 | 1.04 | -0.88 | 0.12 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 77.5234 | 0.05 | 1.05 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 77.6328 | 0.04 | 1.04 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 77.7305 | 0.04 | 1.04 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 77.832 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 77.9336 | -0.06 | 0.94 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 78.043 | -0.1 | 0.9 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 78.1406 | -0.13 | 0.87 | -0.74 | 0.26 | -0.67 | 0.33 | 69.34 | 27.34
2019-09-04 | 13:11 | 78.2422 | 0.01 | 1.01 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 78.3438 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 78.4531 | 0.02 | 1.02 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 78.5508 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 78.6523 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 78.75 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 78.8633 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 78.9609 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 79.0625 | 0.05 | 1.05 | -0.87 | 0.13 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 79.1719 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 79.2734 | 0.05 | 1.05 | -0.87 | 0.13 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 79.3711 | -0.03 | 0.97 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 79.4727 | -0.1 | 0.9 | -0.76 | 0.24 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 79.582 | -0.13 | 0.87 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 79.6836 | -0.12 | 0.88 | -0.73 | 0.27 | -0.66 | 0.34 | 71.29 | 26.37
2019-09-04 | 13:11 | 79.7812 | 0.01 | 1.01 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 79.8828 | 0.02 | 1.02 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 79.9922 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 80.0938 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 80.2031 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 80.3008 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 80.4023 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:11 | 80.5 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 80.6016 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 80.7109 | 0.05 | 1.05 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:11 | 80.8125 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 80.9102 | -0.05 | 0.95 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 81.0234 | -0.12 | 0.88 | -0.74 | 0.26 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:11 | 81.1211 | -0.13 | 0.87 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 81.2227 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 81.332 | 0 | 1 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 81.4336 | 0.02 | 1.02 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 13:11 | 81.5312 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:11 | 81.6328 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 13:11 | 81.7422 | 0.05 | 1.05 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 81.8438 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 81.9414 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 82.043 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 82.1406 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 82.25 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 13:11 | 82.3516 | 0.01 | 1.01 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 82.4609 | -0.09 | 0.91 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 82.5625 | -0.13 | 0.87 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 82.6602 | -0.14 | 0.86 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 82.7617 | 0 | 1 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 82.8711 | 0.03 | 1.03 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 82.9727 | 0.03 | 1.03 | -0.85 | 0.15 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 13:11 | 83.0703 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 83.1719 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 83.2812 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 83.3828 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 83.4805 | 0.06 | 1.06 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 83.582 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 83.6914 | 0.06 | 1.06 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 83.793 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 13:11 | 83.8906 | -0.05 | 0.95 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 84 | -0.1 | 0.9 | -0.74 | 0.26 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:11 | 84.1016 | -0.15 | 0.85 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 84.2031 | -0.06 | 0.94 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 84.3008 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 84.4102 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 84.5117 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 84.6133 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 84.7109 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:11 | 84.8203 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 84.9219 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 85.0234 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 85.1328 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 85.2305 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:11 | 85.332 | 0.03 | 1.03 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 85.4336 | -0.09 | 0.91 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 85.543 | -0.13 | 0.87 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 85.6406 | -0.14 | 0.86 | -0.71 | 0.29 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 85.7422 | -0.01 | 0.99 | -0.83 | 0.17 | -0.67 | 0.33 | 70.31 | 27.34
2019-09-04 | 13:11 | 85.8438 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 85.9531 | 0.02 | 1.02 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 86.0508 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 86.1602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:11 | 86.2617 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 86.3633 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 86.4609 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 86.5625 | 0.05 | 1.05 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:11 | 86.6719 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 86.7734 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 86.8711 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 86.9805 | -0.07 | 0.93 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 87.082 | -0.11 | 0.89 | -0.73 | 0.27 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 87.1836 | -0.14 | 0.86 | -0.7 | 0.3 | -0.67 | 0.33 | 70.31 | 27.34
2019-09-04 | 13:11 | 87.2812 | 0.02 | 1.02 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 87.3906 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 87.4922 | 0.05 | 1.05 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 87.5938 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 87.7031 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 87.8008 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 13:11 | 87.9023 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 88 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 88.1133 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 88.2109 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 88.3125 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 88.4219 | -0.05 | 0.95 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 88.5234 | -0.13 | 0.87 | -0.71 | 0.29 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:11 | 88.6211 | -0.16 | 0.84 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 88.7227 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 88.832 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 88.9336 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:11 | 89.0312 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 89.1328 | 0.03 | 1.03 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 89.2422 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 89.3438 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 89.4414 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 89.543 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 89.6406 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:11 | 89.75 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 89.8516 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 89.9609 | -0.06 | 0.94 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 90.0625 | -0.11 | 0.89 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 90.1602 | -0.14 | 0.86 | -0.7 | 0.3 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:11 | 90.2617 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:11 | 90.3711 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 90.4727 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 90.5703 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 90.6719 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 90.7812 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 90.8828 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:11 | 90.9805 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 91.0938 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 91.1914 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 91.293 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:11 | 91.3906 | -0.02 | 0.98 | -0.78 | 0.22 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 91.5 | -0.11 | 0.89 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 91.6016 | -0.15 | 0.85 | -0.71 | 0.29 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 91.7031 | -0.14 | 0.86 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 91.8008 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 91.9102 | 0.01 | 1.01 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:11 | 92.0117 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 92.1133 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 92.2227 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 92.3203 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 92.4219 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 92.5234 | 0.06 | 1.06 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:11 | 92.6328 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 92.7305 | 0.06 | 1.06 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 92.832 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 92.9414 | -0.05 | 0.95 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 93.043 | -0.1 | 0.9 | -0.73 | 0.27 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 93.1406 | -0.14 | 0.86 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:11 | 93.25 | 0 | 1 | -0.83 | 0.17 | -0.67 | 0.33 | 69.34 | 26.37
2019-09-04 | 13:11 | 93.3516 | 0.03 | 1.03 | -0.85 | 0.15 | -0.68 | 0.32 | 69.34 | 27.34
2019-09-04 | 13:11 | 93.4531 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 93.5508 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 93.6602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 93.7617 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 93.8633 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 93.9727 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 94.0625 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:11 | 94.1719 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 94.2734 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 94.3711 | 0.02 | 1.02 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 94.4805 | -0.1 | 0.9 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 94.582 | -0.14 | 0.86 | -0.71 | 0.29 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 94.6836 | -0.11 | 0.89 | -0.73 | 0.27 | -0.67 | 0.33 | 70.31 | 27.34
2019-09-04 | 13:11 | 94.793 | 0 | 1 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 94.8906 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 94.9922 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 95.0938 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 95.2031 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 95.3008 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 95.4023 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 95.5 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 95.6133 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 95.7109 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 95.8125 | 0.05 | 1.05 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 95.9219 | -0.04 | 0.96 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 96.0234 | -0.1 | 0.9 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 96.1211 | -0.14 | 0.86 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 96.2227 | -0.02 | 0.98 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 96.332 | 0.02 | 1.02 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 96.4336 | 0.03 | 1.03 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 96.5312 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 96.6328 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 96.7422 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:11 | 96.8438 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 96.9414 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 97.0508 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 97.1523 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 97.25 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 97.3516 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 97.4609 | -0.07 | 0.93 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 97.5625 | -0.1 | 0.9 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:11 | 97.6602 | -0.13 | 0.87 | -0.72 | 0.28 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:11 | 97.7617 | 0.01 | 1.01 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:11 | 97.8711 | 0.02 | 1.02 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:11 | 97.9727 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 98.0703 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 98.1836 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 98.2812 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 98.3828 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 98.4922 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 13:11 | 98.5938 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 98.6914 | 0.07 | 1.07 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 98.793 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 98.9023 | -0.01 | 0.99 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 99 | -0.11 | 0.89 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 99.1016 | -0.15 | 0.85 | -0.7 | 0.3 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:11 | 99.2109 | -0.14 | 0.86 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 26.37
2019-09-04 | 13:11 | 99.3125 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 99.4102 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 99.5117 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 99.6211 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:11 | 99.7227 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 99.8203 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 99.9219 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:11 | 100.0234 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 100.1328 | 0.05 | 1.05 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 100.2305 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 100.332 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 100.4414 | -0.03 | 0.97 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 100.543 | -0.12 | 0.88 | -0.74 | 0.26 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:11 | 100.6406 | -0.13 | 0.87 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 100.75 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 100.8516 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 100.9531 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 101.0508 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 101.1602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:11 | 101.2617 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:11 | 101.3633 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:11 | 101.4609 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 101.5625 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:11 | 101.6719 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 101.7734 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 101.8828 | 0.01 | 1.01 | -0.81 | 0.19 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 101.9805 | -0.08 | 0.92 | -0.74 | 0.26 | -0.67 | 0.33 | 72.27 | 27.34
2019-09-04 | 13:11 | 102.082 | -0.13 | 0.87 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 102.1836 | -0.16 | 0.84 | -0.71 | 0.29 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 102.293 | 0 | 1 | -0.84 | 0.16 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:11 | 102.3906 | 0.02 | 1.02 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 102.4922 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 102.5938 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:11 | 102.7031 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:11 | 102.8008 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 102.9023 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 103.0117 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 103.1133 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 103.2109 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 103.3125 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 103.4219 | -0.04 | 0.96 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 103.5234 | -0.08 | 0.92 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:11 | 103.6211 | -0.15 | 0.85 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 103.7227 | -0.04 | 0.96 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:11 | 103.832 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 103.9336 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 104.0313 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 104.1406 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 104.2422 | 0.05 | 1.05 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 104.3438 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 104.4414 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 104.5508 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 104.6523 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 104.75 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 104.8516 | 0.03 | 1.03 | -0.85 | 0.15 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:11 | 104.9609 | -0.08 | 0.92 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 105.0625 | -0.14 | 0.86 | -0.72 | 0.28 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:11 | 105.1719 | -0.16 | 0.84 | -0.7 | 0.3 | -0.67 | 0.33 | 71.29 | 27.34
2019-09-04 | 13:11 | 105.2734 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 105.3711 | 0.02 | 1.02 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:11 | 105.4727 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 105.582 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 105.6836 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 105.7813 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:11 | 105.8828 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:11 | 105.9805 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 106.0938 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:11 | 106.1914 | 0.06 | 1.06 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 106.293 | 0.07 | 1.07 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 106.4023 | -0.03 | 0.97 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 106.5 | -0.12 | 0.88 | -0.74 | 0.26 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 106.6016 | -0.12 | 0.88 | -0.71 | 0.29 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 106.7109 | -0.16 | 0.84 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 106.8125 | 0.01 | 1.01 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:11 | 106.9102 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 107.0117 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 107.1133 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 107.2227 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:11 | 107.3203 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 107.4219 | 0.05 | 1.05 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:11 | 107.5234 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 107.6328 | 0.05 | 1.05 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:11 | 107.7305 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 107.8438 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 107.9414 | -0.07 | 0.93 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:11 | 108.043 | -0.12 | 0.88 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 108.1406 | -0.15 | 0.85 | -0.72 | 0.28 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:11 | 108.25 | -0.01 | 0.99 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:11 | 108.3516 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 108.4531 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 108.5508 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 108.6602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:11 | 108.7617 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 108.8633 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 108.9727 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:11 | 109.0703 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 109.1719 | 0.03 | 1.03 | -0.88 | 0.12 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 109.2734 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 109.3828 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:11 | 109.4805 | -0.07 | 0.93 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:11 | 109.582 | -0.12 | 0.88 | -0.73 | 0.27 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 109.6836 | -0.11 | 0.89 | -0.72 | 0.28 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 13:11 | 109.793 | 0 | 1 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:11 | 109.8906 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 109.9922 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 110.1016 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:11 | 110.2031 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 110.3008 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 13:11 | 110.4023 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 110.5117 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 110.6133 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 110.7109 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 110.8125 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 110.9219 | -0.02 | 0.98 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 111.0234 | -0.1 | 0.9 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 111.1211 | -0.13 | 0.87 | -0.7 | 0.3 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:11 | 111.2305 | -0.06 | 0.94 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:11 | 111.332 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 111.4336 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 111.543 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 111.6406 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 111.7422 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 111.8438 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:11 | 111.9414 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 112.0508 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:11 | 112.1523 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 112.25 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:11 | 112.3516 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 29.3
2019-09-04 | 13:11 | 112.4609 | -0.07 | 0.93 | -0.75 | 0.25 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 112.5625 | -0.15 | 0.85 | -0.71 | 0.29 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:11 | 112.6719 | -0.15 | 0.85 | -0.7 | 0.3 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:11 | 112.7734 | -0.01 | 0.99 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 112.8711 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:11 | 112.9727 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 113.082 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 113.1836 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 113.2813 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:11 | 113.3828 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 113.4805 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:11 | 113.5938 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:11 | 113.6914 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:11 | 113.8008 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 113.9023 | 0 | 1 | -0.81 | 0.19 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:11 | 114.0117 | -0.11 | 0.89 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:11 | 114.1016 | -0.13 | 0.87 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 114.2109 | -0.13 | 0.87 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 114.3125 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 114.4102 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 114.5117 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 114.6211 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 114.7227 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:11 | 114.8203 | 0.03 | 1.03 | -0.86 | 0.14 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:11 | 114.9336 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:11 | 115.0313 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:11 | 115.1328 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:11 | 115.2305 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 72.27 | 27.34
2019-09-04 | 13:11 | 115.3438 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:11 | 115.4414 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:11 | 115.543 | -0.11 | 0.89 | -0.74 | 0.26 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:11 | 115.6406 | -0.11 | 0.89 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:11 | 115.75 | -0.02 | 0.98 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:11 | 115.8516 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:11 | 115.9531 | 0.01 | 1.01 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:11 | 116.0625 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 116.1602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:11 | 116.2617 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:11 | 116.3633 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 116.4727 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 116.5703 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 116.6719 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 116.7734 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:12 | 116.8828 | 0 | 1 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 116.9805 | -0.09 | 0.91 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 117.0938 | -0.13 | 0.87 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 117.1914 | -0.13 | 0.87 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:12 | 117.293 | -0.01 | 0.99 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 117.3906 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 13:12 | 117.5 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 117.6016 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 117.7031 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 13:12 | 117.8008 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 117.9023 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 118.0117 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 118.1133 | 0.06 | 1.06 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 118.2109 | 0.06 | 1.06 | -0.87 | 0.13 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:12 | 118.3125 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:12 | 118.4219 | -0.03 | 0.97 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:12 | 118.5234 | -0.11 | 0.89 | -0.73 | 0.27 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 118.6328 | -0.13 | 0.87 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:12 | 118.7305 | -0.09 | 0.91 | -0.73 | 0.27 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:12 | 118.832 | 0 | 1 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:12 | 118.9414 | 0.03 | 1.03 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:12 | 119.0313 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:12 | 119.1406 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:12 | 119.2422 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:12 | 119.3438 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 119.4531 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 119.5508 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 13:12 | 119.6523 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:12 | 119.7617 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 74.22 | 28.32
2019-09-04 | 13:12 | 119.8633 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 73.24 | 28.32
2019-09-04 | 13:12 | 119.9727 | -0.05 | 0.95 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 120.0625 | -0.11 | 0.89 | -0.72 | 0.28 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:12 | 120.1719 | -0.14 | 0.86 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:12 | 120.2734 | 0.03 | 1.03 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:12 | 120.3711 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 120.4727 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:12 | 120.582 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 120.6836 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 120.7813 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 120.8906 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 120.9922 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 121.0938 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 121.1914 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:12 | 121.3008 | 0.06 | 1.06 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 121.4023 | -0.01 | 0.99 | -0.82 | 0.18 | -0.72 | 0.28 | 71.29 | 28.32
2019-09-04 | 13:12 | 121.5 | -0.1 | 0.9 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:12 | 121.6016 | -0.12 | 0.88 | -0.7 | 0.3 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 13:12 | 121.7109 | -0.15 | 0.85 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:12 | 121.8125 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 28.32
2019-09-04 | 13:12 | 121.9102 | 0.03 | 1.03 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 13:12 | 122.0234 | 0.03 | 1.03 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 122.1211 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:12 | 122.2227 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 13:12 | 122.3203 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 122.4336 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:12 | 122.5313 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 122.6328 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 122.7305 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 122.8438 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 122.9531 | -0.06 | 0.94 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 123.0508 | -0.11 | 0.89 | -0.72 | 0.28 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 13:12 | 123.1523 | -0.13 | 0.87 | -0.71 | 0.29 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:12 | 123.25 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:12 | 123.3516 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 123.4609 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 123.5625 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 123.6602 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:12 | 123.7617 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:12 | 123.8633 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 123.9727 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 124.0703 | 0.05 | 1.05 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 124.1719 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 124.2734 | 0.05 | 1.05 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 124.3828 | 0.01 | 1.01 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 124.4805 | -0.07 | 0.93 | -0.75 | 0.25 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:12 | 124.582 | -0.14 | 0.86 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 29.3
2019-09-04 | 13:12 | 124.6914 | -0.13 | 0.87 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:12 | 124.793 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:12 | 124.8906 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 125 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 125.1016 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 125.2031 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 125.3008 | 0.05 | 1.05 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 125.4102 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 125.5117 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 125.6133 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 125.7227 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:12 | 125.8203 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 125.9219 | -0.05 | 0.95 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 126.0234 | -0.09 | 0.91 | -0.73 | 0.27 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:12 | 126.1328 | -0.13 | 0.87 | -0.71 | 0.29 | -0.7 | 0.3 | 73.24 | 29.3
2019-09-04 | 13:12 | 126.2305 | -0.09 | 0.91 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:12 | 126.332 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:12 | 126.4336 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 126.543 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 126.6406 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 25.39
2019-09-04 | 13:12 | 126.7422 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 126.8516 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 126.9531 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 127.0508 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 25.39
2019-09-04 | 13:12 | 127.1523 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 127.2617 | 0.06 | 1.06 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 127.3633 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 127.4609 | -0.05 | 0.95 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 127.5625 | -0.13 | 0.87 | -0.73 | 0.27 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 127.6719 | -0.14 | 0.86 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:12 | 127.7734 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 127.8711 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 127.9805 | 0.02 | 1.02 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 128.082 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 128.1836 | 0.05 | 1.05 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 128.2813 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 128.3906 | 0.03 | 1.03 | -0.87 | 0.13 | -0.69 | 0.31 | 72.27 | 25.39
2019-09-04 | 13:12 | 128.4922 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 128.5938 | 0.05 | 1.05 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 128.6914 | 0.06 | 1.06 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 128.8008 | 0.03 | 1.03 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 128.9023 | -0.01 | 0.99 | -0.82 | 0.18 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:12 | 129.0117 | -0.1 | 0.9 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 129.1133 | -0.15 | 0.85 | -0.73 | 0.27 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 129.2109 | -0.15 | 0.85 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 25.39
2019-09-04 | 13:12 | 129.3125 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:12 | 129.4102 | 0.02 | 1.02 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:12 | 129.5234 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 129.6211 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 129.7227 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 129.8203 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 129.9336 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:12 | 130.0313 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 130.1328 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:12 | 130.2305 | 0.04 | 1.04 | -0.88 | 0.12 | -0.73 | 0.27 | 71.29 | 27.34
2019-09-04 | 13:12 | 130.3438 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 130.4414 | -0.04 | 0.96 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 130.5508 | -0.12 | 0.88 | -0.74 | 0.26 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:12 | 130.6523 | -0.14 | 0.86 | -0.71 | 0.29 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:12 | 130.75 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 13:12 | 130.8516 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 130.9609 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 131.0625 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:12 | 131.1602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 131.2617 | 0.02 | 1.02 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 131.3633 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:12 | 131.4727 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:12 | 131.5703 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 70.31 | 26.37
2019-09-04 | 13:12 | 131.6836 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 131.7813 | 0.06 | 1.06 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 131.8828 | 0.02 | 1.02 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 28.32
2019-09-04 | 13:12 | 131.9805 | -0.09 | 0.91 | -0.76 | 0.24 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 132.0938 | -0.13 | 0.87 | -0.72 | 0.28 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:12 | 132.1914 | -0.15 | 0.85 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 132.293 | 0.01 | 1.01 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:12 | 132.4023 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 132.5 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 132.6016 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 132.7031 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 132.8125 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:12 | 132.9102 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 133.0117 | 0.03 | 1.03 | -0.86 | 0.14 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 133.1133 | 0.05 | 1.05 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 133.2227 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 133.3203 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 133.4219 | -0.02 | 0.98 | -0.8 | 0.2 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 13:12 | 133.5313 | -0.11 | 0.89 | -0.74 | 0.26 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 133.6328 | -0.14 | 0.86 | -0.7 | 0.3 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 133.7305 | -0.15 | 0.85 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 133.832 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 133.9414 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 134.043 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 134.1406 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 25.39
2019-09-04 | 13:12 | 134.2422 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 134.3516 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 134.4531 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 134.5508 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 70.31 | 27.34
2019-09-04 | 13:12 | 134.6523 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 70.31 | 28.32
2019-09-04 | 13:12 | 134.7617 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:12 | 134.8633 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 25.39
2019-09-04 | 13:12 | 134.9727 | -0.08 | 0.92 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 135.0703 | -0.11 | 0.89 | -0.73 | 0.27 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 135.1719 | -0.13 | 0.87 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 135.2734 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 135.3711 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 135.4805 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:12 | 135.582 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 25.39
2019-09-04 | 13:12 | 135.6836 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 135.7813 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 135.8906 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 72.27 | 27.34
2019-09-04 | 13:12 | 135.9922 | 0.07 | 1.07 | -0.85 | 0.15 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 136.0938 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 136.2031 | 0.06 | 1.06 | -0.86 | 0.14 | -0.73 | 0.27 | 70.31 | 27.34
2019-09-04 | 13:12 | 136.3008 | 0.05 | 1.05 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 136.4023 | 0.03 | 1.03 | -0.82 | 0.18 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 136.5117 | -0.07 | 0.93 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 136.6133 | -0.14 | 0.86 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 136.7109 | -0.13 | 0.87 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:12 | 136.8125 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 136.9102 | 0.01 | 1.01 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 137.0234 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:12 | 137.1211 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 137.2227 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 137.3203 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 137.4336 | 0.01 | 1.01 | -0.87 | 0.13 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:12 | 137.5313 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 137.6406 | 0.04 | 1.04 | -0.87 | 0.13 | -0.73 | 0.27 | 71.29 | 27.34
2019-09-04 | 13:12 | 137.7422 | 0.05 | 1.05 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 28.32
2019-09-04 | 13:12 | 137.8438 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 137.9531 | -0.04 | 0.96 | -0.82 | 0.18 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 138.0508 | -0.11 | 0.89 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 138.1523 | -0.13 | 0.87 | -0.72 | 0.28 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 13:12 | 138.25 | -0.04 | 0.96 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 138.3516 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 138.4609 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 138.5625 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 138.6602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 69.34 | 28.32
2019-09-04 | 13:12 | 138.7734 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:12 | 138.8711 | 0.04 | 1.04 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 138.9727 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 71.29 | 26.37
2019-09-04 | 13:12 | 139.0703 | 0.05 | 1.05 | -0.87 | 0.13 | -0.73 | 0.27 | 70.31 | 27.34
2019-09-04 | 13:12 | 139.1836 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 139.2813 | 0.05 | 1.05 | -0.88 | 0.12 | -0.73 | 0.27 | 72.27 | 27.34
2019-09-04 | 13:12 | 139.3828 | 0.04 | 1.04 | -0.85 | 0.15 | -0.74 | 0.26 | 71.29 | 27.34
2019-09-04 | 13:12 | 139.4922 | -0.08 | 0.92 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 139.5938 | -0.13 | 0.87 | -0.74 | 0.26 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 139.6914 | -0.12 | 0.88 | -0.7 | 0.3 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:12 | 139.793 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 139.9023 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:12 | 140 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 140.1016 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 140.2031 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 140.3125 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 70.31 | 27.34
2019-09-04 | 13:12 | 140.4102 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 140.5117 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 71.29 | 29.3
2019-09-04 | 13:12 | 140.6211 | 0.01 | 1.01 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 140.7227 | 0.05 | 1.05 | -0.87 | 0.13 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:12 | 140.8203 | 0.05 | 1.05 | -0.85 | 0.15 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:12 | 140.9219 | -0.03 | 0.97 | -0.82 | 0.18 | -0.72 | 0.28 | 71.29 | 28.32
2019-09-04 | 13:12 | 141.0313 | -0.1 | 0.9 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 13:12 | 141.1328 | -0.15 | 0.85 | -0.71 | 0.29 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 141.2305 | -0.17 | 0.83 | -0.69 | 0.31 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 141.332 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 141.4414 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 141.543 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 13:12 | 141.6406 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:12 | 141.7422 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 141.8516 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 141.9531 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:12 | 142.0508 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 142.1602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 69.34 | 27.34
2019-09-04 | 13:12 | 142.2617 | 0.04 | 1.04 | -0.86 | 0.14 | -0.73 | 0.27 | 71.29 | 27.34
2019-09-04 | 13:12 | 142.3633 | 0.06 | 1.06 | -0.87 | 0.13 | -0.72 | 0.28 | 71.29 | 28.32
2019-09-04 | 13:12 | 142.4727 | -0.07 | 0.93 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 13:12 | 142.5703 | -0.11 | 0.89 | -0.73 | 0.27 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 142.6719 | -0.15 | 0.85 | -0.7 | 0.3 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 142.7734 | 0 | 1 | -0.81 | 0.19 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 142.8711 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 142.9805 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 143.082 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 143.1836 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:12 | 143.293 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 143.3906 | 0.05 | 1.05 | -0.84 | 0.16 | -0.72 | 0.28 | 72.27 | 27.34
2019-09-04 | 13:12 | 143.4922 | 0.02 | 1.02 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 143.6016 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 72.27 | 28.32
2019-09-04 | 13:12 | 143.7031 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 143.8008 | 0.05 | 1.05 | -0.86 | 0.14 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 143.9023 | 0 | 1 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 144.0117 | -0.09 | 0.91 | -0.75 | 0.25 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 144.1133 | -0.14 | 0.86 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 144.2109 | -0.16 | 0.84 | -0.69 | 0.31 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 144.3125 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 144.4102 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 144.5234 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 144.6211 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 69.34 | 27.34
2019-09-04 | 13:12 | 144.7305 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 144.832 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:12 | 144.9336 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 145.0313 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 145.1406 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 145.2422 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 145.3438 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 69.34 | 28.32
2019-09-04 | 13:12 | 145.4531 | -0.06 | 0.94 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 145.5508 | -0.11 | 0.89 | -0.73 | 0.27 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:12 | 145.6523 | -0.14 | 0.86 | -0.69 | 0.31 | -0.68 | 0.32 | 69.34 | 28.32
2019-09-04 | 13:12 | 145.75 | -0.06 | 0.94 | -0.74 | 0.26 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 145.8633 | 0.03 | 1.03 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 145.9609 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:12 | 146.0625 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 146.1602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 146.2734 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 146.3711 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 146.4727 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:12 | 146.5703 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 146.6836 | 0.05 | 1.05 | -0.84 | 0.16 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 146.7813 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 146.8906 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 146.9922 | -0.08 | 0.92 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 147.0938 | -0.14 | 0.86 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 147.1914 | -0.14 | 0.86 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 147.293 | 0.01 | 1.01 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 147.4023 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 147.5 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:12 | 147.6016 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 147.7031 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 147.8125 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 147.9102 | 0.04 | 1.04 | -0.84 | 0.16 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 148.0234 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 148.1211 | 0.05 | 1.05 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 148.2227 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 148.3203 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 148.4219 | -0.01 | 0.99 | -0.79 | 0.21 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 148.5313 | -0.11 | 0.89 | -0.72 | 0.28 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 148.6328 | -0.15 | 0.85 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 148.7305 | -0.16 | 0.84 | -0.68 | 0.32 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:12 | 148.832 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 148.9414 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 149.043 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 149.1523 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 149.25 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:12 | 149.3516 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:12 | 149.4531 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 149.5625 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 149.6602 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:12 | 149.7617 | 0.04 | 1.04 | -0.84 | 0.16 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:12 | 149.8633 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 149.9727 | -0.05 | 0.95 | -0.77 | 0.23 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 150.0703 | -0.12 | 0.88 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 150.1719 | -0.17 | 0.83 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 150.2813 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:12 | 150.3828 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:12 | 150.4805 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 150.582 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 150.6914 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 150.793 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 150.8906 | 0.05 | 1.05 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 150.9922 | 0.06 | 1.06 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 151.1016 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 151.2031 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 151.3008 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 151.4023 | 0.03 | 1.03 | -0.82 | 0.18 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:12 | 151.5117 | -0.08 | 0.92 | -0.73 | 0.27 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 151.6133 | -0.13 | 0.87 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 151.7227 | -0.16 | 0.84 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 151.8203 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 151.9219 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 152.0234 | 0.03 | 1.03 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:12 | 152.1211 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 152.2305 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:12 | 152.332 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 152.4336 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 152.5313 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:12 | 152.6406 | 0.03 | 1.03 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 152.7422 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 152.8516 | 0.04 | 1.04 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:12 | 152.9531 | 0 | 1 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 153.0508 | -0.13 | 0.87 | -0.72 | 0.28 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 153.1523 | -0.16 | 0.84 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:12 | 153.25 | -0.1 | 0.9 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:12 | 153.3633 | 0.03 | 1.03 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 153.4609 | 0.03 | 1.03 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 153.5625 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 153.6602 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 153.7734 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 153.8711 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 153.9805 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 154.082 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 154.1836 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 154.2813 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 154.3828 | 0.03 | 1.03 | -0.84 | 0.16 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 154.4922 | -0.07 | 0.93 | -0.76 | 0.24 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 154.5938 | -0.14 | 0.86 | -0.7 | 0.3 | -0.68 | 0.32 | 69.34 | 27.34
2019-09-04 | 13:12 | 154.6914 | -0.15 | 0.85 | -0.68 | 0.32 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:12 | 154.8008 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 154.9023 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 155 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 155.1133 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 155.2109 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 155.3125 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 155.4102 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 155.5234 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 155.6211 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 155.7227 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 155.8203 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 155.9336 | 0 | 1 | -0.8 | 0.2 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 156.0313 | -0.09 | 0.91 | -0.75 | 0.25 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 156.1328 | -0.13 | 0.87 | -0.72 | 0.28 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:12 | 156.2422 | -0.16 | 0.84 | -0.68 | 0.32 | -0.67 | 0.33 | 69.34 | 26.37
2019-09-04 | 13:12 | 156.3438 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:12 | 156.4414 | 0.02 | 1.02 | -0.83 | 0.17 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:12 | 156.543 | 0.03 | 1.03 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 156.6523 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 156.75 | 0.02 | 1.02 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 156.8516 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 156.9609 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 157.0625 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 157.1602 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 157.2617 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 157.3633 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 28.32
2019-09-04 | 13:12 | 157.4727 | -0.07 | 0.93 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 157.5703 | -0.12 | 0.88 | -0.71 | 0.29 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 157.6719 | -0.13 | 0.87 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:12 | 157.7813 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 157.8828 | 0.01 | 1.01 | -0.83 | 0.17 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:12 | 157.9805 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 158.082 | 0.03 | 1.03 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 158.1914 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 158.293 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 158.3906 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 158.4922 | 0.03 | 1.03 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 158.6016 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 158.7031 | 0.01 | 1.01 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 158.8008 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:12 | 158.9102 | 0.02 | 1.02 | -0.81 | 0.19 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:12 | 159.0117 | -0.11 | 0.89 | -0.72 | 0.28 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 159.1133 | -0.15 | 0.85 | -0.7 | 0.3 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 159.2109 | -0.14 | 0.86 | -0.68 | 0.32 | -0.67 | 0.33 | 71.29 | 28.32
2019-09-04 | 13:12 | 159.3203 | 0 | 1 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 159.4219 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 159.5234 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 159.6211 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:12 | 159.7305 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 159.832 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 159.9414 | 0.04 | 1.04 | -0.84 | 0.16 | -0.71 | 0.29 | 74.22 | 26.37
2019-09-04 | 13:12 | 160.043 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 160.1406 | 0.04 | 1.04 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:12 | 160.2422 | 0.05 | 1.05 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 160.3516 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 160.4531 | -0.02 | 0.98 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 160.5508 | -0.13 | 0.87 | -0.73 | 0.27 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 160.6602 | -0.15 | 0.85 | -0.7 | 0.3 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 160.7617 | -0.15 | 0.85 | -0.68 | 0.32 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:12 | 160.8633 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 160.9727 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 161.0703 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 161.1719 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 161.2734 | 0.04 | 1.04 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 161.3711 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 161.4805 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 161.582 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 161.6836 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 161.7813 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 161.8906 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 161.9922 | -0.08 | 0.92 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 162.0938 | -0.13 | 0.87 | -0.71 | 0.29 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 162.2031 | -0.16 | 0.84 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 162.3008 | -0.01 | 0.99 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:12 | 162.4023 | 0.02 | 1.02 | -0.82 | 0.18 | -0.69 | 0.31 | 69.34 | 28.32
2019-09-04 | 13:12 | 162.5 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 162.6133 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 162.7109 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 162.8125 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 28.32
2019-09-04 | 13:12 | 162.9102 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 163.0234 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 163.1211 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 163.2227 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:12 | 163.3203 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 163.4336 | -0.01 | 0.99 | -0.81 | 0.19 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 163.5313 | -0.09 | 0.91 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 163.6328 | -0.15 | 0.85 | -0.7 | 0.3 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:12 | 163.7422 | -0.16 | 0.84 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:12 | 163.8438 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 163.9531 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 164.043 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:12 | 164.1523 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 164.25 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 164.3516 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 164.4531 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 164.5625 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 164.6602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 164.7617 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 164.8711 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 164.9727 | -0.06 | 0.94 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 165.0703 | -0.11 | 0.89 | -0.72 | 0.28 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 165.1719 | -0.14 | 0.86 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 165.2813 | -0.02 | 0.98 | -0.78 | 0.22 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 165.3828 | 0.01 | 1.01 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 165.4805 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 165.582 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 165.6914 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:12 | 165.793 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 165.9023 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:12 | 166 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 166.1016 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 166.2031 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 166.3008 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 166.4102 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 166.5117 | -0.08 | 0.92 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 166.6133 | -0.15 | 0.85 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 166.7227 | -0.14 | 0.86 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:12 | 166.8203 | 0 | 1 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:12 | 166.9219 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 167.0313 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 167.1328 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 167.2305 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 167.332 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 167.4414 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 167.543 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 25.39
2019-09-04 | 13:12 | 167.6406 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 167.7422 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 167.8516 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 167.9531 | -0.03 | 0.97 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 168.0508 | -0.11 | 0.89 | -0.72 | 0.28 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 168.1602 | -0.15 | 0.85 | -0.69 | 0.31 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:12 | 168.2617 | -0.15 | 0.85 | -0.68 | 0.32 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 13:12 | 168.3633 | 0 | 1 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 168.4609 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:12 | 168.5703 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 168.6719 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 168.7734 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 168.8828 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 168.9805 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 169.082 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 169.1836 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 169.2813 | 0.03 | 1.03 | -0.87 | 0.13 | -0.72 | 0.28 | 69.34 | 26.37
2019-09-04 | 13:12 | 169.3906 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 169.4922 | -0.05 | 0.95 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:12 | 169.5938 | -0.15 | 0.85 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:12 | 169.7031 | -0.14 | 0.86 | -0.73 | 0.27 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:12 | 169.8008 | -0.01 | 0.99 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:12 | 169.9023 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 170 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 170.1133 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 170.2109 | 0.02 | 1.02 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 170.3125 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:12 | 170.4102 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 170.5234 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 170.6211 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:12 | 170.7227 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:12 | 170.832 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 170.9336 | 0 | 1 | -0.8 | 0.2 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:12 | 171.0313 | -0.12 | 0.88 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 171.1328 | -0.15 | 0.85 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 171.2422 | -0.15 | 0.85 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 171.3438 | 0.01 | 1.01 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:12 | 171.4414 | 0.01 | 1.01 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 171.543 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:12 | 171.6523 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 171.75 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 171.8633 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:12 | 171.9609 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 172.0625 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 172.1602 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 172.2617 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 172.3711 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:12 | 172.4727 | 0 | 1 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 172.5703 | -0.12 | 0.88 | -0.74 | 0.26 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 172.6836 | -0.15 | 0.85 | -0.72 | 0.28 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:12 | 172.7813 | -0.06 | 0.94 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:12 | 172.8828 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 172.9922 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 173.0938 | 0.02 | 1.02 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 173.1914 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 173.293 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:12 | 173.4023 | 0.05 | 1.05 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 173.5 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:12 | 173.6016 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:12 | 173.7031 | 0.02 | 1.02 | -0.87 | 0.13 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:12 | 173.8125 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:12 | 173.9102 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 174.0117 | -0.1 | 0.9 | -0.76 | 0.24 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:12 | 174.1211 | -0.15 | 0.85 | -0.71 | 0.29 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 174.2227 | -0.17 | 0.83 | -0.71 | 0.29 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:12 | 174.3203 | -0.01 | 0.99 | -0.83 | 0.17 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:12 | 174.4219 | 0 | 1 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 174.5313 | 0 | 1 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:12 | 174.6328 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 174.7305 | 0.01 | 1.01 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 25.39
2019-09-04 | 13:12 | 174.832 | 0.02 | 1.02 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 174.9414 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 175.043 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:12 | 175.1406 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 175.2422 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 175.3516 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 175.4531 | -0.02 | 0.98 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 175.5508 | -0.13 | 0.87 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 13:12 | 175.6602 | -0.15 | 0.85 | -0.69 | 0.31 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:12 | 175.7617 | -0.15 | 0.85 | -0.7 | 0.3 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:12 | 175.8633 | 0.01 | 1.01 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:12 | 175.9727 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:12 | 176.0703 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 13:12 | 176.1719 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:12 | 176.2734 | 0.02 | 1.02 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:12 | 176.3828 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:12 | 176.4805 | 0.02 | 1.02 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:12 | 176.582 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 176.6836 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:12 | 176.793 | 0.03 | 1.03 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:12 | 176.8906 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:12 | 176.9922 | -0.05 | 0.95 | -0.79 | 0.21 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:12 | 177.0938 | -0.12 | 0.88 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:12 | 177.2031 | -0.16 | 0.84 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:12 | 177.3008 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 25.39
2019-09-04 | 13:13 | 177.4023 | 0.02 | 1.02 | -0.83 | 0.17 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 13:13 | 177.5117 | 0 | 1 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:13 | 177.6133 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 177.7109 | 0.03 | 1.03 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 177.8203 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 177.9219 | 0.02 | 1.02 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 178.0234 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 178.1211 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:13 | 178.2305 | 0.04 | 1.04 | -0.85 | 0.15 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:13 | 178.332 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 178.4336 | -0.01 | 0.99 | -0.82 | 0.18 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:13 | 178.543 | -0.11 | 0.89 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 178.6406 | -0.15 | 0.85 | -0.71 | 0.29 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 178.7422 | -0.17 | 0.83 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 178.8438 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 178.9531 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 179.0508 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 179.1523 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 179.25 | 0.02 | 1.02 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 179.3633 | 0.03 | 1.03 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 179.4609 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 179.5625 | 0.02 | 1.02 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:13 | 179.6602 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 179.7734 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:13 | 179.8711 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 179.9805 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 180.082 | -0.12 | 0.88 | -0.73 | 0.27 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 180.1836 | -0.18 | 0.82 | -0.7 | 0.3 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 180.2813 | -0.06 | 0.94 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:13 | 180.3828 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 180.4922 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 180.5938 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 180.6914 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:13 | 180.793 | 0 | 1 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:13 | 180.9023 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 181 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 181.1016 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 181.2109 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 181.3125 | 0.01 | 1.01 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 181.4102 | 0.01 | 1.01 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 181.5234 | -0.1 | 0.9 | -0.75 | 0.25 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 181.6211 | -0.15 | 0.85 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:13 | 181.7227 | -0.16 | 0.84 | -0.71 | 0.29 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 181.8203 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 181.9219 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 182.0313 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 182.1328 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 182.2305 | 0.01 | 1.01 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 182.3438 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 182.4414 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 182.543 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 182.6406 | 0.01 | 1.01 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 182.75 | 0.04 | 1.04 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 182.8516 | 0.03 | 1.03 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 25.39
2019-09-04 | 13:13 | 182.9609 | -0.04 | 0.96 | -0.8 | 0.2 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 183.0625 | -0.14 | 0.86 | -0.75 | 0.25 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 183.1602 | -0.18 | 0.82 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 183.2617 | -0.2 | 0.8 | -0.7 | 0.3 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:13 | 183.3711 | -0.06 | 0.94 | -0.83 | 0.17 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:13 | 183.4727 | -0.04 | 0.96 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 24.41
2019-09-04 | 13:13 | 183.5703 | -0.03 | 0.97 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 183.6719 | -0.03 | 0.97 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 183.7813 | -0.02 | 0.98 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 183.8828 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 13:13 | 183.9805 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 184.082 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:13 | 184.1914 | 0 | 1 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:13 | 184.293 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 184.3906 | 0.01 | 1.01 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 25.39
2019-09-04 | 13:13 | 184.5 | -0.07 | 0.93 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 184.6016 | -0.18 | 0.82 | -0.71 | 0.29 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:13 | 184.7031 | -0.2 | 0.8 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 184.8008 | -0.04 | 0.96 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 184.9102 | -0.01 | 0.99 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 185.0117 | -0.02 | 0.98 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 185.1133 | -0.02 | 0.98 | -0.84 | 0.16 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 185.2109 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 185.3203 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 185.4219 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 185.5234 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 185.6328 | 0 | 1 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:13 | 185.7305 | 0.04 | 1.04 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 185.832 | 0 | 1 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 185.9336 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 186.043 | -0.14 | 0.86 | -0.74 | 0.26 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 186.1406 | -0.15 | 0.85 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 186.2422 | -0.18 | 0.82 | -0.68 | 0.32 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 13:13 | 186.3438 | -0.01 | 0.99 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 186.4531 | -0.01 | 0.99 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:13 | 186.5508 | -0.01 | 0.99 | -0.85 | 0.15 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:13 | 186.6523 | 0.01 | 1.01 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 186.75 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 186.8633 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 186.9609 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 187.0625 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 187.1719 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 187.2734 | 0.01 | 1.01 | -0.84 | 0.16 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 187.3711 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:13 | 187.4727 | -0.06 | 0.94 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 187.582 | -0.15 | 0.85 | -0.72 | 0.28 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 187.6836 | -0.15 | 0.85 | -0.71 | 0.29 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:13 | 187.7813 | -0.13 | 0.87 | -0.72 | 0.28 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 187.8828 | -0.02 | 0.98 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 187.9922 | -0.01 | 0.99 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 188.0938 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 188.2031 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 188.3008 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 188.4023 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 188.5 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:13 | 188.6016 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:13 | 188.7109 | 0.01 | 1.01 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 188.8125 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 188.9102 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 189.0117 | -0.08 | 0.92 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 189.1211 | -0.15 | 0.85 | -0.71 | 0.29 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 189.2227 | -0.17 | 0.83 | -0.69 | 0.31 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 189.332 | -0.02 | 0.98 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 189.4336 | -0.02 | 0.98 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 189.5313 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 189.6328 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 189.7422 | 0.01 | 1.01 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 189.8438 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 189.9531 | 0.01 | 1.01 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:13 | 190.043 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 190.1523 | 0 | 1 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 25.39
2019-09-04 | 13:13 | 190.25 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 190.3516 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 190.4609 | -0.05 | 0.95 | -0.8 | 0.2 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:13 | 190.5625 | -0.14 | 0.86 | -0.73 | 0.27 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 190.6602 | -0.17 | 0.83 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 190.7617 | -0.18 | 0.82 | -0.69 | 0.31 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:13 | 190.8711 | -0.02 | 0.98 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 190.9727 | -0.01 | 0.99 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 191.0703 | -0.01 | 0.99 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 191.1719 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 191.2813 | 0 | 1 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 191.3828 | 0 | 1 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:13 | 191.4805 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 191.582 | 0.02 | 1.02 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:13 | 191.6914 | 0.01 | 1.01 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 191.793 | 0.01 | 1.01 | -0.85 | 0.15 | -0.72 | 0.28 | 73.24 | 28.32
2019-09-04 | 13:13 | 191.8906 | 0.03 | 1.03 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:13 | 192 | -0.04 | 0.96 | -0.8 | 0.2 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 192.1016 | -0.15 | 0.85 | -0.72 | 0.28 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 192.2031 | -0.18 | 0.82 | -0.7 | 0.3 | -0.69 | 0.31 | 69.34 | 25.39
2019-09-04 | 13:13 | 192.3008 | -0.05 | 0.95 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:13 | 192.4102 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 192.5117 | -0.02 | 0.98 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 192.6133 | -0.01 | 0.99 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 192.7227 | -0.01 | 0.99 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 192.8203 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 192.9219 | 0 | 1 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:13 | 193.0234 | 0.02 | 1.02 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 193.1328 | 0.01 | 1.01 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 193.2305 | 0 | 1 | -0.84 | 0.16 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:13 | 193.332 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 193.4336 | 0 | 1 | -0.83 | 0.17 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:13 | 193.543 | -0.12 | 0.88 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 193.6406 | -0.17 | 0.83 | -0.72 | 0.28 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:13 | 193.7422 | -0.18 | 0.82 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 25.39
2019-09-04 | 13:13 | 193.8438 | -0.02 | 0.98 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 193.9609 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 194.0625 | -0.01 | 0.99 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 25.39
2019-09-04 | 13:13 | 194.1602 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:13 | 194.2617 | -0.02 | 0.98 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 194.3633 | 0 | 1 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 194.4609 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 194.5625 | -0.02 | 0.98 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 194.6719 | 0 | 1 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:13 | 194.7734 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 194.8711 | 0.01 | 1.01 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:13 | 194.9805 | -0.03 | 0.97 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 195.082 | -0.14 | 0.86 | -0.72 | 0.28 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 195.1836 | -0.15 | 0.85 | -0.69 | 0.31 | -0.68 | 0.32 | 69.34 | 25.39
2019-09-04 | 13:13 | 195.2813 | -0.17 | 0.83 | -0.72 | 0.28 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:13 | 195.3906 | -0.02 | 0.98 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 195.4922 | 0.01 | 1.01 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:13 | 195.5938 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 195.7031 | 0.02 | 1.02 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 195.8008 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 195.9023 | 0.03 | 1.03 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 196 | 0.03 | 1.03 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 196.1016 | 0.02 | 1.02 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:13 | 196.2109 | 0.01 | 1.01 | -0.86 | 0.14 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 196.3125 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 196.4219 | 0 | 1 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 196.5234 | -0.09 | 0.91 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 196.6211 | -0.16 | 0.84 | -0.71 | 0.29 | -0.68 | 0.32 | 70.31 | 25.39
2019-09-04 | 13:13 | 196.7227 | -0.18 | 0.82 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:13 | 196.832 | -0.04 | 0.96 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 196.9336 | -0.03 | 0.97 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 197.0313 | 0.01 | 1.01 | -0.83 | 0.17 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 197.1328 | 0 | 1 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 197.2422 | -0.02 | 0.98 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 197.3438 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 197.4414 | 0.02 | 1.02 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 197.5508 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 197.6523 | 0.01 | 1.01 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 197.75 | 0.02 | 1.02 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 197.8516 | 0.02 | 1.02 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:13 | 197.9609 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 198.0625 | -0.12 | 0.88 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 198.1719 | -0.14 | 0.86 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 198.2617 | -0.2 | 0.8 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 25.39
2019-09-04 | 13:13 | 198.3711 | -0.03 | 0.97 | -0.92 | 0.08 | -0.69 | 0.31 | 69.34 | 25.39
2019-09-04 | 13:13 | 198.4727 | 0 | 1 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 198.582 | -0.01 | 0.99 | -0.89 | 0.11 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:13 | 198.6719 | 0.01 | 1.01 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:13 | 198.7813 | 0 | 1 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 198.8828 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 198.9805 | 0 | 1 | -0.87 | 0.13 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 199.0938 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 199.1914 | 0 | 1 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 199.293 | 0.01 | 1.01 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 199.3906 | 0 | 1 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:13 | 199.5 | -0.06 | 0.94 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 199.6016 | -0.14 | 0.86 | -0.76 | 0.24 | -0.68 | 0.32 | 69.34 | 27.34
2019-09-04 | 13:13 | 199.7031 | -0.18 | 0.82 | -0.77 | 0.23 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:13 | 199.8125 | -0.04 | 0.96 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 199.9102 | -0.01 | 0.99 | -0.9 | 0.1 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 13:13 | 200.0117 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:13 | 200.1211 | 0.01 | 1.01 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 200.2227 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 200.3203 | 0 | 1 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 200.4219 | 0.01 | 1.01 | -0.87 | 0.13 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 200.5313 | 0 | 1 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 200.6328 | 0.01 | 1.01 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 200.7305 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 200.832 | 0 | 1 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:13 | 200.9336 | 0.03 | 1.03 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 201.043 | -0.1 | 0.9 | -0.79 | 0.21 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:13 | 201.1406 | -0.16 | 0.84 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 201.25 | -0.19 | 0.81 | -0.82 | 0.18 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:13 | 201.3516 | -0.03 | 0.97 | -0.94 | 0.06 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 201.4531 | -0.01 | 0.99 | -0.93 | 0.07 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 201.5508 | -0.01 | 0.99 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 201.6602 | 0 | 1 | -0.88 | 0.12 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:13 | 201.7617 | 0.02 | 1.02 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 201.8633 | 0.01 | 1.01 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 201.9727 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 202.0625 | 0.03 | 1.03 | -0.88 | 0.12 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 202.1719 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 202.2734 | 0 | 1 | -0.88 | 0.12 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:13 | 202.3711 | 0.02 | 1.02 | -0.87 | 0.13 | -0.71 | 0.29 | 69.34 | 26.37
2019-09-04 | 13:13 | 202.4805 | -0.03 | 0.97 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 202.582 | -0.12 | 0.88 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:13 | 202.6836 | -0.16 | 0.84 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 202.793 | -0.14 | 0.86 | -0.78 | 0.22 | -0.68 | 0.32 | 69.34 | 27.34
2019-09-04 | 13:13 | 202.8906 | -0.02 | 0.98 | -0.91 | 0.09 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 202.9922 | 0 | 1 | -0.9 | 0.1 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:13 | 203.0938 | 0 | 1 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 203.2031 | 0.01 | 1.01 | -0.89 | 0.11 | -0.7 | 0.3 | 72.27 | 25.39
2019-09-04 | 13:13 | 203.3008 | 0.01 | 1.01 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 203.4023 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:13 | 203.5 | 0.02 | 1.02 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 203.6133 | 0 | 1 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 203.7109 | 0.01 | 1.01 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 203.8125 | 0.02 | 1.02 | -0.87 | 0.13 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:13 | 203.9219 | 0.01 | 1.01 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 204.0234 | -0.09 | 0.91 | -0.81 | 0.19 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 204.1211 | -0.17 | 0.83 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:13 | 204.2227 | -0.18 | 0.82 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:13 | 204.332 | -0.03 | 0.97 | -0.94 | 0.06 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 204.4336 | -0.02 | 0.98 | -0.91 | 0.09 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 204.5313 | -0.02 | 0.98 | -0.9 | 0.1 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 204.6406 | -0.03 | 0.97 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 204.7422 | 0.01 | 1.01 | -0.9 | 0.1 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 204.8438 | 0 | 1 | -0.89 | 0.11 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 204.9531 | -0.02 | 0.98 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 205.0508 | 0 | 1 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 205.1523 | 0 | 1 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 205.25 | 0.01 | 1.01 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 205.3516 | 0.01 | 1.01 | -0.89 | 0.11 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 205.4609 | -0.01 | 0.99 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 205.5625 | -0.14 | 0.86 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 25.39
2019-09-04 | 13:13 | 205.6602 | -0.18 | 0.82 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 205.7734 | -0.17 | 0.83 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 205.8711 | -0.03 | 0.97 | -0.93 | 0.07 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 205.9727 | 0.01 | 1.01 | -0.92 | 0.08 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 206.082 | 0 | 1 | -0.9 | 0.1 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 206.1836 | 0.01 | 1.01 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 206.2813 | 0.02 | 1.02 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:13 | 206.3828 | -0.02 | 0.98 | -0.88 | 0.12 | -0.69 | 0.31 | 69.34 | 25.39
2019-09-04 | 13:13 | 206.4805 | 0 | 1 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 206.5938 | 0.01 | 1.01 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 206.6914 | 0 | 1 | -0.88 | 0.12 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 206.793 | 0.03 | 1.03 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 206.8906 | 0.01 | 1.01 | -0.88 | 0.12 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:13 | 207 | -0.1 | 0.9 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:13 | 207.1016 | -0.17 | 0.83 | -0.8 | 0.2 | -0.68 | 0.32 | 71.29 | 25.39
2019-09-04 | 13:13 | 207.2109 | -0.17 | 0.83 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:13 | 207.3125 | -0.07 | 0.93 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 207.4102 | -0.03 | 0.97 | -0.91 | 0.09 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 207.5117 | 0 | 1 | -0.9 | 0.1 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 207.6211 | -0.01 | 0.99 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 207.7227 | 0 | 1 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 25.39
2019-09-04 | 13:13 | 207.8203 | 0.01 | 1.01 | -0.89 | 0.11 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 207.9219 | 0.02 | 1.02 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 208.0234 | 0.01 | 1.01 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:13 | 208.1328 | 0.01 | 1.01 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 208.2305 | 0.02 | 1.02 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 208.332 | 0.04 | 1.04 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 208.4414 | -0.02 | 0.98 | -0.86 | 0.14 | -0.69 | 0.31 | 69.34 | 27.34
2019-09-04 | 13:13 | 208.543 | -0.12 | 0.88 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 208.6406 | -0.16 | 0.84 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 208.75 | -0.19 | 0.81 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:13 | 208.8516 | -0.03 | 0.97 | -0.92 | 0.08 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:13 | 208.9531 | -0.01 | 0.99 | -0.91 | 0.09 | -0.69 | 0.31 | 71.29 | 25.39
2019-09-04 | 13:13 | 209.0508 | 0 | 1 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 209.1523 | 0.01 | 1.01 | -0.9 | 0.1 | -0.69 | 0.31 | 71.29 | 25.39
2019-09-04 | 13:13 | 209.2617 | 0 | 1 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 209.3633 | 0.03 | 1.03 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:13 | 209.4727 | 0 | 1 | -0.88 | 0.12 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:13 | 209.5703 | 0 | 1 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 209.6719 | 0.01 | 1.01 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 209.7734 | 0.04 | 1.04 | -0.87 | 0.13 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:13 | 209.8828 | 0.02 | 1.02 | -0.87 | 0.13 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:13 | 209.9805 | -0.06 | 0.94 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 210.082 | -0.15 | 0.85 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 210.1836 | -0.17 | 0.83 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 210.293 | -0.19 | 0.81 | -0.77 | 0.23 | -0.67 | 0.33 | 70.31 | 27.34
2019-09-04 | 13:13 | 210.3906 | -0.04 | 0.96 | -0.91 | 0.09 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:13 | 210.4922 | -0.02 | 0.98 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 210.6016 | 0 | 1 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 210.7031 | 0.01 | 1.01 | -0.88 | 0.12 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:13 | 210.8008 | 0.01 | 1.01 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:13 | 210.9023 | 0.01 | 1.01 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 211.0117 | 0.03 | 1.03 | -0.87 | 0.13 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:13 | 211.1133 | 0 | 1 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 211.2109 | 0 | 1 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 211.3125 | 0.01 | 1.01 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:13 | 211.4219 | 0.02 | 1.02 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 211.5234 | -0.09 | 0.91 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 211.6211 | -0.17 | 0.83 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 211.7305 | -0.17 | 0.83 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 211.832 | -0.05 | 0.95 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 211.9336 | -0.02 | 0.98 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 212.043 | -0.01 | 0.99 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 212.1406 | 0.01 | 1.01 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 212.2422 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 212.3438 | 0.01 | 1.01 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 212.4414 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 212.5508 | 0.02 | 1.02 | -0.88 | 0.12 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:13 | 212.6523 | 0.01 | 1.01 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:13 | 212.75 | 0.04 | 1.04 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 212.8516 | 0.03 | 1.03 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 212.9727 | -0.01 | 0.99 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 213.0625 | -0.13 | 0.87 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 213.1719 | -0.18 | 0.82 | -0.78 | 0.22 | -0.67 | 0.33 | 69.34 | 27.34
2019-09-04 | 13:13 | 213.2734 | -0.18 | 0.82 | -0.77 | 0.23 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 213.3711 | -0.02 | 0.98 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 213.4727 | -0.01 | 0.99 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 213.582 | 0.01 | 1.01 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 213.6836 | 0.01 | 1.01 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 27.34
2019-09-04 | 13:13 | 213.7813 | 0.01 | 1.01 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 213.8828 | 0.01 | 1.01 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 213.9922 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 214.0938 | 0.01 | 1.01 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 214.1914 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 214.3008 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 214.4023 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 214.5 | -0.06 | 0.94 | -0.8 | 0.2 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:13 | 214.6016 | -0.17 | 0.83 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 214.7109 | -0.18 | 0.82 | -0.77 | 0.23 | -0.66 | 0.34 | 71.29 | 28.32
2019-09-04 | 13:13 | 214.8125 | -0.13 | 0.87 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 25.39
2019-09-04 | 13:13 | 214.9102 | -0.02 | 0.98 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 215.0117 | 0 | 1 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 215.1211 | -0.01 | 0.99 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 215.2227 | 0 | 1 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 215.3203 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 215.4336 | 0 | 1 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:13 | 215.5313 | 0.01 | 1.01 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 215.6328 | 0.01 | 1.01 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 215.7305 | 0.03 | 1.03 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:13 | 215.8438 | 0 | 1 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:13 | 215.9531 | 0.01 | 1.01 | -0.83 | 0.17 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:13 | 216.043 | -0.09 | 0.91 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 216.1406 | -0.18 | 0.82 | -0.74 | 0.26 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 216.25 | -0.18 | 0.82 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 216.3516 | -0.02 | 0.98 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 28.32
2019-09-04 | 13:13 | 216.4531 | -0.04 | 0.96 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 216.5625 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:13 | 216.6602 | 0.01 | 1.01 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 216.7617 | 0 | 1 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 216.8633 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 216.9727 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 217.0703 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 217.1719 | 0.03 | 1.03 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 217.2734 | 0.01 | 1.01 | -0.87 | 0.13 | -0.71 | 0.29 | 73.24 | 27.34
2019-09-04 | 13:13 | 217.3828 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 217.4805 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 217.5938 | -0.14 | 0.86 | -0.77 | 0.23 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 217.6914 | -0.17 | 0.83 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:13 | 217.793 | -0.2 | 0.8 | -0.75 | 0.25 | -0.67 | 0.33 | 70.31 | 25.39
2019-09-04 | 13:13 | 217.8906 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 218 | 0 | 1 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 218.1016 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 218.2031 | -0.01 | 0.99 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:13 | 218.3008 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:13 | 218.4023 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 218.5117 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 218.6133 | 0 | 1 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 218.7109 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 218.8203 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:13 | 218.9219 | -0.01 | 0.99 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 219.0234 | -0.08 | 0.92 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 219.1328 | -0.18 | 0.82 | -0.73 | 0.27 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 219.2305 | -0.2 | 0.8 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:13 | 219.332 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 219.4336 | -0.02 | 0.98 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 219.5313 | -0.01 | 0.99 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:13 | 219.6406 | -0.01 | 0.99 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 219.7422 | -0.01 | 0.99 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 219.8438 | -0.01 | 0.99 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 219.9531 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 220.0508 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 220.1523 | 0.02 | 1.02 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 13:13 | 220.2617 | -0.01 | 0.99 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 220.3633 | -0.02 | 0.98 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:13 | 220.4609 | -0.03 | 0.97 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 220.5625 | -0.15 | 0.85 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 220.6719 | -0.17 | 0.83 | -0.76 | 0.24 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:13 | 220.7734 | -0.21 | 0.79 | -0.77 | 0.23 | -0.67 | 0.33 | 69.34 | 26.37
2019-09-04 | 13:13 | 220.8711 | -0.04 | 0.96 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 220.9805 | -0.03 | 0.97 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 221.082 | -0.03 | 0.97 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 221.1836 | -0.01 | 0.99 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 29.3
2019-09-04 | 13:13 | 221.2813 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 221.3906 | -0.01 | 0.99 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 221.4922 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 29.3
2019-09-04 | 13:13 | 221.5938 | 0 | 1 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:13 | 221.6914 | -0.02 | 0.98 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 221.8008 | 0 | 1 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 221.9023 | -0.01 | 0.99 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 222 | -0.08 | 0.92 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 222.1016 | -0.15 | 0.85 | -0.77 | 0.23 | -0.7 | 0.3 | 70.31 | 29.3
2019-09-04 | 13:13 | 222.2109 | -0.2 | 0.8 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:13 | 222.3125 | -0.13 | 0.87 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:13 | 222.4102 | -0.03 | 0.97 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 222.5234 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 222.6211 | -0.02 | 0.98 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 222.7227 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 222.8203 | 0 | 1 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 222.9336 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 223.0313 | -0.02 | 0.98 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 223.1328 | 0.01 | 1.01 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 223.2305 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 223.3438 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:13 | 223.4414 | 0.01 | 1.01 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 223.543 | -0.1 | 0.9 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 223.6523 | -0.16 | 0.84 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 13:13 | 223.75 | -0.17 | 0.83 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 26.37
2019-09-04 | 13:13 | 223.8516 | -0.04 | 0.96 | -0.89 | 0.11 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:13 | 223.9727 | -0.04 | 0.96 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 224.0625 | -0.03 | 0.97 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 224.1602 | 0.01 | 1.01 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 224.2617 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:13 | 224.3633 | 0.02 | 1.02 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:13 | 224.4727 | -0.01 | 0.99 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 224.5703 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 224.6836 | 0 | 1 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:13 | 224.7813 | 0 | 1 | -0.86 | 0.14 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:13 | 224.8828 | 0.02 | 1.02 | -0.86 | 0.14 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:13 | 224.9805 | -0.04 | 0.96 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 225.0938 | -0.14 | 0.86 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 13:13 | 225.1914 | -0.17 | 0.83 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:13 | 225.293 | -0.2 | 0.8 | -0.75 | 0.25 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 225.3906 | -0.04 | 0.96 | -0.89 | 0.11 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:13 | 225.4922 | -0.02 | 0.98 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 225.6016 | -0.03 | 0.97 | -0.87 | 0.13 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:13 | 225.7031 | -0.02 | 0.98 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 225.8125 | -0.02 | 0.98 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 225.9102 | 0 | 1 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 226.0117 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:13 | 226.1133 | 0 | 1 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 226.2227 | 0 | 1 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 226.3203 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 226.4219 | 0 | 1 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 226.5234 | -0.11 | 0.89 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 226.6328 | -0.17 | 0.83 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 226.7305 | -0.2 | 0.8 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 226.832 | -0.07 | 0.93 | -0.91 | 0.09 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 226.9414 | -0.01 | 0.99 | -0.92 | 0.08 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 227.043 | -0.04 | 0.96 | -0.9 | 0.1 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 227.1406 | -0.03 | 0.97 | -0.9 | 0.1 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 227.2422 | -0.01 | 0.99 | -0.89 | 0.11 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 227.3516 | -0.01 | 0.99 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 227.4531 | -0.02 | 0.98 | -0.88 | 0.12 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:13 | 227.5508 | -0.02 | 0.98 | -0.88 | 0.12 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:13 | 227.6523 | 0.01 | 1.01 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 227.7617 | 0 | 1 | -0.88 | 0.12 | -0.71 | 0.29 | 71.29 | 29.3
2019-09-04 | 13:13 | 227.8633 | 0 | 1 | -0.88 | 0.12 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 227.9727 | -0.02 | 0.98 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 228.0703 | -0.11 | 0.89 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 228.1719 | -0.18 | 0.82 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 13:13 | 228.2734 | -0.19 | 0.81 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:13 | 228.3711 | -0.05 | 0.95 | -0.93 | 0.07 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 228.4805 | -0.04 | 0.96 | -0.92 | 0.08 | -0.67 | 0.33 | 72.27 | 28.32
2019-09-04 | 13:13 | 228.582 | -0.01 | 0.99 | -0.91 | 0.09 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 228.6836 | -0.02 | 0.98 | -0.9 | 0.1 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 228.7813 | 0 | 1 | -0.9 | 0.1 | -0.71 | 0.29 | 70.31 | 28.32
2019-09-04 | 13:13 | 228.8906 | -0.01 | 0.99 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 228.9922 | 0 | 1 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 229.0938 | -0.01 | 0.99 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 229.1914 | 0 | 1 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 229.3008 | -0.01 | 0.99 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 229.4023 | 0 | 1 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:13 | 229.5117 | -0.04 | 0.96 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 229.6133 | -0.15 | 0.85 | -0.81 | 0.19 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 13:13 | 229.7109 | -0.18 | 0.82 | -0.8 | 0.2 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 13:13 | 229.8125 | -0.19 | 0.81 | -0.8 | 0.2 | -0.66 | 0.34 | 71.29 | 28.32
2019-09-04 | 13:13 | 229.9102 | -0.03 | 0.97 | -0.93 | 0.07 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:13 | 230.0234 | 0 | 1 | -0.91 | 0.09 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 230.1211 | 0 | 1 | -0.9 | 0.1 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 230.2227 | -0.02 | 0.98 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 230.3203 | -0.01 | 0.99 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 230.4336 | -0.02 | 0.98 | -0.89 | 0.11 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 13:13 | 230.5313 | 0.02 | 1.02 | -0.9 | 0.1 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 13:13 | 230.6406 | -0.01 | 0.99 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 230.7422 | 0 | 1 | -0.9 | 0.1 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 230.8438 | -0.02 | 0.98 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 230.9531 | 0.01 | 1.01 | -0.88 | 0.12 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 231.0508 | -0.07 | 0.93 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 231.1523 | -0.18 | 0.82 | -0.81 | 0.19 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:13 | 231.25 | -0.21 | 0.79 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:13 | 231.3516 | -0.05 | 0.95 | -0.94 | 0.06 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 231.4531 | -0.02 | 0.98 | -0.92 | 0.08 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 231.5625 | -0.02 | 0.98 | -0.91 | 0.09 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:13 | 231.6602 | -0.02 | 0.98 | -0.91 | 0.09 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 231.7734 | -0.01 | 0.99 | -0.91 | 0.09 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 231.8711 | 0 | 1 | -0.9 | 0.1 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:13 | 231.9727 | -0.02 | 0.98 | -0.89 | 0.11 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:13 | 232.0703 | -0.01 | 0.99 | -0.9 | 0.1 | -0.72 | 0.28 | 71.29 | 28.32
2019-09-04 | 13:13 | 232.1836 | -0.01 | 0.99 | -0.9 | 0.1 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:13 | 232.2813 | -0.01 | 0.99 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 232.3828 | 0 | 1 | -0.89 | 0.11 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 232.4805 | -0.02 | 0.98 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 232.5938 | -0.12 | 0.88 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:13 | 232.6914 | -0.19 | 0.81 | -0.8 | 0.2 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:13 | 232.793 | -0.21 | 0.79 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:13 | 232.9023 | -0.08 | 0.92 | -0.92 | 0.08 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:13 | 233 | -0.04 | 0.96 | -0.92 | 0.08 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 233.1016 | -0.04 | 0.96 | -0.89 | 0.11 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:13 | 233.2031 | -0.04 | 0.96 | -0.89 | 0.11 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 233.3125 | -0.03 | 0.97 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 233.4102 | -0.03 | 0.97 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 233.5117 | -0.03 | 0.97 | -0.89 | 0.11 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 233.6133 | -0.04 | 0.96 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 233.7227 | -0.04 | 0.96 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 233.8203 | -0.02 | 0.98 | -0.89 | 0.11 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:13 | 233.9219 | -0.04 | 0.96 | -0.9 | 0.1 | -0.7 | 0.3 | 73.24 | 27.34
2019-09-04 | 13:13 | 234.0313 | -0.08 | 0.92 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 234.1328 | -0.2 | 0.8 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 234.2305 | -0.22 | 0.78 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:13 | 234.332 | -0.09 | 0.91 | -0.9 | 0.1 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:13 | 234.4414 | -0.08 | 0.92 | -0.92 | 0.08 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 234.543 | -0.06 | 0.94 | -0.92 | 0.08 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:13 | 234.6406 | -0.05 | 0.95 | -0.9 | 0.1 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:13 | 234.7422 | -0.04 | 0.96 | -0.9 | 0.1 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:13 | 234.8516 | -0.04 | 0.96 | -0.9 | 0.1 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 234.9609 | -0.04 | 0.96 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:13 | 235.0508 | -0.04 | 0.96 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:13 | 235.1602 | -0.03 | 0.97 | -0.9 | 0.1 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 235.2617 | -0.03 | 0.97 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 235.3633 | -0.04 | 0.96 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:13 | 235.4727 | -0.05 | 0.95 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:13 | 235.5703 | -0.14 | 0.86 | -0.81 | 0.19 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:13 | 235.6719 | -0.2 | 0.8 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:13 | 235.7734 | -0.22 | 0.78 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:13 | 235.8711 | -0.08 | 0.92 | -0.93 | 0.07 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:13 | 235.9805 | -0.07 | 0.93 | -0.91 | 0.09 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:13 | 236.082 | -0.04 | 0.96 | -0.9 | 0.1 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:13 | 236.1836 | -0.03 | 0.97 | -0.9 | 0.1 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:13 | 236.293 | -0.03 | 0.97 | -0.9 | 0.1 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 236.3906 | -0.04 | 0.96 | -0.89 | 0.11 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:14 | 236.4922 | -0.04 | 0.96 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 236.6016 | -0.04 | 0.96 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 236.7031 | -0.03 | 0.97 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 236.8008 | 0 | 1 | -0.89 | 0.11 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:14 | 236.9023 | -0.03 | 0.97 | -0.9 | 0.1 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:14 | 237.0117 | -0.07 | 0.93 | -0.86 | 0.14 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:14 | 237.1133 | -0.18 | 0.82 | -0.81 | 0.19 | -0.7 | 0.3 | 69.34 | 25.39
2019-09-04 | 13:14 | 237.2109 | -0.19 | 0.81 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 237.3125 | -0.2 | 0.8 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 237.4102 | -0.05 | 0.95 | -0.91 | 0.09 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 237.5234 | -0.04 | 0.96 | -0.91 | 0.09 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 237.6211 | -0.03 | 0.97 | -0.91 | 0.09 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 237.7305 | -0.02 | 0.98 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 237.832 | -0.03 | 0.97 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 237.9336 | -0.02 | 0.98 | -0.89 | 0.11 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 238.0313 | 0.02 | 1.02 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 238.1406 | -0.02 | 0.98 | -0.89 | 0.11 | -0.72 | 0.28 | 71.29 | 25.39
2019-09-04 | 13:14 | 238.2422 | -0.02 | 0.98 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 238.3438 | -0.03 | 0.97 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 238.4414 | -0.02 | 0.98 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 238.5508 | -0.11 | 0.89 | -0.81 | 0.19 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 238.6523 | -0.19 | 0.81 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 238.75 | -0.23 | 0.77 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 238.8633 | -0.07 | 0.93 | -0.89 | 0.11 | -0.68 | 0.32 | 72.27 | 25.39
2019-09-04 | 13:14 | 238.9609 | -0.04 | 0.96 | -0.91 | 0.09 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 239.0625 | -0.05 | 0.95 | -0.9 | 0.1 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:14 | 239.1602 | -0.04 | 0.96 | -0.9 | 0.1 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 239.2734 | -0.04 | 0.96 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 239.3711 | -0.03 | 0.97 | -0.9 | 0.1 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 239.4727 | -0.03 | 0.97 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 239.5703 | -0.02 | 0.98 | -0.89 | 0.11 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 239.6836 | -0.03 | 0.97 | -0.88 | 0.12 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 239.7813 | -0.03 | 0.97 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 239.8906 | -0.01 | 0.99 | -0.89 | 0.11 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 239.9922 | -0.06 | 0.94 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 240.0938 | -0.17 | 0.83 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 240.1914 | -0.21 | 0.79 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 240.293 | -0.22 | 0.78 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 240.4023 | -0.06 | 0.94 | -0.91 | 0.09 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 240.5 | -0.03 | 0.97 | -0.9 | 0.1 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:14 | 240.6016 | -0.03 | 0.97 | -0.89 | 0.11 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 240.7109 | -0.02 | 0.98 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 240.8125 | -0.04 | 0.96 | -0.89 | 0.11 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 240.9102 | -0.05 | 0.95 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 241.0234 | -0.05 | 0.95 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 241.1211 | -0.03 | 0.97 | -0.89 | 0.11 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 241.2227 | -0.05 | 0.95 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 30.27
2019-09-04 | 13:14 | 241.3203 | -0.05 | 0.95 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 241.4219 | -0.04 | 0.96 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 241.5313 | -0.09 | 0.91 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 241.6328 | -0.17 | 0.83 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:14 | 241.7305 | -0.22 | 0.78 | -0.76 | 0.24 | -0.67 | 0.33 | 70.31 | 27.34
2019-09-04 | 13:14 | 241.832 | -0.12 | 0.88 | -0.83 | 0.17 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 241.9414 | -0.05 | 0.95 | -0.9 | 0.1 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 242.043 | -0.05 | 0.95 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 242.1523 | -0.04 | 0.96 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 242.25 | -0.04 | 0.96 | -0.89 | 0.11 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 242.3516 | -0.04 | 0.96 | -0.89 | 0.11 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 242.4531 | 0.01 | 1.01 | -0.88 | 0.12 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:14 | 242.5625 | -0.03 | 0.97 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 242.6602 | -0.05 | 0.95 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 242.7617 | -0.04 | 0.96 | -0.88 | 0.12 | -0.72 | 0.28 | 71.29 | 27.34
2019-09-04 | 13:14 | 242.8633 | -0.05 | 0.95 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 242.9727 | -0.06 | 0.94 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 243.0703 | -0.12 | 0.88 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 243.1719 | -0.2 | 0.8 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 243.2813 | -0.22 | 0.78 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 243.3828 | -0.06 | 0.94 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 243.4805 | -0.05 | 0.95 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 243.5938 | -0.05 | 0.95 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:14 | 243.6914 | -0.05 | 0.95 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:14 | 243.793 | -0.03 | 0.97 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 243.8906 | -0.04 | 0.96 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 244 | -0.03 | 0.97 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 244.1016 | -0.02 | 0.98 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 244.2031 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 244.3008 | -0.04 | 0.96 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 244.4023 | -0.02 | 0.98 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 244.5117 | -0.07 | 0.93 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 244.6133 | -0.16 | 0.84 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:14 | 244.7109 | -0.2 | 0.8 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:14 | 244.8203 | -0.22 | 0.78 | -0.71 | 0.29 | -0.66 | 0.34 | 69.34 | 26.37
2019-09-04 | 13:14 | 244.9219 | -0.07 | 0.93 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 245.0234 | -0.05 | 0.95 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 245.1211 | -0.02 | 0.98 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:14 | 245.2305 | -0.04 | 0.96 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 245.332 | -0.03 | 0.97 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 245.4336 | -0.02 | 0.98 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:14 | 245.5313 | -0.03 | 0.97 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 245.6406 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:14 | 245.7422 | -0.03 | 0.97 | -0.88 | 0.12 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 245.8438 | -0.02 | 0.98 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 245.9531 | -0.03 | 0.97 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 246.0508 | -0.1 | 0.9 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 246.1523 | -0.19 | 0.81 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:14 | 246.25 | -0.17 | 0.83 | -0.72 | 0.28 | -0.69 | 0.31 | 69.34 | 25.39
2019-09-04 | 13:14 | 246.3633 | -0.08 | 0.92 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 246.4609 | -0.03 | 0.97 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 246.5625 | -0.04 | 0.96 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 246.6602 | -0.05 | 0.95 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 246.7734 | -0.04 | 0.96 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 246.8711 | -0.03 | 0.97 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 246.9805 | -0.03 | 0.97 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 247.082 | -0.02 | 0.98 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 247.1836 | -0.04 | 0.96 | -0.87 | 0.13 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 247.2813 | -0.02 | 0.98 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 247.3828 | -0.02 | 0.98 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:14 | 247.4922 | -0.06 | 0.94 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 247.5938 | -0.13 | 0.87 | -0.78 | 0.22 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 247.6914 | -0.17 | 0.83 | -0.73 | 0.27 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:14 | 247.8008 | -0.22 | 0.78 | -0.7 | 0.3 | -0.67 | 0.33 | 71.29 | 27.34
2019-09-04 | 13:14 | 247.9023 | -0.07 | 0.93 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 248 | -0.04 | 0.96 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 248.1133 | -0.05 | 0.95 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 248.2109 | -0.03 | 0.97 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 248.3125 | -0.02 | 0.98 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 248.4102 | -0.03 | 0.97 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 248.5234 | -0.02 | 0.98 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 248.6211 | -0.04 | 0.96 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 248.7227 | -0.03 | 0.97 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 248.8203 | -0.03 | 0.97 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 248.9336 | 0 | 1 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 249.0313 | -0.11 | 0.89 | -0.8 | 0.2 | -0.71 | 0.29 | 69.34 | 27.34
2019-09-04 | 13:14 | 249.1328 | -0.2 | 0.8 | -0.72 | 0.28 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 249.2422 | -0.2 | 0.8 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:14 | 249.3438 | -0.14 | 0.86 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 25.39
2019-09-04 | 13:14 | 249.4414 | -0.02 | 0.98 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 249.543 | -0.04 | 0.96 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 249.6523 | -0.05 | 0.95 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 13:14 | 249.75 | -0.03 | 0.97 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 249.8516 | -0.06 | 0.94 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 249.9609 | -0.01 | 0.99 | -0.87 | 0.13 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:14 | 250.0625 | -0.03 | 0.97 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 250.1602 | -0.04 | 0.96 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 250.2617 | -0.05 | 0.95 | -0.86 | 0.14 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 250.3711 | -0.04 | 0.96 | -0.85 | 0.15 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:14 | 250.4727 | -0.04 | 0.96 | -0.86 | 0.14 | -0.72 | 0.28 | 72.27 | 27.34
2019-09-04 | 13:14 | 250.5703 | -0.13 | 0.87 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 250.6719 | -0.21 | 0.79 | -0.71 | 0.29 | -0.68 | 0.32 | 69.34 | 27.34
2019-09-04 | 13:14 | 250.7813 | -0.23 | 0.77 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 250.8828 | -0.08 | 0.92 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 250.9805 | -0.08 | 0.92 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 251.082 | -0.06 | 0.94 | -0.87 | 0.13 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 251.1914 | -0.06 | 0.94 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:14 | 251.293 | -0.05 | 0.95 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 251.3906 | -0.06 | 0.94 | -0.86 | 0.14 | -0.7 | 0.3 | 69.34 | 26.37
2019-09-04 | 13:14 | 251.5 | -0.07 | 0.93 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 251.6016 | -0.06 | 0.94 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 251.7031 | -0.08 | 0.92 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 251.8125 | -0.07 | 0.93 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 251.9102 | -0.06 | 0.94 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 252.0117 | -0.11 | 0.89 | -0.81 | 0.19 | -0.7 | 0.3 | 73.24 | 28.32
2019-09-04 | 13:14 | 252.1133 | -0.18 | 0.82 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 252.2109 | -0.22 | 0.78 | -0.71 | 0.29 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 252.3203 | -0.27 | 0.73 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 26.37 | anomalous boiler pressure
2019-09-04 | 13:14 | 252.4219 | -0.08 | 0.92 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 252.5234 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:14 | 252.6328 | -0.09 | 0.91 | -0.86 | 0.14 | -0.7 | 0.3 | 72.27 | 25.39
2019-09-04 | 13:14 | 252.7305 | -0.08 | 0.92 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 252.832 | -0.08 | 0.92 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 252.9414 | -0.08 | 0.92 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 253.043 | -0.06 | 0.94 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:14 | 253.1406 | -0.09 | 0.91 | -0.86 | 0.14 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 253.2422 | -0.06 | 0.94 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 253.3438 | -0.08 | 0.92 | -0.85 | 0.15 | -0.71 | 0.29 | 69.34 | 25.39
2019-09-04 | 13:14 | 253.4531 | -0.06 | 0.94 | -0.85 | 0.15 | -0.72 | 0.28 | 70.31 | 27.34
2019-09-04 | 13:14 | 253.5508 | -0.17 | 0.83 | -0.77 | 0.23 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 253.6523 | -0.23 | 0.77 | -0.7 | 0.3 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 253.75 | -0.27 | 0.73 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:14 | 253.8633 | -0.14 | 0.86 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 253.9727 | -0.1 | 0.9 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 254.0703 | -0.09 | 0.91 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 254.1719 | -0.09 | 0.91 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 254.2734 | -0.09 | 0.91 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 254.3711 | -0.09 | 0.91 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 254.4805 | -0.07 | 0.93 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 254.582 | -0.08 | 0.92 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 254.6836 | -0.06 | 0.94 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 254.7813 | -0.09 | 0.91 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 254.8906 | -0.1 | 0.9 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 254.9922 | -0.08 | 0.92 | -0.85 | 0.15 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 255.1016 | -0.19 | 0.81 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 255.2031 | -0.25 | 0.75 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 255.3008 | -0.27 | 0.73 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 255.4023 | -0.12 | 0.88 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 255.5 | -0.09 | 0.91 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 255.6133 | -0.09 | 0.91 | -0.83 | 0.17 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:14 | 255.7109 | -0.08 | 0.92 | -0.84 | 0.16 | -0.71 | 0.29 | 73.24 | 27.34
2019-09-04 | 13:14 | 255.8125 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 255.9102 | -0.06 | 0.94 | -0.84 | 0.16 | -0.71 | 0.29 | 73.24 | 27.34
2019-09-04 | 13:14 | 256.0234 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 256.1211 | -0.1 | 0.9 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 256.2227 | -0.07 | 0.93 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:14 | 256.332 | -0.08 | 0.92 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 256.4336 | -0.07 | 0.93 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 256.5313 | -0.1 | 0.9 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 256.6328 | -0.22 | 0.78 | -0.71 | 0.29 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 256.7422 | -0.25 | 0.75 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 28.32
2019-09-04 | 13:14 | 256.8438 | -0.2 | 0.8 | -0.73 | 0.27 | -0.68 | 0.32 | 69.34 | 26.37
2019-09-04 | 13:14 | 256.9531 | -0.11 | 0.89 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 257.043 | -0.07 | 0.93 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 257.1523 | -0.08 | 0.92 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 257.25 | -0.07 | 0.93 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 257.3516 | -0.09 | 0.91 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:14 | 257.4609 | -0.07 | 0.93 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 257.5625 | -0.07 | 0.93 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 257.6719 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 257.7734 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 257.8711 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:14 | 257.9727 | -0.07 | 0.93 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 258.0703 | -0.15 | 0.85 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 258.1719 | -0.23 | 0.77 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:14 | 258.293 | -0.25 | 0.75 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:14 | 258.3906 | -0.1 | 0.9 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 258.4922 | -0.09 | 0.91 | -0.83 | 0.17 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 258.5938 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 258.6914 | -0.09 | 0.91 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 258.793 | -0.07 | 0.93 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 258.9023 | -0.07 | 0.93 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 259 | -0.09 | 0.91 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 25.39
2019-09-04 | 13:14 | 259.1016 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:14 | 259.2031 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 69.34 | 27.34
2019-09-04 | 13:14 | 259.3008 | -0.08 | 0.92 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:14 | 259.4102 | -0.07 | 0.93 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 259.5117 | -0.08 | 0.92 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 259.6133 | -0.18 | 0.82 | -0.74 | 0.26 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 259.7227 | -0.23 | 0.77 | -0.69 | 0.31 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 259.8203 | -0.24 | 0.76 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 259.9219 | -0.09 | 0.91 | -0.82 | 0.18 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 260.043 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 260.1328 | -0.08 | 0.92 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 260.2305 | -0.08 | 0.92 | -0.83 | 0.17 | -0.7 | 0.3 | 73.24 | 28.32
2019-09-04 | 13:14 | 260.332 | -0.06 | 0.94 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 260.4414 | -0.05 | 0.95 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 260.543 | -0.06 | 0.94 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 260.6406 | -0.06 | 0.94 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 260.7422 | -0.05 | 0.95 | -0.84 | 0.16 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:14 | 260.8516 | -0.07 | 0.93 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:14 | 260.9609 | -0.06 | 0.94 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 261.0508 | -0.13 | 0.87 | -0.78 | 0.22 | -0.71 | 0.29 | 69.34 | 25.39
2019-09-04 | 13:14 | 261.1602 | -0.21 | 0.79 | -0.71 | 0.29 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:14 | 261.2617 | -0.23 | 0.77 | -0.68 | 0.32 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:14 | 261.3633 | -0.13 | 0.87 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 261.4609 | -0.1 | 0.9 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 13:14 | 261.5703 | -0.08 | 0.92 | -0.83 | 0.17 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 261.6719 | -0.09 | 0.91 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 261.7734 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 261.8711 | -0.06 | 0.94 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:14 | 261.9805 | -0.06 | 0.94 | -0.85 | 0.15 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 262.082 | -0.06 | 0.94 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 262.1836 | -0.06 | 0.94 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 262.293 | -0.06 | 0.94 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:14 | 262.3906 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 262.4922 | -0.06 | 0.94 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 262.5938 | -0.19 | 0.81 | -0.74 | 0.26 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 262.7031 | -0.23 | 0.77 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 262.8008 | -0.25 | 0.75 | -0.66 | 0.34 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 262.9023 | -0.08 | 0.92 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 263 | -0.08 | 0.92 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 263.1133 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 263.2109 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 263.3125 | -0.06 | 0.94 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 263.4219 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 263.5234 | -0.05 | 0.95 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:14 | 263.6211 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 263.7227 | -0.05 | 0.95 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 263.832 | -0.05 | 0.95 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 263.9336 | -0.05 | 0.95 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 264.0313 | -0.1 | 0.9 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 264.1523 | -0.18 | 0.82 | -0.73 | 0.27 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 264.2422 | -0.22 | 0.78 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 264.3438 | -0.24 | 0.76 | -0.66 | 0.34 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 264.4531 | -0.08 | 0.92 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 264.5508 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:14 | 264.6523 | -0.03 | 0.97 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 264.75 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:14 | 264.8516 | -0.04 | 0.96 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 264.9609 | -0.06 | 0.94 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 265.0625 | -0.04 | 0.96 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 265.1602 | -0.04 | 0.96 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 265.2734 | -0.04 | 0.96 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 265.3711 | -0.04 | 0.96 | -0.83 | 0.17 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 265.4727 | -0.04 | 0.96 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 265.582 | -0.15 | 0.85 | -0.76 | 0.24 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 265.6836 | -0.22 | 0.78 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 28.32
2019-09-04 | 13:14 | 265.7813 | -0.24 | 0.76 | -0.67 | 0.33 | -0.67 | 0.33 | 71.29 | 27.34
2019-09-04 | 13:14 | 265.8828 | -0.1 | 0.9 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 265.9922 | -0.08 | 0.92 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:14 | 266.0938 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 266.1914 | -0.04 | 0.96 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 266.293 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 266.3906 | -0.06 | 0.94 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:14 | 266.5 | -0.04 | 0.96 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 266.6016 | -0.05 | 0.95 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 266.7109 | -0.04 | 0.96 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 266.8125 | -0.03 | 0.97 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 266.9102 | -0.05 | 0.95 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 267.0234 | -0.08 | 0.92 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 267.1211 | -0.19 | 0.81 | -0.72 | 0.28 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 267.2227 | -0.22 | 0.78 | -0.68 | 0.32 | -0.67 | 0.33 | 70.31 | 28.32
2019-09-04 | 13:14 | 267.3203 | -0.24 | 0.76 | -0.66 | 0.34 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 267.4219 | -0.08 | 0.92 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 25.39
2019-09-04 | 13:14 | 267.5313 | -0.08 | 0.92 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 267.6328 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 267.7305 | -0.04 | 0.96 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 267.8438 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 267.9414 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 268.043 | -0.05 | 0.95 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 268.1406 | -0.05 | 0.95 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 268.25 | -0.04 | 0.96 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 268.3516 | -0.01 | 0.99 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 268.4531 | -0.06 | 0.94 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 268.5508 | -0.13 | 0.87 | -0.75 | 0.25 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 268.6602 | -0.21 | 0.79 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 268.7617 | -0.23 | 0.77 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 268.8633 | -0.1 | 0.9 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 268.9727 | -0.08 | 0.92 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:14 | 269.0703 | -0.05 | 0.95 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 13:14 | 269.1719 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 269.2734 | -0.05 | 0.95 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:14 | 269.3828 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 269.4805 | -0.06 | 0.94 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 269.582 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 269.6836 | -0.06 | 0.94 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 269.793 | -0.05 | 0.95 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 269.8906 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 269.9922 | -0.08 | 0.92 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:14 | 270.0938 | -0.18 | 0.82 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 270.2031 | -0.24 | 0.76 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 270.3008 | -0.24 | 0.76 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 270.4102 | -0.1 | 0.9 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 270.5117 | -0.09 | 0.91 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 270.6133 | -0.08 | 0.92 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 270.7109 | -0.05 | 0.95 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 270.8203 | -0.05 | 0.95 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 270.9219 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 271.0234 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 271.1211 | -0.06 | 0.94 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 271.2305 | -0.05 | 0.95 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 271.332 | -0.05 | 0.95 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:14 | 271.4336 | -0.07 | 0.93 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 271.543 | -0.1 | 0.9 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 271.6406 | -0.18 | 0.82 | -0.72 | 0.28 | -0.69 | 0.31 | 73.24 | 28.32
2019-09-04 | 13:14 | 271.7422 | -0.25 | 0.75 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:14 | 271.8438 | -0.25 | 0.75 | -0.65 | 0.35 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 271.9531 | -0.08 | 0.92 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 272.0508 | -0.07 | 0.93 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 272.1523 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 272.25 | -0.08 | 0.92 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:14 | 272.3633 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 25.39
2019-09-04 | 13:14 | 272.4609 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 272.5625 | -0.07 | 0.93 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 25.39
2019-09-04 | 13:14 | 272.6719 | -0.06 | 0.94 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 272.7734 | -0.07 | 0.93 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 272.8711 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 272.9805 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 273.082 | -0.16 | 0.84 | -0.75 | 0.25 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 273.1836 | -0.23 | 0.77 | -0.69 | 0.31 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 273.2813 | -0.23 | 0.77 | -0.68 | 0.32 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 273.3828 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 27.34
2019-09-04 | 13:14 | 273.4922 | -0.06 | 0.94 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 25.39
2019-09-04 | 13:14 | 273.5938 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 273.6914 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 273.8008 | -0.05 | 0.95 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 273.9023 | -0.05 | 0.95 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 274.0117 | -0.05 | 0.95 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 274.1016 | -0.07 | 0.93 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 274.2109 | -0.05 | 0.95 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 274.3125 | -0.06 | 0.94 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 274.4102 | -0.07 | 0.93 | -0.84 | 0.16 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 274.5234 | -0.09 | 0.91 | -0.81 | 0.19 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 274.6211 | -0.18 | 0.82 | -0.73 | 0.27 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 274.7227 | -0.26 | 0.74 | -0.69 | 0.31 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 274.832 | -0.27 | 0.73 | -0.66 | 0.34 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:14 | 274.9336 | -0.09 | 0.91 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 275.0313 | -0.09 | 0.91 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 275.1328 | -0.08 | 0.92 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 275.2305 | -0.07 | 0.93 | -0.82 | 0.18 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 275.3438 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 275.4414 | -0.05 | 0.95 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 275.543 | -0.06 | 0.94 | -0.85 | 0.15 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 275.6523 | -0.07 | 0.93 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 275.75 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 73.24 | 27.34
2019-09-04 | 13:14 | 275.8516 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 275.9609 | -0.04 | 0.96 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 276.0625 | -0.09 | 0.91 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 276.1602 | -0.21 | 0.79 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 276.2617 | -0.25 | 0.75 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 276.3711 | -0.13 | 0.87 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 276.4727 | -0.11 | 0.89 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 276.5703 | -0.1 | 0.9 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 276.6719 | -0.07 | 0.93 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 276.7813 | -0.08 | 0.92 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 276.8828 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 276.9805 | -0.05 | 0.95 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 277.082 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 277.1914 | -0.05 | 0.95 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 277.293 | -0.06 | 0.94 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 277.3906 | -0.06 | 0.94 | -0.83 | 0.17 | -0.71 | 0.29 | 73.24 | 27.34
2019-09-04 | 13:14 | 277.5 | -0.06 | 0.94 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 277.6016 | -0.17 | 0.83 | -0.73 | 0.27 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:14 | 277.7031 | -0.25 | 0.75 | -0.68 | 0.32 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:14 | 277.8008 | -0.24 | 0.76 | -0.66 | 0.34 | -0.68 | 0.32 | 72.27 | 28.32
2019-09-04 | 13:14 | 277.9102 | -0.08 | 0.92 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 278.0117 | -0.05 | 0.95 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 278.1133 | -0.06 | 0.94 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 278.2109 | -0.05 | 0.95 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 278.3203 | -0.04 | 0.96 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 278.4219 | -0.05 | 0.95 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 278.5234 | -0.04 | 0.96 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 278.6328 | -0.03 | 0.97 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 278.7305 | -0.02 | 0.98 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:14 | 278.832 | -0.04 | 0.96 | -0.84 | 0.16 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 278.9336 | -0.04 | 0.96 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 279.043 | -0.06 | 0.94 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 279.1406 | -0.17 | 0.83 | -0.72 | 0.28 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 279.2422 | -0.22 | 0.78 | -0.68 | 0.32 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 279.3438 | -0.21 | 0.79 | -0.66 | 0.34 | -0.79 | 0.21 | 70.31 | 26.37
2019-09-04 | 13:14 | 279.4531 | -0.05 | 0.95 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 279.5508 | -0.04 | 0.96 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 279.6523 | -0.03 | 0.97 | -0.81 | 0.19 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 279.7617 | -0.05 | 0.95 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 279.8633 | -0.02 | 0.98 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 279.9727 | -0.04 | 0.96 | -0.84 | 0.16 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 280.0625 | -0.03 | 0.97 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 280.1719 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 280.2734 | -0.02 | 0.98 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 280.3711 | -0.02 | 0.98 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 280.4727 | -0.03 | 0.97 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 280.582 | -0.12 | 0.88 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 280.6836 | -0.19 | 0.81 | -0.7 | 0.3 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 280.7813 | -0.19 | 0.81 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 280.8906 | -0.07 | 0.93 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 280.9922 | -0.04 | 0.96 | -0.8 | 0.2 | -0.68 | 0.32 | 71.29 | 25.39
2019-09-04 | 13:14 | 281.0938 | -0.03 | 0.97 | -0.82 | 0.18 | -0.69 | 0.31 | 72.27 | 28.32
2019-09-04 | 13:14 | 281.1914 | -0.03 | 0.97 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 281.3008 | -0.02 | 0.98 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 281.4023 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 281.5 | -0.03 | 0.97 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 281.6016 | -0.02 | 0.98 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 281.7109 | 0.01 | 1.01 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 281.8125 | -0.01 | 0.99 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 281.9219 | -0.02 | 0.98 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 282.0234 | 0 | 1 | -0.8 | 0.2 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:14 | 282.1211 | -0.14 | 0.86 | -0.73 | 0.27 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 282.2227 | -0.19 | 0.81 | -0.66 | 0.34 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 282.332 | -0.22 | 0.78 | -0.65 | 0.35 | -0.66 | 0.34 | 71.29 | 27.34
2019-09-04 | 13:14 | 282.4336 | -0.04 | 0.96 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 282.5313 | -0.03 | 0.97 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:14 | 282.6328 | -0.03 | 0.97 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 25.39
2019-09-04 | 13:14 | 282.7305 | -0.03 | 0.97 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 282.8438 | -0.01 | 0.99 | -0.83 | 0.17 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 282.9414 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 283.0508 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 283.1523 | -0.01 | 0.99 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 283.25 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 283.3516 | 0.01 | 1.01 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 27.34
2019-09-04 | 13:14 | 283.4609 | -0.01 | 0.99 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 283.5625 | -0.09 | 0.91 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 283.6602 | -0.16 | 0.84 | -0.69 | 0.31 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 283.7617 | -0.21 | 0.79 | -0.66 | 0.34 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:14 | 283.8711 | -0.11 | 0.89 | -0.73 | 0.27 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:14 | 283.9805 | -0.05 | 0.95 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 284.0703 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 284.1836 | -0.02 | 0.98 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 284.2813 | -0.02 | 0.98 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 284.3828 | -0.02 | 0.98 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:14 | 284.4805 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 284.5938 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 284.6914 | 0.01 | 1.01 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 284.793 | -0.01 | 0.99 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 25.39
2019-09-04 | 13:14 | 284.8906 | -0.01 | 0.99 | -0.84 | 0.16 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:14 | 285 | 0.01 | 1.01 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 285.1016 | -0.1 | 0.9 | -0.74 | 0.26 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 285.2031 | -0.19 | 0.81 | -0.67 | 0.33 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 285.3125 | -0.19 | 0.81 | -0.66 | 0.34 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:14 | 285.4102 | -0.05 | 0.95 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:14 | 285.5117 | -0.03 | 0.97 | -0.81 | 0.19 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 285.6211 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 285.7227 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 28.32
2019-09-04 | 13:14 | 285.8203 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 285.9219 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 286.0234 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 286.1328 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 286.2305 | 0.01 | 1.01 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 286.332 | 0.01 | 1.01 | -0.83 | 0.17 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:14 | 286.4336 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 286.543 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 286.6406 | -0.09 | 0.91 | -0.76 | 0.24 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 286.7422 | -0.17 | 0.83 | -0.68 | 0.32 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 286.8516 | -0.2 | 0.8 | -0.66 | 0.34 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:14 | 286.9531 | -0.03 | 0.97 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 287.0508 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 287.1523 | -0.02 | 0.98 | -0.82 | 0.18 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 287.2617 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 287.3633 | 0 | 1 | -0.81 | 0.19 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:14 | 287.4609 | -0.01 | 0.99 | -0.82 | 0.18 | -0.71 | 0.29 | 70.31 | 25.39
2019-09-04 | 13:14 | 287.5625 | -0.01 | 0.99 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:14 | 287.6719 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 287.7734 | 0 | 1 | -0.84 | 0.16 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 287.8711 | 0.01 | 1.01 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 287.9805 | 0.01 | 1.01 | -0.82 | 0.18 | -0.72 | 0.28 | 74.22 | 28.32
2019-09-04 | 13:14 | 288.082 | -0.08 | 0.92 | -0.77 | 0.23 | -0.71 | 0.29 | 75.2 | 27.34
2019-09-04 | 13:14 | 288.1836 | -0.16 | 0.84 | -0.68 | 0.32 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 288.293 | -0.18 | 0.82 | -0.66 | 0.34 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 288.3906 | -0.05 | 0.95 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 288.4922 | -0.04 | 0.96 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 288.5938 | -0.01 | 0.99 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 288.6914 | -0.02 | 0.98 | -0.8 | 0.2 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 288.8008 | -0.02 | 0.98 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 25.39
2019-09-04 | 13:14 | 288.9023 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 289.0117 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 289.1133 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 289.2227 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 27.34
2019-09-04 | 13:14 | 289.3125 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 289.4219 | -0.01 | 0.99 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 289.5234 | -0.04 | 0.96 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 289.6211 | -0.13 | 0.87 | -0.71 | 0.29 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 289.7227 | -0.18 | 0.82 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 289.832 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:14 | 289.9336 | -0.03 | 0.97 | -0.79 | 0.21 | -0.69 | 0.31 | 69.34 | 26.37
2019-09-04 | 13:14 | 290.0313 | -0.02 | 0.98 | -0.8 | 0.2 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 290.1406 | -0.03 | 0.97 | -0.8 | 0.2 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 290.2422 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 290.3438 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 290.4414 | 0.01 | 1.01 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:14 | 290.5508 | 0 | 1 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 290.6523 | -0.01 | 0.99 | -0.83 | 0.17 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 290.75 | -0.02 | 0.98 | -0.83 | 0.17 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 290.8516 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 25.39
2019-09-04 | 13:14 | 290.9727 | 0.01 | 1.01 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 291.0625 | -0.02 | 0.98 | -0.78 | 0.22 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 291.1602 | -0.15 | 0.85 | -0.7 | 0.3 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 291.2734 | -0.19 | 0.81 | -0.67 | 0.33 | -0.69 | 0.31 | 72.27 | 27.34
2019-09-04 | 13:14 | 291.3711 | -0.11 | 0.89 | -0.7 | 0.3 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 291.4727 | -0.02 | 0.98 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 291.582 | -0.02 | 0.98 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:14 | 291.6836 | 0.01 | 1.01 | -0.81 | 0.19 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:14 | 291.7813 | -0.01 | 0.99 | -0.81 | 0.19 | -0.71 | 0.29 | 70.31 | 26.37
2019-09-04 | 13:14 | 291.8828 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:14 | 291.9922 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 292.0938 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 292.1914 | 0 | 1 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 292.293 | -0.02 | 0.98 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 292.4023 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:14 | 292.5 | -0.01 | 0.99 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 26.37
2019-09-04 | 13:14 | 292.6016 | -0.09 | 0.91 | -0.74 | 0.26 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 292.7031 | -0.15 | 0.85 | -0.7 | 0.3 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 292.8125 | -0.19 | 0.81 | -0.67 | 0.33 | -0.68 | 0.32 | 71.29 | 27.34
2019-09-04 | 13:14 | 292.9102 | -0.04 | 0.96 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:14 | 293.0117 | -0.01 | 0.99 | -0.79 | 0.21 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 293.1211 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 26.37
2019-09-04 | 13:14 | 293.2227 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 293.3203 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 293.4219 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 293.5313 | 0 | 1 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:14 | 293.6328 | 0 | 1 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 293.7305 | 0 | 1 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 293.8438 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 293.9414 | 0 | 1 | -0.81 | 0.19 | -0.71 | 0.29 | 71.29 | 26.37
2019-09-04 | 13:14 | 294.043 | -0.04 | 0.96 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 28.32
2019-09-04 | 13:14 | 294.1406 | -0.13 | 0.87 | -0.7 | 0.3 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 294.25 | -0.18 | 0.82 | -0.67 | 0.33 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:14 | 294.3516 | -0.18 | 0.82 | -0.64 | 0.36 | -0.68 | 0.32 | 71.29 | 28.32
2019-09-04 | 13:14 | 294.4531 | -0.02 | 0.98 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 28.32
2019-09-04 | 13:14 | 294.5508 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 294.6523 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 294.7617 | 0 | 1 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 294.8633 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 13:14 | 294.9727 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:14 | 295.0703 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 295.1719 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 29.3
2019-09-04 | 13:14 | 295.2734 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 295.3828 | 0 | 1 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 295.4805 | 0 | 1 | -0.83 | 0.17 | -0.72 | 0.28 | 70.31 | 26.37
2019-09-04 | 13:14 | 295.582 | -0.07 | 0.93 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:14 | 295.6836 | -0.15 | 0.85 | -0.68 | 0.32 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 295.793 | -0.16 | 0.84 | -0.66 | 0.34 | -0.68 | 0.32 | 71.29 | 26.37
2019-09-04 | 13:14 | 295.8906 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 70.31 | 27.34
2019-09-04 | 13:14 | 295.9922 | 0 | 1 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 27.34
2019-09-04 | 13:14 | 296.1016 | -0.03 | 0.97 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 296.2031 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 296.3008 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 296.4023 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 296.5117 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 296.6133 | 0 | 1 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 27.34
2019-09-04 | 13:14 | 296.7109 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 25.39
2019-09-04 | 13:14 | 296.8125 | 0 | 1 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-09-04 | 13:14 | 296.9219 | 0 | 1 | -0.82 | 0.18 | -0.7 | 0.3 | 70.31 | 27.34
2019-09-04 | 13:14 | 297.0234 | -0.03 | 0.97 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 26.37
2019-09-04 | 13:14 | 297.1328 | -0.12 | 0.88 | -0.72 | 0.28 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:14 | 297.2305 | -0.17 | 0.83 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:14 | 297.332 | -0.19 | 0.81 | -0.65 | 0.35 | -0.66 | 0.34 | 71.29 | 27.34
2019-09-04 | 13:15 | 297.4336 | -0.05 | 0.95 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:15 | 297.5313 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:15 | 297.6406 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:15 | 297.7422 | 0.01 | 1.01 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:15 | 297.8438 | -0.01 | 0.99 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:15 | 297.9531 | 0.01 | 1.01 | -0.81 | 0.19 | -0.7 | 0.3 | 70.31 | 28.32
2019-09-04 | 13:15 | 298.0508 | -0.01 | 0.99 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:15 | 298.1523 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 26.37
2019-09-04 | 13:15 | 298.25 | 0.02 | 1.02 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-09-04 | 13:15 | 298.3516 | 0.02 | 1.02 | -0.83 | 0.17 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:15 | 298.4609 | 0 | 1 | -0.82 | 0.18 | -0.71 | 0.29 | 71.29 | 28.32
2019-09-04 | 13:15 | 298.5625 | -0.06 | 0.94 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 27.34
2019-09-04 | 13:15 | 298.6602 | -0.17 | 0.83 | -0.68 | 0.32 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:15 | 298.7734 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 71.29 | 27.34
2019-09-04 | 13:15 | 298.8711 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 70.31 | 26.37
2019-09-04 | 13:15 | 298.9805 | -0.02 | 0.98 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:15 | 299.0703 | 0 | 1 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:15 | 299.1836 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 26.37
2019-09-04 | 13:15 | 299.2813 | 0 | 1 | -0.81 | 0.19 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:15 | 299.3828 | -0.01 | 0.99 | -0.81 | 0.19 | -0.69 | 0.31 | 70.31 | 27.34
2019-09-04 | 13:15 | 299.4922 | -0.01 | 0.99 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 28.32
2019-09-04 | 13:15 | 299.5938 | 0 | 1 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:15 | 299.6914 | 0 | 1 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:15 | 299.8008 | 0.01 | 1.01 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:15 | 299.9023 | 0.01 | 1.01 | -0.82 | 0.18 | -0.71 | 0.29 | 72.27 | 28.32
2019-09-04 | 13:15 | 300 | -0.02 | 0.98 | -0.83 | 0.17 | -0.72 | 0.28 | 71.29 | 26.37
2019-09-04 | 13:15 | 300.1016 | -0.07 | 0.93 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 26.37
2019-09-04 | 13:15 | 300.2109 | -0.16 | 0.84 | -0.67 | 0.33 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:15 | 300.3125 | -0.19 | 0.81 | -0.66 | 0.34 | -0.67 | 0.33 | 71.29 | 26.37
2019-09-04 | 13:15 | 300.4102 | -0.05 | 0.95 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:15 | 300.5117 | -0.03 | 0.97 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 26.37
2019-09-04 | 13:15 | 300.6211 | -0.01 | 0.99 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 27.34
2019-09-04 | 13:15 | 300.7227 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 27.34
2019-09-04 | 13:15 | 300.8203 | -0.01 | 0.99 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 27.34
2019-09-04 | 13:15 | 300.9336 | 0.01 | 1.01 | -0.81 | 0.19 | -0.69 | 0.31 | 72.27 | 26.37
2019-09-04 | 13:15 | 301.0313 | 0.03 | 1.03 | -0.81 | 0.19 | -0.7 | 0.3 | 71.29 | 27.34

## 13.1mL s
|  |  | BoilerPressure |  | HEPressure |  | SCPressure
Date | Clock | Timer | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | gauge (raw) | absolute (edit) | HETemperature | SCTemperature
2019-09-04 | 14:16 | 0.17188 | 0.06 | 1.06 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 26.37 |  | Flow
2019-09-04 | 14:16 | 0.26953 | 0.08 | 1.08 | -0.25 | 0.75 | -0.17 | 0.83 | 41.02 | 25.39 |  | mL | seconds | flow | start
2019-09-04 | 14:16 | 0.37891 | 0.06 | 1.06 | -0.26 | 0.74 | -0.17 | 0.83 | 40.04 | 25.39 |  | 100 | 8 | 12.5
2019-09-04 | 14:16 | 0.48047 | 0.08 | 1.08 | -0.26 | 0.74 | -0.19 | 0.81 | 41.99 | 25.39 |  | 100 | 7 | 14.3
2019-09-04 | 14:16 | 0.58203 | 0.08 | 1.08 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 25.39 |  | 100 | 7 | 14.3
2019-09-04 | 14:16 | 0.69141 | 0.07 | 1.07 | -0.27 | 0.73 | -0.18 | 0.82 | 41.02 | 24.41
2019-09-04 | 14:16 | 0.78906 | 0.07 | 1.07 | -0.26 | 0.74 | -0.19 | 0.81 | 41.99 | 25.39 |  | 100 | 8 | 12.5 | end
2019-09-04 | 14:16 | 0.89062 | 0.07 | 1.07 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 24.41 |  | 100 | 8 | 12.5
2019-09-04 | 14:16 | 0.99219 | 0.09 | 1.09 | -0.25 | 0.75 | -0.19 | 0.81 | 42.97 | 26.37 |  | 100 | 8 | 12.5
2019-09-04 | 14:16 | 1.0898 | 0.08 | 1.08 | -0.26 | 0.74 | -0.21 | 0.79 | 40.04 | 25.39
2019-09-04 | 14:16 | 1.1992 | 0.03 | 1.03 | -0.25 | 0.75 | -0.19 | 0.81 | 41.99 | 26.37 |  |  |  | 13.1 | average
2019-09-04 | 14:16 | 1.3008 | 0.03 | 1.03 | -0.22 | 0.78 | -0.18 | 0.82 | 42.97 | 26.37
2019-09-04 | 14:16 | 1.4023 | 0.03 | 1.03 | -0.23 | 0.77 | -0.17 | 0.83 | 43.95 | 26.37
2019-09-04 | 14:16 | 1.5117 | 0.02 | 1.02 | -0.21 | 0.79 | -0.17 | 0.83 | 41.02 | 26.37
2019-09-04 | 14:16 | 1.6094 | 0.01 | 1.01 | -0.22 | 0.78 | -0.15 | 0.85 | 42.97 | 26.37
2019-09-04 | 14:16 | 1.7109 | 0.05 | 1.05 | -0.24 | 0.76 | -0.18 | 0.82 | 41.02 | 24.41
2019-09-04 | 14:16 | 1.8125 | 0.07 | 1.07 | -0.25 | 0.75 | -0.17 | 0.83 | 41.99 | 25.39
2019-09-04 | 14:16 | 1.9219 | 0.07 | 1.07 | -0.25 | 0.75 | -0.19 | 0.81 | 41.02 | 25.39
2019-09-04 | 14:16 | 2.0195 | 0.06 | 1.06 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 24.41
2019-09-04 | 14:16 | 2.1211 | 0.08 | 1.08 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 24.41
2019-09-04 | 14:16 | 2.2227 | 0.07 | 1.07 | -0.26 | 0.74 | -0.2 | 0.8 | 41.99 | 25.39
2019-09-04 | 14:16 | 2.332 | 0.08 | 1.08 | -0.26 | 0.74 | -0.2 | 0.8 | 41.02 | 25.39
2019-09-04 | 14:16 | 2.4297 | 0.07 | 1.07 | -0.26 | 0.74 | -0.2 | 0.8 | 41.99 | 25.39
2019-09-04 | 14:16 | 2.5391 | 0.08 | 1.08 | -0.27 | 0.73 | -0.2 | 0.8 | 41.02 | 26.37
2019-09-04 | 14:16 | 2.6406 | 0.07 | 1.07 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 25.39
2019-09-04 | 14:16 | 2.7422 | 0.03 | 1.03 | -0.25 | 0.75 | -0.19 | 0.81 | 42.97 | 25.39
2019-09-04 | 14:16 | 2.8398 | 0.03 | 1.03 | -0.22 | 0.78 | -0.17 | 0.83 | 41.99 | 26.37
2019-09-04 | 14:16 | 2.9492 | 0.02 | 1.02 | -0.22 | 0.78 | -0.17 | 0.83 | 42.97 | 25.39
2019-09-04 | 14:16 | 3.0508 | 0.02 | 1.02 | -0.23 | 0.77 | -0.16 | 0.84 | 41.99 | 24.41
2019-09-04 | 14:16 | 3.1523 | 0.05 | 1.05 | -0.25 | 0.75 | -0.17 | 0.83 | 40.04 | 25.39
2019-09-04 | 14:16 | 3.25 | 0.07 | 1.07 | -0.25 | 0.75 | -0.17 | 0.83 | 41.99 | 26.37
2019-09-04 | 14:16 | 3.3594 | 0.09 | 1.09 | -0.25 | 0.75 | -0.18 | 0.82 | 41.99 | 25.39
2019-09-04 | 14:16 | 3.4609 | 0.07 | 1.07 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 25.39
2019-09-04 | 14:16 | 3.5625 | 0.06 | 1.06 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 26.37
2019-09-04 | 14:16 | 3.6602 | 0.08 | 1.08 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 24.41
2019-09-04 | 14:16 | 3.7695 | 0.06 | 1.06 | -0.25 | 0.75 | -0.2 | 0.8 | 41.02 | 25.39
2019-09-04 | 14:16 | 3.8711 | 0.07 | 1.07 | -0.26 | 0.74 | -0.21 | 0.79 | 41.02 | 26.37 |  | Take equilibrium pressures from 150 seconds
2019-09-04 | 14:16 | 3.9727 | 0.08 | 1.08 | -0.26 | 0.74 | -0.2 | 0.8 | 41.02 | 26.37
2019-09-04 | 14:16 | 4.082 | 0.07 | 1.07 | -0.28 | 0.72 | -0.2 | 0.8 | 41.02 | 27.34 |  | minimum boiler pressure from 150 seconds is: | [6 empty] | 0.85 | average Pb |  | 1.0186
2019-09-04 | 14:16 | 4.1797 | 0.04 | 1.04 | -0.23 | 0.77 | -0.18 | 0.82 | 41.99 | 26.37 |  | maximum boiler pressure from 150 seconds is: | [6 empty] | 1.09
2019-09-04 | 14:16 | 4.2812 | 0.04 | 1.04 | -0.22 | 0.78 | -0.19 | 0.81 | 42.97 | 26.37
2019-09-04 | 14:16 | 4.3789 | 0.02 | 1.02 | -0.21 | 0.79 | -0.18 | 0.82 | 41.02 | 25.39 |  | minimum heat exchanger pressure from 150 seconds is: | [6 empty] | 0.21 | average Phe |  | 0.25668
2019-09-04 | 14:16 | 4.4922 | 0.02 | 1.02 | -0.2 | 0.8 | -0.17 | 0.83 | 41.99 | 26.37 |  | maximum heat exchanger pressure from 150 seconds is: | [6 empty] | 0.42
2019-09-04 | 14:16 | 4.5898 | 0.02 | 1.02 | -0.22 | 0.78 | -0.17 | 0.83 | 41.99 | 25.39
2019-09-04 | 14:16 | 4.6914 | 0.06 | 1.06 | -0.25 | 0.75 | -0.17 | 0.83 | 41.02 | 24.41
2019-09-04 | 14:16 | 4.7891 | 0.06 | 1.06 | -0.25 | 0.75 | -0.18 | 0.82 | 41.99 | 24.41
2019-09-04 | 14:16 | 4.8906 | 0.08 | 1.08 | -0.24 | 0.76 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 5 | 0.09 | 1.09 | -0.24 | 0.76 | -0.18 | 0.82 | 41.02 | 26.37
2019-09-04 | 14:16 | 5.1016 | 0.1 | 1.1 | -0.27 | 0.73 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 5.2109 | 0.09 | 1.09 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 26.37
2019-09-04 | 14:16 | 5.3125 | 0.07 | 1.07 | -0.26 | 0.74 | -0.19 | 0.81 | 41.99 | 25.39
2019-09-04 | 14:16 | 5.4102 | 0.07 | 1.07 | -0.25 | 0.75 | -0.19 | 0.81 | 41.02 | 24.41
2019-09-04 | 14:16 | 5.5117 | 0.07 | 1.07 | -0.26 | 0.74 | -0.2 | 0.8 | 41.99 | 24.41
2019-09-04 | 14:16 | 5.6211 | 0.08 | 1.08 | -0.27 | 0.73 | -0.2 | 0.8 | 42.97 | 26.37
2019-09-04 | 14:16 | 5.7227 | 0.03 | 1.03 | -0.23 | 0.77 | -0.2 | 0.8 | 41.99 | 26.37
2019-09-04 | 14:16 | 5.8203 | 0.01 | 1.01 | -0.22 | 0.78 | -0.18 | 0.82 | 41.99 | 25.39
2019-09-04 | 14:16 | 5.9219 | 0.01 | 1.01 | -0.22 | 0.78 | -0.17 | 0.83 | 41.02 | 26.37
2019-09-04 | 14:16 | 6.0312 | 0.02 | 1.02 | -0.21 | 0.79 | -0.16 | 0.84 | 41.99 | 26.37
2019-09-04 | 14:16 | 6.1289 | 0.05 | 1.05 | -0.21 | 0.79 | -0.16 | 0.84 | 41.99 | 26.37
2019-09-04 | 14:16 | 6.2305 | 0.09 | 1.09 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 6.3398 | 0.07 | 1.07 | -0.25 | 0.75 | -0.17 | 0.83 | 41.99 | 25.39
2019-09-04 | 14:16 | 6.4414 | 0.08 | 1.08 | -0.26 | 0.74 | -0.18 | 0.82 | 41.99 | 26.37
2019-09-04 | 14:16 | 6.5391 | 0.07 | 1.07 | -0.26 | 0.74 | -0.19 | 0.81 | 40.04 | 25.39
2019-09-04 | 14:16 | 6.6406 | 0.09 | 1.09 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 6.75 | 0.07 | 1.07 | -0.25 | 0.75 | -0.21 | 0.79 | 41.02 | 24.41
2019-09-04 | 14:16 | 6.8516 | 0.07 | 1.07 | -0.27 | 0.73 | -0.19 | 0.81 | 41.02 | 25.39 |  | temperature equilibrium from 150 seconds
2019-09-04 | 14:16 | 6.9492 | 0.08 | 1.08 | -0.27 | 0.73 | -0.19 | 0.81 | 41.99 | 25.39
2019-09-04 | 14:16 | 7.0508 | 0.09 | 1.09 | -0.27 | 0.73 | -0.21 | 0.79 | 42.97 | 25.39 |  | minimum heat exchanger outlet temperature is: |  |  |  |  | 71.29 |  | average SC bath temp |  | 31.7692
2019-09-04 | 14:16 | 7.1602 | 0.07 | 1.07 | -0.26 | 0.74 | -0.2 | 0.8 | 41.02 | 25.39 |  | maximum heat exchanger outlet temperature is: |  |  |  |  | 75.2
2019-09-04 | 14:16 | 7.2617 | 0.02 | 1.02 | -0.23 | 0.77 | -0.17 | 0.83 | 41.99 | 26.37
2019-09-04 | 14:16 | 7.3594 | 0.02 | 1.02 | -0.22 | 0.78 | -0.18 | 0.82 | 42.97 | 25.39 |  | average HE outlet temperature is: |  |  |  | 72.8162
2019-09-04 | 14:16 | 7.4727 | 0.02 | 1.02 | -0.22 | 0.78 | -0.18 | 0.82 | 43.95 | 26.37
2019-09-04 | 14:16 | 7.5703 | 0.02 | 1.02 | -0.22 | 0.78 | -0.16 | 0.84 | 41.02 | 25.39 |  | number of temperature points measured is: |  |  |  | 1471 |  | STDEV | 0.78608
2019-09-04 | 14:16 | 7.6719 | 0.07 | 1.07 | -0.22 | 0.78 | -0.17 | 0.83 | 42.97 | 26.37
2019-09-04 | 14:16 | 7.7695 | 0.05 | 1.05 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 26.37
2019-09-04 | 14:16 | 7.8789 | 0.07 | 1.07 | -0.25 | 0.75 | -0.19 | 0.81 | 41.02 | 25.39
2019-09-04 | 14:16 | 7.9805 | 0.06 | 1.06 | -0.26 | 0.74 | -0.18 | 0.82 | 41.99 | 25.39
2019-09-04 | 14:16 | 8.082 | 0.06 | 1.06 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 8.1797 | 0.07 | 1.07 | -0.26 | 0.74 | -0.18 | 0.82 | 41.02 | 27.34
2019-09-04 | 14:16 | 8.2891 | 0.07 | 1.07 | -0.26 | 0.74 | -0.21 | 0.79 | 41.99 | 26.37
2019-09-04 | 14:16 | 8.3906 | 0.1 | 1.1 | -0.27 | 0.73 | -0.2 | 0.8 | 41.99 | 26.37
2019-09-04 | 14:16 | 8.4922 | 0.08 | 1.08 | -0.25 | 0.75 | -0.2 | 0.8 | 41.02 | 25.39
2019-09-04 | 14:16 | 8.5898 | 0.07 | 1.07 | -0.26 | 0.74 | -0.2 | 0.8 | 41.02 | 24.41
2019-09-04 | 14:16 | 8.6992 | 0.04 | 1.04 | -0.23 | 0.77 | -0.18 | 0.82 | 41.99 | 26.37
2019-09-04 | 14:16 | 8.8008 | 0.05 | 1.05 | -0.23 | 0.77 | -0.18 | 0.82 | 41.99 | 26.37
2019-09-04 | 14:16 | 8.9102 | 0.01 | 1.01 | -0.23 | 0.77 | -0.18 | 0.82 | 41.02 | 26.37
2019-09-04 | 14:16 | 9.0117 | -0.01 | 0.99 | -0.22 | 0.78 | -0.17 | 0.83 | 41.02 | 26.37
2019-09-04 | 14:16 | 9.1094 | 0.02 | 1.02 | -0.21 | 0.79 | -0.17 | 0.83 | 41.02 | 24.41
2019-09-04 | 14:16 | 9.2109 | 0.07 | 1.07 | -0.25 | 0.75 | -0.19 | 0.81 | 41.99 | 25.39
2019-09-04 | 14:16 | 9.3203 | 0.06 | 1.06 | -0.23 | 0.77 | -0.18 | 0.82 | 41.02 | 24.41
2019-09-04 | 14:16 | 9.4219 | 0.07 | 1.07 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 9.5195 | 0.08 | 1.08 | -0.25 | 0.75 | -0.19 | 0.81 | 41.02 | 25.39
2019-09-04 | 14:16 | 9.6211 | 0.08 | 1.08 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 26.37
2019-09-04 | 14:16 | 9.7227 | 0.09 | 1.09 | -0.25 | 0.75 | -0.19 | 0.81 | 42.97 | 27.34
2019-09-04 | 14:16 | 9.832 | 0.07 | 1.07 | -0.27 | 0.73 | -0.2 | 0.8 | 41.02 | 26.37
2019-09-04 | 14:16 | 9.9297 | 0.06 | 1.06 | -0.27 | 0.73 | -0.21 | 0.79 | 41.02 | 25.39
2019-09-04 | 14:16 | 10.0391 | 0.09 | 1.09 | -0.27 | 0.73 | -0.2 | 0.8 | 41.02 | 26.37
2019-09-04 | 14:16 | 10.1406 | 0.09 | 1.09 | -0.27 | 0.73 | -0.2 | 0.8 | 42.97 | 26.37
2019-09-04 | 14:16 | 10.2422 | 0.03 | 1.03 | -0.23 | 0.77 | -0.2 | 0.8 | 40.04 | 25.39
2019-09-04 | 14:16 | 10.3398 | 0.02 | 1.02 | -0.23 | 0.77 | -0.19 | 0.81 | 41.02 | 25.39
2019-09-04 | 14:16 | 10.4492 | 0 | 1 | -0.22 | 0.78 | -0.18 | 0.82 | 41.99 | 28.32
2019-09-04 | 14:16 | 10.5508 | 0.01 | 1.01 | -0.22 | 0.78 | -0.17 | 0.83 | 41.02 | 25.39
2019-09-04 | 14:16 | 10.6523 | 0.04 | 1.04 | -0.24 | 0.76 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 10.75 | 0.07 | 1.07 | -0.24 | 0.76 | -0.18 | 0.82 | 41.99 | 26.37
2019-09-04 | 14:16 | 10.8594 | 0.08 | 1.08 | -0.24 | 0.76 | -0.19 | 0.81 | 42.97 | 26.37
2019-09-04 | 14:16 | 10.9609 | 0.07 | 1.07 | -0.26 | 0.74 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 11.0625 | 0.07 | 1.07 | -0.26 | 0.74 | -0.18 | 0.82 | 41.02 | 27.34
2019-09-04 | 14:16 | 11.1602 | 0.08 | 1.08 | -0.26 | 0.74 | -0.19 | 0.81 | 41.02 | 25.39
2019-09-04 | 14:16 | 11.2695 | 0.06 | 1.06 | -0.26 | 0.74 | -0.2 | 0.8 | 41.99 | 26.37
2019-09-04 | 14:16 | 11.3711 | 0.08 | 1.08 | -0.27 | 0.73 | -0.21 | 0.79 | 41.02 | 25.39
2019-09-04 | 14:16 | 11.4727 | 0.09 | 1.09 | -0.26 | 0.74 | -0.21 | 0.79 | 41.02 | 25.39
2019-09-04 | 14:16 | 11.582 | 0.07 | 1.07 | -0.26 | 0.74 | -0.18 | 0.82 | 41.99 | 26.37
2019-09-04 | 14:16 | 11.6797 | 0.05 | 1.05 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 25.39
2019-09-04 | 14:16 | 11.7812 | 0.03 | 1.03 | -0.23 | 0.77 | -0.19 | 0.81 | 41.02 | 26.37
2019-09-04 | 14:16 | 11.8789 | 0.02 | 1.02 | -0.21 | 0.79 | -0.17 | 0.83 | 41.02 | 26.37
2019-09-04 | 14:16 | 11.9922 | 0.03 | 1.03 | -0.21 | 0.79 | -0.17 | 0.83 | 41.02 | 25.39
2019-09-04 | 14:16 | 12.0898 | 0.02 | 1.02 | -0.22 | 0.78 | -0.16 | 0.84 | 41.02 | 25.39
2019-09-04 | 14:16 | 12.1914 | 0.06 | 1.06 | -0.23 | 0.77 | -0.16 | 0.84 | 41.99 | 27.34
2019-09-04 | 14:16 | 12.2891 | 0.07 | 1.07 | -0.25 | 0.75 | -0.19 | 0.81 | 41.99 | 25.39
2019-09-04 | 14:16 | 12.3906 | 0.05 | 1.05 | -0.25 | 0.75 | -0.17 | 0.83 | 41.02 | 24.41
2019-09-04 | 14:16 | 12.5 | 0.07 | 1.07 | -0.25 | 0.75 | -0.18 | 0.82 | 41.02 | 26.37
2019-09-04 | 14:16 | 12.6016 | 0.07 | 1.07 | -0.25 | 0.75 | -0.19 | 0.81 | 41.99 | 25.39
2019-09-04 | 14:16 | 12.7109 | 0.07 | 1.07 | -0.25 | 0.75 | -0.19 | 0.81 | 42.97 | 28.32
2019-09-04 | 14:16 | 12.8125 | 0.06 | 1.06 | -0.27 | 0.73 | -0.2 | 0.8 | 41.02 | 25.39
2019-09-04 | 14:16 | 12.9102 | 0.09 | 1.09 | -0.26 | 0.74 | -0.2 | 0.8 | 41.99 | 27.34
2019-09-04 | 14:16 | 13.0117 | 0.08 | 1.08 | -0.26 | 0.74 | -0.21 | 0.79 | 41.02 | 26.37
2019-09-04 | 14:16 | 13.1211 | 0.07 | 1.07 | -0.28 | 0.72 | -0.21 | 0.79 | 41.99 | 28.32
2019-09-04 | 14:16 | 13.2227 | 0.03 | 1.03 | -0.26 | 0.74 | -0.2 | 0.8 | 39.06 | 25.39
2019-09-04 | 14:16 | 13.3203 | 0.03 | 1.03 | -0.24 | 0.76 | -0.21 | 0.79 | 42.97 | 26.37
2019-09-04 | 14:16 | 13.4219 | 0.02 | 1.02 | -0.23 | 0.77 | -0.19 | 0.81 | 42.97 | 28.32
2019-09-04 | 14:16 | 13.5312 | 0.01 | 1.01 | -0.24 | 0.76 | -0.2 | 0.8 | 42.97 | 25.39
2019-09-04 | 14:16 | 13.6289 | 0.03 | 1.03 | -0.25 | 0.75 | -0.2 | 0.8 | 44.92 | 25.39
2019-09-04 | 14:16 | 13.7305 | 0.06 | 1.06 | -0.3 | 0.7 | -0.23 | 0.77 | 46.88 | 26.37
2019-09-04 | 14:16 | 13.8398 | 0.07 | 1.07 | -0.3 | 0.7 | -0.25 | 0.75 | 48.83 | 25.39
2019-09-04 | 14:16 | 13.9414 | 0.08 | 1.08 | -0.33 | 0.67 | -0.25 | 0.75 | 47.85 | 25.39
2019-09-04 | 14:16 | 14.0391 | 0.06 | 1.06 | -0.33 | 0.67 | -0.27 | 0.73 | 51.76 | 24.41
2019-09-04 | 14:16 | 14.1406 | 0.08 | 1.08 | -0.33 | 0.67 | -0.27 | 0.73 | 54.69 | 26.37
2019-09-04 | 14:16 | 14.25 | 0.08 | 1.08 | -0.34 | 0.66 | -0.29 | 0.71 | 56.64 | 25.39
2019-09-04 | 14:16 | 14.3516 | 0.06 | 1.06 | -0.36 | 0.64 | -0.3 | 0.7 | 57.62 | 27.34
2019-09-04 | 14:16 | 14.4492 | 0.05 | 1.05 | -0.38 | 0.62 | -0.31 | 0.69 | 61.52 | 25.39
2019-09-04 | 14:16 | 14.5508 | 0.06 | 1.06 | -0.39 | 0.61 | -0.32 | 0.68 | 61.52 | 25.39
2019-09-04 | 14:16 | 14.6602 | 0.07 | 1.07 | -0.38 | 0.62 | -0.33 | 0.67 | 62.5 | 27.34
2019-09-04 | 14:16 | 14.7617 | 0.03 | 1.03 | -0.35 | 0.65 | -0.32 | 0.68 | 60.55 | 25.39
2019-09-04 | 14:16 | 14.8594 | 0 | 1 | -0.32 | 0.68 | -0.31 | 0.69 | 68.36 | 26.37
2019-09-04 | 14:16 | 14.9727 | 0 | 1 | -0.33 | 0.67 | -0.31 | 0.69 | 67.38 | 27.34
2019-09-04 | 14:16 | 15.0703 | -0.02 | 0.98 | -0.32 | 0.68 | -0.31 | 0.69 | 70.31 | 26.37
2019-09-04 | 14:16 | 15.1719 | 0.06 | 1.06 | -0.39 | 0.61 | -0.33 | 0.67 | 70.31 | 26.37
2019-09-04 | 14:16 | 15.2695 | 0.06 | 1.06 | -0.42 | 0.58 | -0.32 | 0.68 | 72.27 | 27.34
2019-09-04 | 14:16 | 15.3789 | 0.08 | 1.08 | -0.42 | 0.58 | -0.37 | 0.63 | 72.27 | 25.39
2019-09-04 | 14:16 | 15.4805 | 0.07 | 1.07 | -0.43 | 0.57 | -0.37 | 0.63 | 67.38 | 26.37
2019-09-04 | 14:16 | 15.582 | 0.07 | 1.07 | -0.43 | 0.57 | -0.37 | 0.63 | 72.27 | 24.41
2019-09-04 | 14:16 | 15.6797 | 0.08 | 1.08 | -0.44 | 0.56 | -0.38 | 0.62 | 75.2 | 24.41
2019-09-04 | 14:16 | 15.7891 | 0.06 | 1.06 | -0.44 | 0.56 | -0.37 | 0.63 | 74.22 | 25.39
2019-09-04 | 14:16 | 15.8906 | 0.08 | 1.08 | -0.45 | 0.55 | -0.38 | 0.62 | 74.22 | 26.37
2019-09-04 | 14:16 | 15.9922 | 0.07 | 1.07 | -0.47 | 0.53 | -0.4 | 0.6 | 75.2 | 25.39
2019-09-04 | 14:16 | 16.0898 | 0.07 | 1.07 | -0.47 | 0.53 | -0.41 | 0.59 | 75.2 | 25.39
2019-09-04 | 14:16 | 16.1992 | 0.04 | 1.04 | -0.43 | 0.57 | -0.39 | 0.61 | 75.2 | 25.39
2019-09-04 | 14:16 | 16.3008 | 0 | 1 | -0.37 | 0.63 | -0.37 | 0.63 | 67.38 | 27.34
2019-09-04 | 14:16 | 16.4023 | -0.01 | 0.99 | -0.37 | 0.63 | -0.37 | 0.63 | 77.15 | 27.34
2019-09-04 | 14:16 | 16.5117 | -0.02 | 0.98 | -0.36 | 0.64 | -0.37 | 0.63 | 75.2 | 25.39
2019-09-04 | 14:16 | 16.6094 | -0.04 | 0.96 | -0.37 | 0.63 | -0.37 | 0.63 | 75.2 | 25.39
2019-09-04 | 14:16 | 16.7109 | 0.07 | 1.07 | -0.47 | 0.53 | -0.39 | 0.61 | 75.2 | 27.34
2019-09-04 | 14:16 | 16.8125 | 0.08 | 1.08 | -0.48 | 0.52 | -0.41 | 0.59 | 77.15 | 25.39
2019-09-04 | 14:16 | 16.9219 | 0.09 | 1.09 | -0.47 | 0.53 | -0.41 | 0.59 | 76.17 | 27.34
2019-09-04 | 14:16 | 17.0195 | 0.08 | 1.08 | -0.49 | 0.51 | -0.42 | 0.58 | 75.2 | 27.34
2019-09-04 | 14:16 | 17.1211 | 0.11 | 1.11 | -0.49 | 0.51 | -0.42 | 0.58 | 74.22 | 26.37
2019-09-04 | 14:16 | 17.2227 | 0.06 | 1.06 | -0.5 | 0.5 | -0.43 | 0.57 | 74.22 | 25.39
2019-09-04 | 14:16 | 17.332 | 0.07 | 1.07 | -0.51 | 0.49 | -0.44 | 0.56 | 75.2 | 26.37
2019-09-04 | 14:16 | 17.4297 | 0.08 | 1.08 | -0.51 | 0.49 | -0.44 | 0.56 | 75.2 | 26.37
2019-09-04 | 14:16 | 17.5391 | 0.08 | 1.08 | -0.5 | 0.5 | -0.45 | 0.55 | 76.17 | 27.34
2019-09-04 | 14:16 | 17.6406 | 0.08 | 1.08 | -0.52 | 0.48 | -0.46 | 0.54 | 74.22 | 26.37
2019-09-04 | 14:16 | 17.7422 | 0.05 | 1.05 | -0.47 | 0.53 | -0.43 | 0.57 | 75.2 | 26.37
2019-09-04 | 14:16 | 17.8398 | 0 | 1 | -0.42 | 0.58 | -0.43 | 0.57 | 65.43 | 25.39
2019-09-04 | 14:16 | 17.9492 | -0.04 | 0.96 | -0.42 | 0.58 | -0.42 | 0.58 | 73.24 | 25.39
2019-09-04 | 14:16 | 18.0508 | -0.01 | 0.99 | -0.39 | 0.61 | -0.42 | 0.58 | 76.17 | 27.34
2019-09-04 | 14:16 | 18.1523 | 0.04 | 1.04 | -0.48 | 0.52 | -0.43 | 0.57 | 73.24 | 25.39
2019-09-04 | 14:16 | 18.25 | 0.05 | 1.05 | -0.51 | 0.49 | -0.43 | 0.57 | 73.24 | 26.37
2019-09-04 | 14:16 | 18.3516 | 0.07 | 1.07 | -0.52 | 0.48 | -0.46 | 0.54 | 74.22 | 27.34
2019-09-04 | 14:16 | 18.4609 | 0.06 | 1.06 | -0.52 | 0.48 | -0.45 | 0.55 | 74.22 | 26.37
2019-09-04 | 14:16 | 18.5625 | 0.06 | 1.06 | -0.53 | 0.47 | -0.47 | 0.53 | 73.24 | 25.39
2019-09-04 | 14:16 | 18.6719 | 0.06 | 1.06 | -0.54 | 0.46 | -0.45 | 0.55 | 68.36 | 25.39
2019-09-04 | 14:16 | 18.7695 | 0.08 | 1.08 | -0.53 | 0.47 | -0.47 | 0.53 | 73.24 | 26.37
2019-09-04 | 14:16 | 18.8711 | 0.06 | 1.06 | -0.54 | 0.46 | -0.48 | 0.52 | 73.24 | 25.39
2019-09-04 | 14:16 | 18.9727 | 0.07 | 1.07 | -0.54 | 0.46 | -0.48 | 0.52 | 74.22 | 25.39
2019-09-04 | 14:16 | 19.082 | 0.07 | 1.07 | -0.55 | 0.45 | -0.49 | 0.51 | 73.24 | 26.37
2019-09-04 | 14:16 | 19.1797 | 0.07 | 1.07 | -0.55 | 0.45 | -0.48 | 0.52 | 73.24 | 27.34
2019-09-04 | 14:16 | 19.2812 | 0.01 | 1.01 | -0.47 | 0.53 | -0.47 | 0.53 | 72.27 | 26.37
2019-09-04 | 14:16 | 19.3789 | -0.04 | 0.96 | -0.42 | 0.58 | -0.45 | 0.55 | 64.45 | 26.37
2019-09-04 | 14:16 | 19.4922 | -0.07 | 0.93 | -0.43 | 0.57 | -0.45 | 0.55 | 71.29 | 27.34
2019-09-04 | 14:16 | 19.5898 | -0.04 | 0.96 | -0.42 | 0.58 | -0.42 | 0.58 | 73.24 | 26.37
2019-09-04 | 14:16 | 19.6914 | 0.04 | 1.04 | -0.53 | 0.47 | -0.48 | 0.52 | 72.27 | 25.39
2019-09-04 | 14:16 | 19.8008 | 0.07 | 1.07 | -0.56 | 0.44 | -0.49 | 0.51 | 73.24 | 26.37
2019-09-04 | 14:16 | 19.9023 | 0.07 | 1.07 | -0.55 | 0.45 | -0.49 | 0.51 | 73.24 | 27.34
2019-09-04 | 14:16 | 20 | 0.06 | 1.06 | -0.57 | 0.43 | -0.5 | 0.5 | 74.22 | 26.37
2019-09-04 | 14:16 | 20.1016 | 0.07 | 1.07 | -0.56 | 0.44 | -0.49 | 0.51 | 73.24 | 27.34
2019-09-04 | 14:16 | 20.2109 | 0.08 | 1.08 | -0.58 | 0.42 | -0.5 | 0.5 | 66.41 | 26.37
2019-09-04 | 14:16 | 20.3125 | 0.07 | 1.07 | -0.56 | 0.44 | -0.49 | 0.51 | 73.24 | 25.39
2019-09-04 | 14:16 | 20.4102 | 0.09 | 1.09 | -0.56 | 0.44 | -0.51 | 0.49 | 73.24 | 26.37
2019-09-04 | 14:16 | 20.5117 | 0.08 | 1.08 | -0.57 | 0.43 | -0.5 | 0.5 | 74.22 | 28.32
2019-09-04 | 14:16 | 20.6211 | 0.07 | 1.07 | -0.58 | 0.42 | -0.5 | 0.5 | 74.22 | 26.37
2019-09-04 | 14:16 | 20.7227 | 0.06 | 1.06 | -0.55 | 0.45 | -0.5 | 0.5 | 74.22 | 26.37
2019-09-04 | 14:16 | 20.832 | -0.03 | 0.97 | -0.45 | 0.55 | -0.48 | 0.52 | 73.24 | 26.37
2019-09-04 | 14:16 | 20.9297 | -0.05 | 0.95 | -0.45 | 0.55 | -0.47 | 0.53 | 65.43 | 27.34
2019-09-04 | 14:16 | 21.0312 | -0.06 | 0.94 | -0.45 | 0.55 | -0.47 | 0.53 | 68.36 | 26.37
2019-09-04 | 14:16 | 21.1289 | -0.06 | 0.94 | -0.44 | 0.56 | -0.47 | 0.53 | 72.27 | 25.39
2019-09-04 | 14:16 | 21.2422 | 0.06 | 1.06 | -0.56 | 0.44 | -0.49 | 0.51 | 73.24 | 27.34
2019-09-04 | 14:16 | 21.3398 | 0.06 | 1.06 | -0.57 | 0.43 | -0.5 | 0.5 | 72.27 | 26.37
2019-09-04 | 14:16 | 21.4414 | 0.07 | 1.07 | -0.58 | 0.42 | -0.5 | 0.5 | 73.24 | 26.37
2019-09-04 | 14:16 | 21.5391 | 0.07 | 1.07 | -0.59 | 0.41 | -0.52 | 0.48 | 73.24 | 26.37
2019-09-04 | 14:16 | 21.6523 | 0.07 | 1.07 | -0.59 | 0.41 | -0.52 | 0.48 | 74.22 | 26.37
2019-09-04 | 14:16 | 21.75 | 0.09 | 1.09 | -0.59 | 0.41 | -0.53 | 0.47 | 64.45 | 25.39
2019-09-04 | 14:16 | 21.8516 | 0.08 | 1.08 | -0.6 | 0.4 | -0.53 | 0.47 | 72.27 | 26.37
2019-09-04 | 14:16 | 21.9492 | 0.07 | 1.07 | -0.6 | 0.4 | -0.52 | 0.48 | 72.27 | 26.37
2019-09-04 | 14:16 | 22.0508 | 0.08 | 1.08 | -0.6 | 0.4 | -0.54 | 0.46 | 73.24 | 26.37
2019-09-04 | 14:16 | 22.1602 | 0.09 | 1.09 | -0.61 | 0.39 | -0.53 | 0.47 | 72.27 | 25.39
2019-09-04 | 14:16 | 22.2617 | -0.01 | 0.99 | -0.5 | 0.5 | -0.51 | 0.49 | 73.24 | 27.34
2019-09-04 | 14:16 | 22.3711 | -0.04 | 0.96 | -0.48 | 0.52 | -0.51 | 0.49 | 73.24 | 27.34
2019-09-04 | 14:16 | 22.4727 | -0.08 | 0.92 | -0.45 | 0.55 | -0.49 | 0.51 | 66.41 | 26.37
2019-09-04 | 14:16 | 22.5703 | -0.05 | 0.95 | -0.45 | 0.55 | -0.49 | 0.51 | 68.36 | 26.37
2019-09-04 | 14:16 | 22.6719 | 0.04 | 1.04 | -0.57 | 0.43 | -0.51 | 0.49 | 73.24 | 26.37
2019-09-04 | 14:16 | 22.7812 | 0.07 | 1.07 | -0.6 | 0.4 | -0.52 | 0.48 | 71.29 | 26.37
2019-09-04 | 14:16 | 22.8789 | 0.07 | 1.07 | -0.61 | 0.39 | -0.54 | 0.46 | 71.29 | 26.37
2019-09-04 | 14:16 | 22.9805 | 0.06 | 1.06 | -0.58 | 0.42 | -0.53 | 0.47 | 71.29 | 25.39
2019-09-04 | 14:17 | 23.082 | 0.07 | 1.07 | -0.61 | 0.39 | -0.53 | 0.47 | 72.27 | 26.37
2019-09-04 | 14:17 | 23.1797 | 0.08 | 1.08 | -0.6 | 0.4 | -0.54 | 0.46 | 71.29 | 27.34
2019-09-04 | 14:17 | 23.2891 | 0.07 | 1.07 | -0.6 | 0.4 | -0.55 | 0.45 | 65.43 | 28.32
2019-09-04 | 14:17 | 23.3906 | 0.06 | 1.06 | -0.61 | 0.39 | -0.55 | 0.45 | 70.31 | 25.39
2019-09-04 | 14:17 | 23.5 | 0.07 | 1.07 | -0.62 | 0.38 | -0.55 | 0.45 | 72.27 | 27.34
2019-09-04 | 14:17 | 23.6016 | 0.07 | 1.07 | -0.62 | 0.38 | -0.55 | 0.45 | 71.29 | 25.39
2019-09-04 | 14:17 | 23.6992 | 0.07 | 1.07 | -0.61 | 0.39 | -0.55 | 0.45 | 72.27 | 26.37
2019-09-04 | 14:17 | 23.8008 | -0.02 | 0.98 | -0.51 | 0.49 | -0.53 | 0.47 | 71.29 | 26.37
2019-09-04 | 14:17 | 23.9102 | -0.05 | 0.95 | -0.47 | 0.53 | -0.52 | 0.48 | 71.29 | 25.39
2019-09-04 | 14:17 | 24.0117 | -0.08 | 0.92 | -0.47 | 0.53 | -0.52 | 0.48 | 66.41 | 25.39
2019-09-04 | 14:17 | 24.1094 | -0.05 | 0.95 | -0.47 | 0.53 | -0.5 | 0.5 | 64.45 | 26.37
2019-09-04 | 14:17 | 24.2109 | 0.06 | 1.06 | -0.59 | 0.41 | -0.53 | 0.47 | 71.29 | 27.34
2019-09-04 | 14:17 | 24.3125 | 0.05 | 1.05 | -0.61 | 0.39 | -0.54 | 0.46 | 70.31 | 27.34
2019-09-04 | 14:17 | 24.4219 | 0.08 | 1.08 | -0.61 | 0.39 | -0.54 | 0.46 | 71.29 | 27.34
2019-09-04 | 14:17 | 24.5195 | 0.08 | 1.08 | -0.61 | 0.39 | -0.54 | 0.46 | 71.29 | 27.34
2019-09-04 | 14:17 | 24.6211 | 0.08 | 1.08 | -0.62 | 0.38 | -0.55 | 0.45 | 72.27 | 27.34
2019-09-04 | 14:17 | 24.7305 | 0.09 | 1.09 | -0.62 | 0.38 | -0.56 | 0.44 | 70.31 | 26.37
2019-09-04 | 14:17 | 24.832 | 0.06 | 1.06 | -0.62 | 0.38 | -0.55 | 0.45 | 64.45 | 26.37
2019-09-04 | 14:17 | 24.9297 | 0.08 | 1.08 | -0.62 | 0.38 | -0.55 | 0.45 | 70.31 | 26.37
2019-09-04 | 14:17 | 25.0391 | 0.06 | 1.06 | -0.62 | 0.38 | -0.55 | 0.45 | 72.27 | 25.39
2019-09-04 | 14:17 | 25.1406 | 0.07 | 1.07 | -0.63 | 0.37 | -0.54 | 0.46 | 70.31 | 27.34
2019-09-04 | 14:17 | 25.2422 | 0.04 | 1.04 | -0.58 | 0.42 | -0.54 | 0.46 | 70.31 | 27.34
2019-09-04 | 14:17 | 25.3398 | -0.03 | 0.97 | -0.5 | 0.5 | -0.53 | 0.47 | 71.29 | 26.37
2019-09-04 | 14:17 | 25.4492 | -0.06 | 0.94 | -0.48 | 0.52 | -0.51 | 0.49 | 71.29 | 26.37
2019-09-04 | 14:17 | 25.5508 | -0.07 | 0.93 | -0.47 | 0.53 | -0.49 | 0.51 | 69.34 | 26.37
2019-09-04 | 14:17 | 25.6523 | 0.03 | 1.03 | -0.56 | 0.44 | -0.49 | 0.51 | 65.43 | 26.37
2019-09-04 | 14:17 | 25.75 | 0.06 | 1.06 | -0.6 | 0.4 | -0.52 | 0.48 | 70.31 | 27.34
2019-09-04 | 14:17 | 25.8516 | 0.05 | 1.05 | -0.6 | 0.4 | -0.53 | 0.47 | 71.29 | 26.37
2019-09-04 | 14:17 | 25.9609 | 0.07 | 1.07 | -0.6 | 0.4 | -0.53 | 0.47 | 70.31 | 26.37
2019-09-04 | 14:17 | 26.0625 | 0.06 | 1.06 | -0.6 | 0.4 | -0.52 | 0.48 | 70.31 | 25.39
2019-09-04 | 14:17 | 26.1719 | 0.06 | 1.06 | -0.6 | 0.4 | -0.54 | 0.46 | 71.29 | 27.34
2019-09-04 | 14:17 | 26.2695 | 0.06 | 1.06 | -0.61 | 0.39 | -0.54 | 0.46 | 72.27 | 26.37
2019-09-04 | 14:17 | 26.3711 | 0.07 | 1.07 | -0.61 | 0.39 | -0.54 | 0.46 | 64.45 | 26.37
2019-09-04 | 14:17 | 26.4727 | 0.08 | 1.08 | -0.62 | 0.38 | -0.55 | 0.45 | 69.34 | 26.37
2019-09-04 | 14:17 | 26.582 | 0.07 | 1.07 | -0.62 | 0.38 | -0.54 | 0.46 | 70.31 | 25.39
2019-09-04 | 14:17 | 26.6797 | 0.06 | 1.06 | -0.62 | 0.38 | -0.55 | 0.45 | 70.31 | 26.37
2019-09-04 | 14:17 | 26.7891 | -0.02 | 0.98 | -0.52 | 0.48 | -0.53 | 0.47 | 70.31 | 26.37
2019-09-04 | 14:17 | 26.8906 | -0.07 | 0.93 | -0.48 | 0.52 | -0.52 | 0.48 | 71.29 | 27.34
2019-09-04 | 14:17 | 26.9922 | -0.06 | 0.94 | -0.47 | 0.53 | -0.51 | 0.49 | 70.31 | 26.37
2019-09-04 | 14:17 | 27.0898 | -0.06 | 0.94 | -0.47 | 0.53 | -0.5 | 0.5 | 71.29 | 26.37
2019-09-04 | 14:17 | 27.1914 | 0.04 | 1.04 | -0.58 | 0.42 | -0.52 | 0.48 | 64.45 | 25.39
2019-09-04 | 14:17 | 27.3008 | 0.07 | 1.07 | -0.59 | 0.41 | -0.52 | 0.48 | 72.27 | 26.37
2019-09-04 | 14:17 | 27.4023 | 0.07 | 1.07 | -0.6 | 0.4 | -0.54 | 0.46 | 72.27 | 26.37
2019-09-04 | 14:17 | 27.5 | 0.06 | 1.06 | -0.6 | 0.4 | -0.54 | 0.46 | 72.27 | 26.37
2019-09-04 | 14:17 | 27.6016 | 0.07 | 1.07 | -0.61 | 0.39 | -0.54 | 0.46 | 70.31 | 26.37
2019-09-04 | 14:17 | 27.7109 | 0.07 | 1.07 | -0.61 | 0.39 | -0.54 | 0.46 | 71.29 | 28.32
2019-09-04 | 14:17 | 27.8125 | 0.06 | 1.06 | -0.62 | 0.38 | -0.54 | 0.46 | 71.29 | 27.34
2019-09-04 | 14:17 | 27.9102 | 0.09 | 1.09 | -0.61 | 0.39 | -0.54 | 0.46 | 65.43 | 25.39
2019-09-04 | 14:17 | 28.0117 | 0.06 | 1.06 | -0.61 | 0.39 | -0.54 | 0.46 | 71.29 | 26.37
2019-09-04 | 14:17 | 28.1211 | 0.08 | 1.08 | -0.62 | 0.38 | -0.54 | 0.46 | 71.29 | 26.37
2019-09-04 | 14:17 | 28.2227 | 0.06 | 1.06 | -0.62 | 0.38 | -0.55 | 0.45 | 71.29 | 25.39
2019-09-04 | 14:17 | 28.3203 | -0.03 | 0.97 | -0.53 | 0.47 | -0.52 | 0.48 | 71.29 | 27.34
2019-09-04 | 14:17 | 28.4297 | -0.06 | 0.94 | -0.49 | 0.51 | -0.51 | 0.49 | 73.24 | 28.32
2019-09-04 | 14:17 | 28.5312 | -0.06 | 0.94 | -0.48 | 0.52 | -0.5 | 0.5 | 73.24 | 26.37
2019-09-04 | 14:17 | 28.6289 | -0.07 | 0.93 | -0.47 | 0.53 | -0.5 | 0.5 | 72.27 | 26.37
2019-09-04 | 14:17 | 28.7305 | 0.07 | 1.07 | -0.58 | 0.42 | -0.51 | 0.49 | 74.22 | 26.37
2019-09-04 | 14:17 | 28.8398 | 0.07 | 1.07 | -0.59 | 0.41 | -0.53 | 0.47 | 72.27 | 26.37
2019-09-04 | 14:17 | 28.9414 | 0.07 | 1.07 | -0.6 | 0.4 | -0.54 | 0.46 | 73.24 | 27.34
2019-09-04 | 14:17 | 29.0391 | 0.07 | 1.07 | -0.61 | 0.39 | -0.53 | 0.47 | 73.24 | 26.37
2019-09-04 | 14:17 | 29.1406 | 0.07 | 1.07 | -0.62 | 0.38 | -0.54 | 0.46 | 73.24 | 27.34
2019-09-04 | 14:17 | 29.25 | 0.07 | 1.07 | -0.61 | 0.39 | -0.55 | 0.45 | 73.24 | 28.32
2019-09-04 | 14:17 | 29.3516 | 0.07 | 1.07 | -0.62 | 0.38 | -0.54 | 0.46 | 73.24 | 28.32
2019-09-04 | 14:17 | 29.4492 | 0.08 | 1.08 | -0.62 | 0.38 | -0.55 | 0.45 | 73.24 | 28.32
2019-09-04 | 14:17 | 29.5625 | 0.09 | 1.09 | -0.63 | 0.37 | -0.56 | 0.44 | 74.22 | 27.34
2019-09-04 | 14:17 | 29.6602 | 0.06 | 1.06 | -0.63 | 0.37 | -0.56 | 0.44 | 74.22 | 27.34
2019-09-04 | 14:17 | 29.7617 | 0.01 | 1.01 | -0.55 | 0.45 | -0.55 | 0.45 | 76.17 | 29.3
2019-09-04 | 14:17 | 29.8711 | -0.05 | 0.95 | -0.52 | 0.48 | -0.54 | 0.46 | 74.22 | 28.32
2019-09-04 | 14:17 | 29.9727 | -0.08 | 0.92 | -0.49 | 0.51 | -0.53 | 0.47 | 74.22 | 28.32
2019-09-04 | 14:17 | 30.0703 | -0.08 | 0.92 | -0.49 | 0.51 | -0.53 | 0.47 | 74.22 | 28.32
2019-09-04 | 14:17 | 30.1719 | 0.04 | 1.04 | -0.59 | 0.41 | -0.53 | 0.47 | 75.2 | 28.32
2019-09-04 | 14:17 | 30.2695 | 0.06 | 1.06 | -0.62 | 0.38 | -0.53 | 0.47 | 75.2 | 27.34
2019-09-04 | 14:17 | 30.3789 | 0.08 | 1.08 | -0.62 | 0.38 | -0.55 | 0.45 | 75.2 | 29.3
2019-09-04 | 14:17 | 30.4805 | 0.07 | 1.07 | -0.62 | 0.38 | -0.54 | 0.46 | 76.17 | 29.3
2019-09-04 | 14:17 | 30.582 | 0.07 | 1.07 | -0.63 | 0.37 | -0.55 | 0.45 | 75.2 | 30.27
2019-09-04 | 14:17 | 30.6914 | 0.07 | 1.07 | -0.62 | 0.38 | -0.57 | 0.43 | 75.2 | 29.3
2019-09-04 | 14:17 | 30.7891 | 0.07 | 1.07 | -0.64 | 0.36 | -0.56 | 0.44 | 75.2 | 29.3
2019-09-04 | 14:17 | 30.8906 | 0.08 | 1.08 | -0.64 | 0.36 | -0.56 | 0.44 | 77.15 | 31.25
2019-09-04 | 14:17 | 31 | 0.07 | 1.07 | -0.65 | 0.35 | -0.56 | 0.44 | 76.17 | 30.27
2019-09-04 | 14:17 | 31.1016 | 0.06 | 1.06 | -0.65 | 0.35 | -0.57 | 0.43 | 75.2 | 29.3
2019-09-04 | 14:17 | 31.1992 | 0.06 | 1.06 | -0.65 | 0.35 | -0.55 | 0.45 | 77.15 | 31.25
2019-09-04 | 14:17 | 31.3008 | 0 | 1 | -0.56 | 0.44 | -0.54 | 0.46 | 77.15 | 31.25
2019-09-04 | 14:17 | 31.4102 | -0.07 | 0.93 | -0.51 | 0.49 | -0.53 | 0.47 | 76.17 | 30.27
2019-09-04 | 14:17 | 31.5117 | -0.08 | 0.92 | -0.51 | 0.49 | -0.52 | 0.48 | 76.17 | 31.25
2019-09-04 | 14:17 | 31.6094 | -0.07 | 0.93 | -0.48 | 0.52 | -0.52 | 0.48 | 76.17 | 31.25
2019-09-04 | 14:17 | 31.7109 | 0.05 | 1.05 | -0.6 | 0.4 | -0.53 | 0.47 | 76.17 | 30.27
2019-09-04 | 14:17 | 31.8125 | 0.06 | 1.06 | -0.61 | 0.39 | -0.54 | 0.46 | 76.17 | 29.3
2019-09-04 | 14:17 | 31.9219 | 0.06 | 1.06 | -0.62 | 0.38 | -0.54 | 0.46 | 76.17 | 31.25
2019-09-04 | 14:17 | 32.0195 | 0.07 | 1.07 | -0.63 | 0.37 | -0.55 | 0.45 | 76.17 | 31.25
2019-09-04 | 14:17 | 32.1289 | 0.08 | 1.08 | -0.63 | 0.37 | -0.55 | 0.45 | 77.15 | 30.27
2019-09-04 | 14:17 | 32.2305 | 0.07 | 1.07 | -0.63 | 0.37 | -0.56 | 0.44 | 76.17 | 31.25
2019-09-04 | 14:17 | 32.332 | 0.05 | 1.05 | -0.63 | 0.37 | -0.57 | 0.43 | 76.17 | 32.23
2019-09-04 | 14:17 | 32.4297 | 0.07 | 1.07 | -0.64 | 0.36 | -0.56 | 0.44 | 77.15 | 31.25
2019-09-04 | 14:17 | 32.5391 | 0.07 | 1.07 | -0.64 | 0.36 | -0.56 | 0.44 | 76.17 | 30.27
2019-09-04 | 14:17 | 32.6406 | 0.06 | 1.06 | -0.65 | 0.35 | -0.57 | 0.43 | 76.17 | 30.27
2019-09-04 | 14:17 | 32.7422 | 0.02 | 1.02 | -0.62 | 0.38 | -0.56 | 0.44 | 76.17 | 32.23
2019-09-04 | 14:17 | 32.8516 | -0.04 | 0.96 | -0.54 | 0.46 | -0.53 | 0.47 | 77.15 | 32.23
2019-09-04 | 14:17 | 32.9492 | -0.07 | 0.93 | -0.52 | 0.48 | -0.53 | 0.47 | 76.17 | 33.2
2019-09-04 | 14:17 | 33.0508 | -0.08 | 0.92 | -0.5 | 0.5 | -0.53 | 0.47 | 77.15 | 32.23
2019-09-04 | 14:17 | 33.1523 | -0.01 | 0.99 | -0.55 | 0.45 | -0.52 | 0.48 | 78.12 | 32.23
2019-09-04 | 14:17 | 33.2617 | 0.05 | 1.05 | -0.61 | 0.39 | -0.55 | 0.45 | 77.15 | 32.23
2019-09-04 | 14:17 | 33.3594 | 0.07 | 1.07 | -0.63 | 0.37 | -0.55 | 0.45 | 77.15 | 32.23
2019-09-04 | 14:17 | 33.4609 | 0.06 | 1.06 | -0.64 | 0.36 | -0.55 | 0.45 | 77.15 | 32.23
2019-09-04 | 14:17 | 33.5625 | 0.07 | 1.07 | -0.64 | 0.36 | -0.56 | 0.44 | 76.17 | 32.23
2019-09-04 | 14:17 | 33.6719 | 0.06 | 1.06 | -0.65 | 0.35 | -0.57 | 0.43 | 77.15 | 32.23
2019-09-04 | 14:17 | 33.7695 | 0.06 | 1.06 | -0.64 | 0.36 | -0.57 | 0.43 | 78.12 | 33.2
2019-09-04 | 14:17 | 33.8711 | 0.06 | 1.06 | -0.66 | 0.34 | -0.58 | 0.42 | 77.15 | 32.23
2019-09-04 | 14:17 | 33.9727 | 0.08 | 1.08 | -0.66 | 0.34 | -0.57 | 0.43 | 77.15 | 33.2
2019-09-04 | 14:17 | 34.082 | 0.06 | 1.06 | -0.67 | 0.33 | -0.58 | 0.42 | 77.15 | 31.25
2019-09-04 | 14:17 | 34.1797 | 0.08 | 1.08 | -0.66 | 0.34 | -0.58 | 0.42 | 78.12 | 33.2
2019-09-04 | 14:17 | 34.2812 | 0.03 | 1.03 | -0.61 | 0.39 | -0.57 | 0.43 | 77.15 | 34.18
2019-09-04 | 14:17 | 34.3906 | -0.03 | 0.97 | -0.55 | 0.45 | -0.55 | 0.45 | 78.12 | 34.18
2019-09-04 | 14:17 | 34.4922 | -0.08 | 0.92 | -0.51 | 0.49 | -0.54 | 0.46 | 79.1 | 35.16
2019-09-04 | 14:17 | 34.5898 | -0.08 | 0.92 | -0.51 | 0.49 | -0.55 | 0.45 | 77.15 | 36.13
2019-09-04 | 14:17 | 34.6914 | 0.03 | 1.03 | -0.63 | 0.37 | -0.54 | 0.46 | 77.15 | 34.18
2019-09-04 | 14:17 | 34.8008 | 0.05 | 1.05 | -0.63 | 0.37 | -0.55 | 0.45 | 78.12 | 36.13
2019-09-04 | 14:17 | 34.9023 | 0.06 | 1.06 | -0.65 | 0.35 | -0.56 | 0.44 | 77.15 | 32.23
2019-09-04 | 14:17 | 35 | 0.08 | 1.08 | -0.65 | 0.35 | -0.57 | 0.43 | 79.1 | 34.18
2019-09-04 | 14:17 | 35.1016 | 0.07 | 1.07 | -0.65 | 0.35 | -0.57 | 0.43 | 77.15 | 34.18
2019-09-04 | 14:17 | 35.2109 | 0.07 | 1.07 | -0.66 | 0.34 | -0.56 | 0.44 | 78.12 | 35.16
2019-09-04 | 14:17 | 35.3125 | 0.07 | 1.07 | -0.65 | 0.35 | -0.58 | 0.42 | 77.15 | 34.18
2019-09-04 | 14:17 | 35.4102 | 0.07 | 1.07 | -0.66 | 0.34 | -0.58 | 0.42 | 78.12 | 34.18
2019-09-04 | 14:17 | 35.5195 | 0.09 | 1.09 | -0.66 | 0.34 | -0.58 | 0.42 | 78.12 | 34.18
2019-09-04 | 14:17 | 35.6211 | 0.06 | 1.06 | -0.66 | 0.34 | -0.59 | 0.41 | 77.15 | 34.18
2019-09-04 | 14:17 | 35.7227 | 0.08 | 1.08 | -0.67 | 0.33 | -0.59 | 0.41 | 77.15 | 33.2
2019-09-04 | 14:17 | 35.832 | -0.03 | 0.97 | -0.57 | 0.43 | -0.56 | 0.44 | 77.15 | 36.13
2019-09-04 | 14:17 | 35.9297 | -0.08 | 0.92 | -0.54 | 0.46 | -0.56 | 0.44 | 77.15 | 34.18
2019-09-04 | 14:17 | 36.0312 | -0.07 | 0.93 | -0.52 | 0.48 | -0.55 | 0.45 | 76.17 | 34.18
2019-09-04 | 14:17 | 36.1289 | -0.08 | 0.92 | -0.52 | 0.48 | -0.54 | 0.46 | 78.12 | 36.13
2019-09-04 | 14:17 | 36.2305 | 0.04 | 1.04 | -0.64 | 0.36 | -0.56 | 0.44 | 77.15 | 36.13
2019-09-04 | 14:17 | 36.3398 | 0.05 | 1.05 | -0.64 | 0.36 | -0.56 | 0.44 | 78.12 | 36.13
2019-09-04 | 14:17 | 36.4414 | 0.07 | 1.07 | -0.66 | 0.34 | -0.58 | 0.42 | 77.15 | 33.2
2019-09-04 | 14:17 | 36.5391 | 0.05 | 1.05 | -0.65 | 0.35 | -0.57 | 0.43 | 77.15 | 35.16
2019-09-04 | 14:17 | 36.6406 | 0.06 | 1.06 | -0.66 | 0.34 | -0.57 | 0.43 | 78.12 | 35.16
2019-09-04 | 14:17 | 36.75 | 0.06 | 1.06 | -0.65 | 0.35 | -0.58 | 0.42 | 77.15 | 36.13
2019-09-04 | 14:17 | 36.8516 | 0.07 | 1.07 | -0.66 | 0.34 | -0.58 | 0.42 | 78.12 | 35.16
2019-09-04 | 14:17 | 36.9609 | 0.07 | 1.07 | -0.67 | 0.33 | -0.58 | 0.42 | 78.12 | 36.13
2019-09-04 | 14:17 | 37.0625 | 0.07 | 1.07 | -0.66 | 0.34 | -0.58 | 0.42 | 78.12 | 36.13
2019-09-04 | 14:17 | 37.1602 | 0.06 | 1.06 | -0.67 | 0.33 | -0.59 | 0.41 | 78.12 | 36.13
2019-09-04 | 14:17 | 37.2617 | 0.02 | 1.02 | -0.6 | 0.4 | -0.58 | 0.42 | 77.15 | 33.2
2019-09-04 | 14:17 | 37.3711 | -0.06 | 0.94 | -0.53 | 0.47 | -0.56 | 0.44 | 77.15 | 35.16
2019-09-04 | 14:17 | 37.4727 | -0.1 | 0.9 | -0.53 | 0.47 | -0.55 | 0.45 | 79.1 | 35.16
2019-09-04 | 14:17 | 37.5703 | -0.09 | 0.91 | -0.51 | 0.49 | -0.55 | 0.45 | 77.15 | 36.13
2019-09-04 | 14:17 | 37.6719 | 0.04 | 1.04 | -0.62 | 0.38 | -0.55 | 0.45 | 78.12 | 35.16
2019-09-04 | 14:17 | 37.7812 | 0.07 | 1.07 | -0.62 | 0.38 | -0.56 | 0.44 | 80.08 | 37.11
2019-09-04 | 14:17 | 37.8789 | 0.05 | 1.05 | -0.64 | 0.36 | -0.56 | 0.44 | 77.15 | 36.13
2019-09-04 | 14:17 | 37.9805 | 0.06 | 1.06 | -0.65 | 0.35 | -0.57 | 0.43 | 78.12 | 36.13
2019-09-04 | 14:17 | 38.0898 | 0.06 | 1.06 | -0.64 | 0.36 | -0.57 | 0.43 | 78.12 | 35.16
2019-09-04 | 14:17 | 38.1914 | 0.07 | 1.07 | -0.66 | 0.34 | -0.58 | 0.42 | 79.1 | 36.13
2019-09-04 | 14:17 | 38.2891 | 0.07 | 1.07 | -0.66 | 0.34 | -0.58 | 0.42 | 78.12 | 37.11
2019-09-04 | 14:17 | 38.3906 | 0.07 | 1.07 | -0.66 | 0.34 | -0.59 | 0.41 | 77.15 | 36.13
2019-09-04 | 14:17 | 38.5 | 0.06 | 1.06 | -0.67 | 0.33 | -0.59 | 0.41 | 79.1 | 35.16
2019-09-04 | 14:17 | 38.6016 | 0.09 | 1.09 | -0.66 | 0.34 | -0.59 | 0.41 | 79.1 | 36.13
2019-09-04 | 14:17 | 38.6992 | 0.06 | 1.06 | -0.66 | 0.34 | -0.58 | 0.42 | 79.1 | 38.09
2019-09-04 | 14:17 | 38.8125 | -0.04 | 0.96 | -0.57 | 0.43 | -0.57 | 0.43 | 78.12 | 33.2
2019-09-04 | 14:17 | 38.9102 | -0.08 | 0.92 | -0.52 | 0.48 | -0.56 | 0.44 | 78.12 | 35.16
2019-09-04 | 14:17 | 39.0117 | -0.07 | 0.93 | -0.53 | 0.47 | -0.54 | 0.46 | 79.1 | 36.13
2019-09-04 | 14:17 | 39.1094 | -0.09 | 0.91 | -0.52 | 0.48 | -0.54 | 0.46 | 79.1 | 34.18
2019-09-04 | 14:17 | 39.2227 | 0.06 | 1.06 | -0.64 | 0.36 | -0.56 | 0.44 | 79.1 | 37.11
2019-09-04 | 14:17 | 39.3203 | 0.07 | 1.07 | -0.65 | 0.35 | -0.57 | 0.43 | 78.12 | 36.13
2019-09-04 | 14:17 | 39.4219 | 0.07 | 1.07 | -0.65 | 0.35 | -0.56 | 0.44 | 79.1 | 36.13
2019-09-04 | 14:17 | 39.5195 | 0.09 | 1.09 | -0.65 | 0.35 | -0.57 | 0.43 | 78.12 | 36.13
2019-09-04 | 14:17 | 39.6289 | 0.07 | 1.07 | -0.65 | 0.35 | -0.58 | 0.42 | 78.12 | 33.2
2019-09-04 | 14:17 | 39.7305 | 0.08 | 1.08 | -0.67 | 0.33 | -0.58 | 0.42 | 78.12 | 36.13
2019-09-04 | 14:17 | 39.832 | 0.07 | 1.07 | -0.67 | 0.33 | -0.58 | 0.42 | 77.15 | 36.13
2019-09-04 | 14:17 | 39.9297 | 0.06 | 1.06 | -0.66 | 0.34 | -0.59 | 0.41 | 77.15 | 35.16
2019-09-04 | 14:17 | 40.0391 | 0.09 | 1.09 | -0.68 | 0.32 | -0.58 | 0.42 | 79.1 | 37.11
2019-09-04 | 14:17 | 40.1406 | 0.06 | 1.06 | -0.66 | 0.34 | -0.6 | 0.4 | 78.12 | 37.11
2019-09-04 | 14:17 | 40.2422 | 0.05 | 1.05 | -0.65 | 0.35 | -0.59 | 0.41 | 78.12 | 36.13
2019-09-04 | 14:17 | 40.3516 | -0.04 | 0.96 | -0.55 | 0.45 | -0.57 | 0.43 | 78.12 | 36.13
2019-09-04 | 14:17 | 40.4492 | -0.07 | 0.93 | -0.54 | 0.46 | -0.56 | 0.44 | 78.12 | 35.16
2019-09-04 | 14:17 | 40.5508 | -0.09 | 0.91 | -0.53 | 0.47 | -0.56 | 0.44 | 78.12 | 36.13
2019-09-04 | 14:17 | 40.6602 | -0.03 | 0.97 | -0.57 | 0.43 | -0.54 | 0.46 | 79.1 | 36.13
2019-09-04 | 14:17 | 40.7617 | 0.04 | 1.04 | -0.65 | 0.35 | -0.57 | 0.43 | 77.15 | 35.16
2019-09-04 | 14:17 | 40.8594 | 0.05 | 1.05 | -0.66 | 0.34 | -0.56 | 0.44 | 77.15 | 37.11
2019-09-04 | 14:17 | 40.9609 | 0.06 | 1.06 | -0.66 | 0.34 | -0.57 | 0.43 | 79.1 | 36.13
2019-09-04 | 14:17 | 41.0625 | 0.06 | 1.06 | -0.65 | 0.35 | -0.58 | 0.42 | 79.1 | 36.13
2019-09-04 | 14:17 | 41.1719 | 0.05 | 1.05 | -0.67 | 0.33 | -0.59 | 0.41 | 77.15 | 33.2
2019-09-04 | 14:17 | 41.2695 | 0.07 | 1.07 | -0.68 | 0.32 | -0.59 | 0.41 | 79.1 | 35.16
2019-09-04 | 14:17 | 41.3711 | 0.06 | 1.06 | -0.68 | 0.32 | -0.6 | 0.4 | 78.12 | 37.11
2019-09-04 | 14:17 | 41.4727 | 0.06 | 1.06 | -0.68 | 0.32 | -0.6 | 0.4 | 78.12 | 36.13
2019-09-04 | 14:17 | 41.582 | 0.07 | 1.07 | -0.68 | 0.32 | -0.59 | 0.41 | 77.15 | 37.11
2019-09-04 | 14:17 | 41.6797 | 0.07 | 1.07 | -0.68 | 0.32 | -0.6 | 0.4 | 78.12 | 38.09
2019-09-04 | 14:17 | 41.7891 | 0.03 | 1.03 | -0.63 | 0.37 | -0.59 | 0.41 | 78.12 | 37.11
2019-09-04 | 14:17 | 41.8906 | -0.05 | 0.95 | -0.58 | 0.42 | -0.56 | 0.44 | 79.1 | 37.11
2019-09-04 | 14:17 | 41.9922 | -0.09 | 0.91 | -0.53 | 0.47 | -0.57 | 0.43 | 77.15 | 33.2
2019-09-04 | 14:17 | 42.0898 | -0.08 | 0.92 | -0.51 | 0.49 | -0.56 | 0.44 | 77.15 | 35.16
2019-09-04 | 14:17 | 42.1914 | 0.04 | 1.04 | -0.64 | 0.36 | -0.55 | 0.45 | 79.1 | 37.11
2019-09-04 | 14:17 | 42.3008 | 0.05 | 1.05 | -0.65 | 0.35 | -0.58 | 0.42 | 80.08 | 37.11
2019-09-04 | 14:17 | 42.4023 | 0.05 | 1.05 | -0.67 | 0.33 | -0.58 | 0.42 | 78.12 | 37.11
2019-09-04 | 14:17 | 42.5 | 0.06 | 1.06 | -0.67 | 0.33 | -0.58 | 0.42 | 78.12 | 37.11
2019-09-04 | 14:17 | 42.6016 | 0.08 | 1.08 | -0.67 | 0.33 | -0.59 | 0.41 | 78.12 | 37.11
2019-09-04 | 14:17 | 42.7109 | 0.09 | 1.09 | -0.68 | 0.32 | -0.6 | 0.4 | 79.1 | 39.06
2019-09-04 | 14:17 | 42.8125 | 0.09 | 1.09 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 36.13
2019-09-04 | 14:17 | 42.9219 | 0.05 | 1.05 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 37.11
2019-09-04 | 14:17 | 43.0195 | 0.07 | 1.07 | -0.67 | 0.33 | -0.6 | 0.4 | 78.12 | 37.11
2019-09-04 | 14:17 | 43.1211 | 0.08 | 1.08 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 36.13
2019-09-04 | 14:17 | 43.2227 | 0.07 | 1.07 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 38.09
2019-09-04 | 14:17 | 43.332 | -0.02 | 0.98 | -0.61 | 0.39 | -0.58 | 0.42 | 78.12 | 38.09
2019-09-04 | 14:17 | 43.4297 | -0.07 | 0.93 | -0.56 | 0.44 | -0.57 | 0.43 | 78.12 | 37.11
2019-09-04 | 14:17 | 43.5312 | -0.08 | 0.92 | -0.55 | 0.45 | -0.56 | 0.44 | 78.12 | 36.13
2019-09-04 | 14:17 | 43.6406 | -0.1 | 0.9 | -0.54 | 0.46 | -0.56 | 0.44 | 78.12 | 37.11
2019-09-04 | 14:17 | 43.7422 | 0.04 | 1.04 | -0.67 | 0.33 | -0.57 | 0.43 | 79.1 | 36.13
2019-09-04 | 14:17 | 43.8398 | 0.05 | 1.05 | -0.67 | 0.33 | -0.58 | 0.42 | 79.1 | 36.13
2019-09-04 | 14:17 | 43.9414 | 0.06 | 1.06 | -0.68 | 0.32 | -0.57 | 0.43 | 77.15 | 37.11
2019-09-04 | 14:17 | 44.0508 | 0.05 | 1.05 | -0.68 | 0.32 | -0.58 | 0.42 | 79.1 | 37.11
2019-09-04 | 14:17 | 44.1523 | 0.06 | 1.06 | -0.68 | 0.32 | -0.59 | 0.41 | 79.1 | 39.06
2019-09-04 | 14:17 | 44.25 | 0.07 | 1.07 | -0.69 | 0.31 | -0.61 | 0.39 | 79.1 | 37.11
2019-09-04 | 14:17 | 44.3516 | 0.09 | 1.09 | -0.7 | 0.3 | -0.59 | 0.41 | 79.1 | 33.2
2019-09-04 | 14:17 | 44.4609 | 0.07 | 1.07 | -0.7 | 0.3 | -0.6 | 0.4 | 77.15 | 36.13
2019-09-04 | 14:17 | 44.5625 | 0.07 | 1.07 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 36.13
2019-09-04 | 14:17 | 44.6602 | 0.06 | 1.06 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 36.13
2019-09-04 | 14:17 | 44.7617 | 0.04 | 1.04 | -0.68 | 0.32 | -0.61 | 0.39 | 78.12 | 36.13
2019-09-04 | 14:17 | 44.8711 | -0.03 | 0.97 | -0.59 | 0.41 | -0.58 | 0.42 | 81.05 | 38.09
2019-09-04 | 14:17 | 44.9727 | -0.09 | 0.91 | -0.56 | 0.44 | -0.57 | 0.43 | 79.1 | 37.11
2019-09-04 | 14:17 | 45.0703 | -0.09 | 0.91 | -0.55 | 0.45 | -0.57 | 0.43 | 78.12 | 36.13
2019-09-04 | 14:17 | 45.1797 | 0.04 | 1.04 | -0.65 | 0.35 | -0.58 | 0.42 | 78.12 | 34.18
2019-09-04 | 14:17 | 45.2812 | 0.04 | 1.04 | -0.68 | 0.32 | -0.57 | 0.43 | 78.12 | 36.13
2019-09-04 | 14:17 | 45.3789 | 0.05 | 1.05 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 38.09
2019-09-04 | 14:17 | 45.4805 | 0.04 | 1.04 | -0.68 | 0.32 | -0.59 | 0.41 | 78.12 | 36.13
2019-09-04 | 14:17 | 45.5898 | 0.08 | 1.08 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 37.11
2019-09-04 | 14:17 | 45.6914 | 0.07 | 1.07 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 37.11
2019-09-04 | 14:17 | 45.7891 | 0.06 | 1.06 | -0.7 | 0.3 | -0.6 | 0.4 | 77.15 | 38.09
2019-09-04 | 14:17 | 45.8906 | 0.06 | 1.06 | -0.69 | 0.31 | -0.61 | 0.39 | 78.12 | 37.11
2019-09-04 | 14:17 | 46 | 0.07 | 1.07 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 34.18
2019-09-04 | 14:17 | 46.1016 | 0.06 | 1.06 | -0.7 | 0.3 | -0.62 | 0.38 | 78.12 | 36.13
2019-09-04 | 14:17 | 46.1992 | 0.06 | 1.06 | -0.69 | 0.31 | -0.61 | 0.39 | 79.1 | 36.13
2019-09-04 | 14:17 | 46.3008 | 0.01 | 1.01 | -0.63 | 0.37 | -0.6 | 0.4 | 79.1 | 38.09
2019-09-04 | 14:17 | 46.4102 | -0.09 | 0.91 | -0.58 | 0.42 | -0.58 | 0.42 | 78.12 | 36.13
2019-09-04 | 14:17 | 46.5117 | -0.07 | 0.93 | -0.56 | 0.44 | -0.57 | 0.43 | 78.12 | 37.11
2019-09-04 | 14:17 | 46.6094 | -0.1 | 0.9 | -0.55 | 0.45 | -0.56 | 0.44 | 78.12 | 38.09
2019-09-04 | 14:17 | 46.7227 | 0.05 | 1.05 | -0.66 | 0.34 | -0.58 | 0.42 | 78.12 | 34.18
2019-09-04 | 14:17 | 46.8203 | 0.05 | 1.05 | -0.67 | 0.33 | -0.59 | 0.41 | 77.15 | 35.16
2019-09-04 | 14:17 | 46.9219 | 0.05 | 1.05 | -0.69 | 0.31 | -0.59 | 0.41 | 77.15 | 36.13
2019-09-04 | 14:17 | 47.0195 | 0.05 | 1.05 | -0.68 | 0.32 | -0.6 | 0.4 | 79.1 | 36.13
2019-09-04 | 14:17 | 47.1289 | 0.06 | 1.06 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 38.09
2019-09-04 | 14:17 | 47.2305 | 0.06 | 1.06 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 38.09
2019-09-04 | 14:17 | 47.332 | 0.06 | 1.06 | -0.71 | 0.29 | -0.59 | 0.41 | 78.12 | 36.13
2019-09-04 | 14:17 | 47.4297 | 0.06 | 1.06 | -0.7 | 0.3 | -0.6 | 0.4 | 77.15 | 36.13
2019-09-04 | 14:17 | 47.5391 | 0.06 | 1.06 | -0.7 | 0.3 | -0.61 | 0.39 | 79.1 | 32.23
2019-09-04 | 14:17 | 47.6406 | 0.09 | 1.09 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 36.13
2019-09-04 | 14:17 | 47.75 | 0.06 | 1.06 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 37.11
2019-09-04 | 14:17 | 47.8516 | -0.02 | 0.98 | -0.61 | 0.39 | -0.59 | 0.41 | 79.1 | 36.13
2019-09-04 | 14:17 | 47.9492 | -0.06 | 0.94 | -0.58 | 0.42 | -0.58 | 0.42 | 78.12 | 37.11
2019-09-04 | 14:17 | 48.0508 | -0.09 | 0.91 | -0.55 | 0.45 | -0.58 | 0.42 | 77.15 | 37.11
2019-09-04 | 14:17 | 48.1523 | -0.09 | 0.91 | -0.56 | 0.44 | -0.57 | 0.43 | 77.15 | 36.13
2019-09-04 | 14:17 | 48.2617 | 0.04 | 1.04 | -0.67 | 0.33 | -0.59 | 0.41 | 78.12 | 37.11
2019-09-04 | 14:17 | 48.3594 | 0.05 | 1.05 | -0.69 | 0.31 | -0.6 | 0.4 | 78.12 | 33.2
2019-09-04 | 14:17 | 48.4609 | 0.04 | 1.04 | -0.69 | 0.31 | -0.58 | 0.42 | 78.12 | 36.13
2019-09-04 | 14:17 | 48.5625 | 0.08 | 1.08 | -0.7 | 0.3 | -0.59 | 0.41 | 77.15 | 36.13
2019-09-04 | 14:17 | 48.6719 | 0.06 | 1.06 | -0.7 | 0.3 | -0.6 | 0.4 | 77.15 | 36.13
2019-09-04 | 14:17 | 48.7695 | 0.06 | 1.06 | -0.71 | 0.29 | -0.6 | 0.4 | 78.12 | 36.13
2019-09-04 | 14:17 | 48.8789 | 0.06 | 1.06 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 37.11
2019-09-04 | 14:17 | 48.9805 | 0.06 | 1.06 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 37.11
2019-09-04 | 14:17 | 49.082 | 0.07 | 1.07 | -0.72 | 0.28 | -0.62 | 0.38 | 78.12 | 36.13
2019-09-04 | 14:17 | 49.1797 | 0.05 | 1.05 | -0.71 | 0.29 | -0.62 | 0.38 | 77.15 | 34.18
2019-09-04 | 14:17 | 49.2812 | 0.03 | 1.03 | -0.67 | 0.33 | -0.61 | 0.39 | 77.15 | 36.13
2019-09-04 | 14:17 | 49.3906 | -0.05 | 0.95 | -0.6 | 0.4 | -0.6 | 0.4 | 77.15 | 37.11
2019-09-04 | 14:17 | 49.4922 | -0.09 | 0.91 | -0.58 | 0.42 | -0.58 | 0.42 | 77.15 | 36.13
2019-09-04 | 14:17 | 49.5898 | -0.08 | 0.92 | -0.57 | 0.43 | -0.58 | 0.42 | 78.12 | 36.13
2019-09-04 | 14:17 | 49.6914 | 0.04 | 1.04 | -0.68 | 0.32 | -0.59 | 0.41 | 77.15 | 37.11
2019-09-04 | 14:17 | 49.8008 | 0.06 | 1.06 | -0.69 | 0.31 | -0.59 | 0.41 | 77.15 | 37.11
2019-09-04 | 14:17 | 49.9023 | 0.05 | 1.05 | -0.69 | 0.31 | -0.59 | 0.41 | 78.12 | 36.13
2019-09-04 | 14:17 | 50.0117 | 0.05 | 1.05 | -0.7 | 0.3 | -0.6 | 0.4 | 78.12 | 34.18
2019-09-04 | 14:17 | 50.1094 | 0.08 | 1.08 | -0.69 | 0.31 | -0.59 | 0.41 | 79.1 | 38.09
2019-09-04 | 14:17 | 50.2109 | 0.06 | 1.06 | -0.7 | 0.3 | -0.62 | 0.38 | 78.12 | 37.11
2019-09-04 | 14:17 | 50.3125 | 0.07 | 1.07 | -0.72 | 0.28 | -0.6 | 0.4 | 76.17 | 35.16
2019-09-04 | 14:17 | 50.4219 | 0.07 | 1.07 | -0.71 | 0.29 | -0.61 | 0.39 | 78.12 | 36.13
2019-09-04 | 14:17 | 50.5195 | 0.07 | 1.07 | -0.72 | 0.28 | -0.61 | 0.39 | 77.15 | 37.11
2019-09-04 | 14:17 | 50.6211 | 0.07 | 1.07 | -0.71 | 0.29 | -0.62 | 0.38 | 79.1 | 36.13
2019-09-04 | 14:17 | 50.7305 | 0.06 | 1.06 | -0.71 | 0.29 | -0.62 | 0.38 | 77.15 | 36.13
2019-09-04 | 14:17 | 50.832 | 0.02 | 1.02 | -0.67 | 0.33 | -0.61 | 0.39 | 78.12 | 33.2
2019-09-04 | 14:17 | 50.9297 | -0.05 | 0.95 | -0.59 | 0.41 | -0.59 | 0.41 | 79.1 | 37.11
2019-09-04 | 14:17 | 51.0312 | -0.08 | 0.92 | -0.58 | 0.42 | -0.59 | 0.41 | 77.15 | 35.16
2019-09-04 | 14:17 | 51.1406 | -0.07 | 0.93 | -0.56 | 0.44 | -0.58 | 0.42 | 78.12 | 35.16
2019-09-04 | 14:17 | 51.2422 | 0.04 | 1.04 | -0.68 | 0.32 | -0.59 | 0.41 | 77.15 | 36.13
2019-09-04 | 14:17 | 51.3398 | 0.05 | 1.05 | -0.7 | 0.3 | -0.6 | 0.4 | 77.15 | 35.16
2019-09-04 | 14:17 | 51.4414 | 0.07 | 1.07 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 37.11
2019-09-04 | 14:17 | 51.5508 | 0.06 | 1.06 | -0.71 | 0.29 | -0.62 | 0.38 | 78.12 | 36.13
2019-09-04 | 14:17 | 51.6523 | 0.06 | 1.06 | -0.72 | 0.28 | -0.61 | 0.39 | 78.12 | 34.18
2019-09-04 | 14:17 | 51.75 | 0.07 | 1.07 | -0.71 | 0.29 | -0.63 | 0.37 | 79.1 | 36.13
2019-09-04 | 14:17 | 51.8516 | 0.07 | 1.07 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 35.16
2019-09-04 | 14:17 | 51.9609 | 0.07 | 1.07 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 36.13
2019-09-04 | 14:17 | 52.0625 | 0.08 | 1.08 | -0.73 | 0.27 | -0.65 | 0.35 | 78.12 | 35.16
2019-09-04 | 14:17 | 52.1602 | 0.06 | 1.06 | -0.74 | 0.26 | -0.64 | 0.36 | 79.1 | 36.13
2019-09-04 | 14:17 | 52.2617 | 0.07 | 1.07 | -0.73 | 0.27 | -0.64 | 0.36 | 79.1 | 36.13
2019-09-04 | 14:17 | 52.3711 | 0 | 1 | -0.66 | 0.34 | -0.63 | 0.37 | 79.1 | 33.2
2019-09-04 | 14:17 | 52.4727 | -0.09 | 0.91 | -0.61 | 0.39 | -0.61 | 0.39 | 78.12 | 35.16
2019-09-04 | 14:17 | 52.5703 | -0.06 | 0.94 | -0.59 | 0.41 | -0.6 | 0.4 | 78.12 | 37.11
2019-09-04 | 14:17 | 52.6797 | 0.03 | 1.03 | -0.67 | 0.33 | -0.59 | 0.41 | 77.15 | 35.16
2019-09-04 | 14:17 | 52.7812 | 0.06 | 1.06 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 36.13
2019-09-04 | 14:17 | 52.8789 | 0.05 | 1.05 | -0.71 | 0.29 | -0.61 | 0.39 | 79.1 | 36.13
2019-09-04 | 14:17 | 52.9805 | 0.07 | 1.07 | -0.72 | 0.28 | -0.63 | 0.37 | 80.08 | 35.16
2019-09-04 | 14:17 | 53.0898 | 0.09 | 1.09 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 36.13
2019-09-04 | 14:17 | 53.1914 | 0.06 | 1.06 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 32.23
2019-09-04 | 14:17 | 53.2891 | 0.07 | 1.07 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 33.2
2019-09-04 | 14:17 | 53.3906 | 0.06 | 1.06 | -0.73 | 0.27 | -0.64 | 0.36 | 77.15 | 35.16
2019-09-04 | 14:17 | 53.5 | 0.08 | 1.08 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 36.13
2019-09-04 | 14:17 | 53.6016 | 0.07 | 1.07 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 35.16
2019-09-04 | 14:17 | 53.6992 | 0.07 | 1.07 | -0.73 | 0.27 | -0.65 | 0.35 | 78.12 | 36.13
2019-09-04 | 14:17 | 53.8125 | 0.01 | 1.01 | -0.68 | 0.32 | -0.63 | 0.37 | 78.12 | 35.16
2019-09-04 | 14:17 | 53.9102 | -0.07 | 0.93 | -0.61 | 0.39 | -0.62 | 0.38 | 78.12 | 36.13
2019-09-04 | 14:17 | 54.0117 | -0.09 | 0.91 | -0.59 | 0.41 | -0.61 | 0.39 | 79.1 | 37.11
2019-09-04 | 14:17 | 54.1094 | -0.09 | 0.91 | -0.58 | 0.42 | -0.6 | 0.4 | 76.17 | 33.2
2019-09-04 | 14:17 | 54.2227 | 0.04 | 1.04 | -0.7 | 0.3 | -0.61 | 0.39 | 78.12 | 36.13
2019-09-04 | 14:17 | 54.3203 | 0.06 | 1.06 | -0.71 | 0.29 | -0.61 | 0.39 | 77.15 | 36.13
2019-09-04 | 14:17 | 54.4219 | 0.07 | 1.07 | -0.72 | 0.28 | -0.63 | 0.37 | 79.1 | 36.13
2019-09-04 | 14:17 | 54.5195 | 0.07 | 1.07 | -0.71 | 0.29 | -0.62 | 0.38 | 77.15 | 34.18
2019-09-04 | 14:17 | 54.6289 | 0.06 | 1.06 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 37.11
2019-09-04 | 14:17 | 54.7305 | 0.07 | 1.07 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 35.16
2019-09-04 | 14:17 | 54.8398 | 0.06 | 1.06 | -0.73 | 0.27 | -0.63 | 0.37 | 77.15 | 35.16
2019-09-04 | 14:17 | 54.9414 | 0.08 | 1.08 | -0.73 | 0.27 | -0.64 | 0.36 | 77.15 | 32.23
2019-09-04 | 14:17 | 55.0391 | 0.07 | 1.07 | -0.74 | 0.26 | -0.65 | 0.35 | 80.08 | 37.11
2019-09-04 | 14:17 | 55.1406 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 77.15 | 34.18
2019-09-04 | 14:17 | 55.25 | 0.08 | 1.08 | -0.74 | 0.26 | -0.64 | 0.36 | 79.1 | 37.11
2019-09-04 | 14:17 | 55.3516 | 0.02 | 1.02 | -0.68 | 0.32 | -0.63 | 0.37 | 78.12 | 34.18
2019-09-04 | 14:17 | 55.4492 | -0.05 | 0.95 | -0.61 | 0.39 | -0.62 | 0.38 | 80.08 | 36.13
2019-09-04 | 14:17 | 55.5508 | -0.09 | 0.91 | -0.6 | 0.4 | -0.61 | 0.39 | 78.12 | 35.16
2019-09-04 | 14:17 | 55.6602 | -0.1 | 0.9 | -0.58 | 0.42 | -0.61 | 0.39 | 77.15 | 36.13
2019-09-04 | 14:17 | 55.7617 | 0.05 | 1.05 | -0.71 | 0.29 | -0.63 | 0.37 | 78.12 | 35.16
2019-09-04 | 14:17 | 55.8594 | 0.06 | 1.06 | -0.73 | 0.27 | -0.63 | 0.37 | 78.12 | 34.18
2019-09-04 | 14:17 | 55.9727 | 0.06 | 1.06 | -0.73 | 0.27 | -0.62 | 0.38 | 79.1 | 36.13
2019-09-04 | 14:17 | 56.0703 | 0.07 | 1.07 | -0.74 | 0.26 | -0.62 | 0.38 | 80.08 | 36.13
2019-09-04 | 14:17 | 56.1719 | 0.07 | 1.07 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 35.16
2019-09-04 | 14:17 | 56.2695 | 0.08 | 1.08 | -0.74 | 0.26 | -0.64 | 0.36 | 78.12 | 36.13
2019-09-04 | 14:17 | 56.3789 | 0.07 | 1.07 | -0.75 | 0.25 | -0.65 | 0.35 | 77.15 | 34.18
2019-09-04 | 14:17 | 56.4805 | 0.08 | 1.08 | -0.76 | 0.24 | -0.65 | 0.35 | 78.12 | 36.13
2019-09-04 | 14:17 | 56.582 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 76.17 | 33.2
2019-09-04 | 14:17 | 56.6797 | 0.08 | 1.08 | -0.75 | 0.25 | -0.65 | 0.35 | 77.15 | 34.18
2019-09-04 | 14:17 | 56.7891 | 0.04 | 1.04 | -0.73 | 0.27 | -0.65 | 0.35 | 77.15 | 34.18
2019-09-04 | 14:17 | 56.8906 | -0.03 | 0.97 | -0.64 | 0.36 | -0.64 | 0.36 | 78.12 | 34.18
2019-09-04 | 14:17 | 56.9922 | -0.08 | 0.92 | -0.6 | 0.4 | -0.61 | 0.39 | 78.12 | 34.18
2019-09-04 | 14:17 | 57.1016 | -0.09 | 0.91 | -0.6 | 0.4 | -0.62 | 0.38 | 78.12 | 35.16
2019-09-04 | 14:17 | 57.1992 | 0.04 | 1.04 | -0.7 | 0.3 | -0.61 | 0.39 | 77.15 | 34.18
2019-09-04 | 14:17 | 57.3008 | 0.05 | 1.05 | -0.72 | 0.28 | -0.63 | 0.37 | 77.15 | 35.16
2019-09-04 | 14:17 | 57.4023 | 0.06 | 1.06 | -0.74 | 0.26 | -0.64 | 0.36 | 79.1 | 35.16
2019-09-04 | 14:17 | 57.5117 | 0.06 | 1.06 | -0.74 | 0.26 | -0.63 | 0.37 | 77.15 | 36.13
2019-09-04 | 14:17 | 57.6094 | 0.06 | 1.06 | -0.74 | 0.26 | -0.64 | 0.36 | 77.15 | 34.18
2019-09-04 | 14:17 | 57.7109 | 0.08 | 1.08 | -0.74 | 0.26 | -0.64 | 0.36 | 78.12 | 34.18
2019-09-04 | 14:17 | 57.8125 | 0.06 | 1.06 | -0.75 | 0.25 | -0.65 | 0.35 | 77.15 | 35.16
2019-09-04 | 14:17 | 57.9219 | 0.09 | 1.09 | -0.75 | 0.25 | -0.65 | 0.35 | 78.12 | 34.18
2019-09-04 | 14:17 | 58.0195 | 0.07 | 1.07 | -0.77 | 0.23 | -0.65 | 0.35 | 77.15 | 34.18
2019-09-04 | 14:17 | 58.1211 | 0.08 | 1.08 | -0.75 | 0.25 | -0.66 | 0.34 | 78.12 | 35.16
2019-09-04 | 14:17 | 58.2227 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 77.15 | 33.2
2019-09-04 | 14:17 | 58.332 | 0.02 | 1.02 | -0.7 | 0.3 | -0.64 | 0.36 | 79.1 | 35.16
2019-09-04 | 14:17 | 58.4297 | -0.04 | 0.96 | -0.63 | 0.37 | -0.63 | 0.37 | 77.15 | 35.16
2019-09-04 | 14:17 | 58.5312 | -0.08 | 0.92 | -0.6 | 0.4 | -0.62 | 0.38 | 78.12 | 35.16
2019-09-04 | 14:17 | 58.6406 | -0.12 | 0.88 | -0.58 | 0.42 | -0.61 | 0.39 | 80.08 | 35.16
2019-09-04 | 14:17 | 58.7422 | 0.03 | 1.03 | -0.72 | 0.28 | -0.63 | 0.37 | 79.1 | 35.16
2019-09-04 | 14:17 | 58.8398 | 0.07 | 1.07 | -0.72 | 0.28 | -0.63 | 0.37 | 79.1 | 36.13
2019-09-04 | 14:17 | 58.9414 | 0.06 | 1.06 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 35.16
2019-09-04 | 14:17 | 59.0508 | 0.04 | 1.04 | -0.74 | 0.26 | -0.64 | 0.36 | 80.08 | 33.2
2019-09-04 | 14:17 | 59.1523 | 0.07 | 1.07 | -0.75 | 0.25 | -0.64 | 0.36 | 77.15 | 34.18
2019-09-04 | 14:17 | 59.25 | 0.06 | 1.06 | -0.75 | 0.25 | -0.65 | 0.35 | 78.12 | 34.18
2019-09-04 | 14:17 | 59.3516 | 0.06 | 1.06 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 59.4609 | 0.06 | 1.06 | -0.76 | 0.24 | -0.64 | 0.36 | 78.12 | 33.2
2019-09-04 | 14:17 | 59.5625 | 0.08 | 1.08 | -0.77 | 0.23 | -0.66 | 0.34 | 77.15 | 34.18
2019-09-04 | 14:17 | 59.6602 | 0.11 | 1.11 | -0.78 | 0.22 | -0.65 | 0.35 | 77.15 | 35.16
2019-09-04 | 14:17 | 59.7695 | 0.08 | 1.08 | -0.77 | 0.23 | -0.67 | 0.33 | 78.12 | 36.13
2019-09-04 | 14:17 | 59.8711 | -0.02 | 0.98 | -0.68 | 0.32 | -0.66 | 0.34 | 77.15 | 33.2
2019-09-04 | 14:17 | 59.9727 | -0.06 | 0.94 | -0.64 | 0.36 | -0.64 | 0.36 | 78.12 | 35.16
2019-09-04 | 14:17 | 60.0703 | -0.09 | 0.91 | -0.61 | 0.39 | -0.63 | 0.37 | 78.12 | 34.18
2019-09-04 | 14:17 | 60.1797 | -0.01 | 0.99 | -0.68 | 0.32 | -0.62 | 0.38 | 78.12 | 34.18
2019-09-04 | 14:17 | 60.2812 | 0.04 | 1.04 | -0.74 | 0.26 | -0.63 | 0.37 | 78.12 | 35.16
2019-09-04 | 14:17 | 60.3789 | 0.05 | 1.05 | -0.75 | 0.25 | -0.63 | 0.37 | 77.15 | 35.16
2019-09-04 | 14:17 | 60.4805 | 0.06 | 1.06 | -0.75 | 0.25 | -0.64 | 0.36 | 78.12 | 34.18
2019-09-04 | 14:17 | 60.5898 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 77.15 | 33.2
2019-09-04 | 14:17 | 60.6914 | 0.04 | 1.04 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 60.8008 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 78.12 | 33.2
2019-09-04 | 14:17 | 60.9023 | 0.07 | 1.07 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 61 | 0.05 | 1.05 | -0.77 | 0.23 | -0.65 | 0.35 | 76.17 | 35.16
2019-09-04 | 14:17 | 61.1016 | 0.05 | 1.05 | -0.77 | 0.23 | -0.66 | 0.34 | 78.12 | 34.18
2019-09-04 | 14:17 | 61.1992 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 33.2
2019-09-04 | 14:17 | 61.3125 | 0.06 | 1.06 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 61.4102 | -0.03 | 0.97 | -0.66 | 0.34 | -0.64 | 0.36 | 77.15 | 34.18
2019-09-04 | 14:17 | 61.5117 | -0.08 | 0.92 | -0.62 | 0.38 | -0.63 | 0.37 | 76.17 | 31.25
2019-09-04 | 14:17 | 61.6211 | -0.1 | 0.9 | -0.6 | 0.4 | -0.62 | 0.38 | 76.17 | 34.18
2019-09-04 | 14:17 | 61.7227 | 0.03 | 1.03 | -0.73 | 0.27 | -0.64 | 0.36 | 77.15 | 33.2
2019-09-04 | 14:17 | 61.8203 | 0.07 | 1.07 | -0.75 | 0.25 | -0.64 | 0.36 | 76.17 | 33.2
2019-09-04 | 14:17 | 61.9297 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 77.15 | 34.18
2019-09-04 | 14:17 | 62.0312 | 0.06 | 1.06 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 34.18
2019-09-04 | 14:17 | 62.1289 | 0.07 | 1.07 | -0.75 | 0.25 | -0.64 | 0.36 | 78.12 | 34.18
2019-09-04 | 14:17 | 62.2305 | 0.08 | 1.08 | -0.77 | 0.23 | -0.65 | 0.35 | 76.17 | 34.18
2019-09-04 | 14:17 | 62.3398 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 32.23
2019-09-04 | 14:17 | 62.4414 | 0.08 | 1.08 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 62.5391 | 0.08 | 1.08 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:17 | 62.6523 | 0.07 | 1.07 | -0.78 | 0.22 | -0.67 | 0.33 | 78.12 | 33.2
2019-09-04 | 14:17 | 62.75 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 33.2
2019-09-04 | 14:17 | 62.8516 | 0.02 | 1.02 | -0.71 | 0.29 | -0.67 | 0.33 | 76.17 | 34.18
2019-09-04 | 14:17 | 62.9492 | -0.08 | 0.92 | -0.64 | 0.36 | -0.64 | 0.36 | 76.17 | 34.18
2019-09-04 | 14:17 | 63.0625 | -0.12 | 0.88 | -0.62 | 0.38 | -0.63 | 0.37 | 76.17 | 33.2
2019-09-04 | 14:17 | 63.1602 | -0.09 | 0.91 | -0.59 | 0.41 | -0.63 | 0.37 | 76.17 | 31.25
2019-09-04 | 14:17 | 63.2617 | 0.04 | 1.04 | -0.74 | 0.26 | -0.65 | 0.35 | 76.17 | 33.2
2019-09-04 | 14:17 | 63.3594 | 0.05 | 1.05 | -0.75 | 0.25 | -0.64 | 0.36 | 77.15 | 33.2
2019-09-04 | 14:17 | 63.4727 | 0.05 | 1.05 | -0.75 | 0.25 | -0.67 | 0.33 | 77.15 | 32.23
2019-09-04 | 14:17 | 63.5703 | 0.07 | 1.07 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 63.6719 | 0.07 | 1.07 | -0.78 | 0.22 | -0.66 | 0.34 | 75.2 | 34.18
2019-09-04 | 14:17 | 63.7695 | 0.07 | 1.07 | -0.77 | 0.23 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 63.8789 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 77.15 | 33.2
2019-09-04 | 14:17 | 63.9805 | 0.07 | 1.07 | -0.78 | 0.22 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 64.082 | 0.07 | 1.07 | -0.78 | 0.22 | -0.66 | 0.34 | 76.17 | 34.18
2019-09-04 | 14:17 | 64.1797 | 0.08 | 1.08 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 64.2891 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 76.17 | 33.2
2019-09-04 | 14:17 | 64.3906 | -0.03 | 0.97 | -0.66 | 0.34 | -0.65 | 0.35 | 76.17 | 35.16
2019-09-04 | 14:17 | 64.4922 | -0.09 | 0.91 | -0.61 | 0.39 | -0.65 | 0.35 | 77.15 | 34.18
2019-09-04 | 14:17 | 64.6016 | -0.11 | 0.89 | -0.6 | 0.4 | -0.64 | 0.36 | 76.17 | 33.2
2019-09-04 | 14:17 | 64.6992 | 0.03 | 1.03 | -0.73 | 0.27 | -0.64 | 0.36 | 76.17 | 33.2
2019-09-04 | 14:17 | 64.8008 | 0.04 | 1.04 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 31.25
2019-09-04 | 14:17 | 64.9023 | 0.06 | 1.06 | -0.76 | 0.24 | -0.64 | 0.36 | 77.15 | 33.2
2019-09-04 | 14:17 | 65.0117 | 0.04 | 1.04 | -0.76 | 0.24 | -0.66 | 0.34 | 77.15 | 33.2
2019-09-04 | 14:17 | 65.1094 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 34.18
2019-09-04 | 14:17 | 65.2109 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 33.2
2019-09-04 | 14:17 | 65.3125 | 0.07 | 1.07 | -0.78 | 0.22 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 65.4219 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 65.5195 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 65.6211 | 0.06 | 1.06 | -0.78 | 0.22 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 65.7305 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 76.17 | 32.23
2019-09-04 | 14:17 | 65.832 | 0.02 | 1.02 | -0.72 | 0.28 | -0.66 | 0.34 | 77.15 | 32.23
2019-09-04 | 14:17 | 65.9297 | -0.06 | 0.94 | -0.65 | 0.35 | -0.65 | 0.35 | 77.15 | 32.23
2019-09-04 | 14:17 | 66.0312 | -0.11 | 0.89 | -0.6 | 0.4 | -0.64 | 0.36 | 75.2 | 33.2
2019-09-04 | 14:17 | 66.1406 | -0.08 | 0.92 | -0.61 | 0.39 | -0.63 | 0.37 | 76.17 | 33.2
2019-09-04 | 14:17 | 66.2422 | 0.04 | 1.04 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 32.23
2019-09-04 | 14:17 | 66.3398 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 32.23
2019-09-04 | 14:17 | 66.4414 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 76.17 | 31.25
2019-09-04 | 14:17 | 66.5508 | 0.06 | 1.06 | -0.75 | 0.25 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 66.6523 | 0.06 | 1.06 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 66.7617 | 0.06 | 1.06 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 34.18
2019-09-04 | 14:17 | 66.8594 | 0.08 | 1.08 | -0.76 | 0.24 | -0.66 | 0.34 | 77.15 | 34.18
2019-09-04 | 14:17 | 66.9609 | 0.06 | 1.06 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 32.23
2019-09-04 | 14:17 | 67.0625 | 0.08 | 1.08 | -0.78 | 0.22 | -0.67 | 0.33 | 77.15 | 33.2
2019-09-04 | 14:17 | 67.1719 | 0.09 | 1.09 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 32.23
2019-09-04 | 14:17 | 67.2695 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 76.17 | 31.25
2019-09-04 | 14:17 | 67.3711 | 0 | 1 | -0.71 | 0.29 | -0.66 | 0.34 | 75.2 | 32.23
2019-09-04 | 14:17 | 67.4727 | -0.06 | 0.94 | -0.63 | 0.37 | -0.65 | 0.35 | 76.17 | 35.16
2019-09-04 | 14:17 | 67.582 | -0.09 | 0.91 | -0.61 | 0.39 | -0.64 | 0.36 | 75.2 | 32.23
2019-09-04 | 14:17 | 67.6797 | -0.03 | 0.97 | -0.66 | 0.34 | -0.64 | 0.36 | 77.15 | 34.18
2019-09-04 | 14:17 | 67.7812 | 0.04 | 1.04 | -0.74 | 0.26 | -0.64 | 0.36 | 76.17 | 35.16
2019-09-04 | 14:17 | 67.8906 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 76.17 | 34.18
2019-09-04 | 14:17 | 67.9922 | 0.06 | 1.06 | -0.76 | 0.24 | -0.66 | 0.34 | 77.15 | 33.2
2019-09-04 | 14:17 | 68.0898 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 77.15 | 33.2
2019-09-04 | 14:17 | 68.1914 | 0.06 | 1.06 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 32.23
2019-09-04 | 14:17 | 68.3008 | 0.06 | 1.06 | -0.76 | 0.24 | -0.65 | 0.35 | 76.17 | 34.18
2019-09-04 | 14:17 | 68.4023 | 0.07 | 1.07 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 34.18
2019-09-04 | 14:17 | 68.5 | 0.07 | 1.07 | -0.78 | 0.22 | -0.66 | 0.34 | 75.2 | 33.2
2019-09-04 | 14:17 | 68.6016 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 77.15 | 33.2
2019-09-04 | 14:17 | 68.7109 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:17 | 68.8125 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 34.18
2019-09-04 | 14:17 | 68.9102 | -0.04 | 0.96 | -0.68 | 0.32 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 69.0195 | -0.1 | 0.9 | -0.61 | 0.39 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 69.1211 | -0.11 | 0.89 | -0.59 | 0.41 | -0.64 | 0.36 | 76.17 | 32.23
2019-09-04 | 14:17 | 69.2227 | 0.04 | 1.04 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 33.2
2019-09-04 | 14:17 | 69.3203 | 0.04 | 1.04 | -0.75 | 0.25 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 69.4297 | 0.06 | 1.06 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 34.18
2019-09-04 | 14:17 | 69.5312 | 0.05 | 1.05 | -0.77 | 0.23 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 69.6406 | 0.06 | 1.06 | -0.77 | 0.23 | -0.65 | 0.35 | 76.17 | 34.18
2019-09-04 | 14:17 | 69.7305 | 0.07 | 1.07 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 32.23
2019-09-04 | 14:17 | 69.8398 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 33.2
2019-09-04 | 14:17 | 69.9414 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 70.0391 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 70.1406 | 0.07 | 1.07 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 70.25 | 0.08 | 1.08 | -0.78 | 0.22 | -0.68 | 0.32 | 77.15 | 34.18
2019-09-04 | 14:17 | 70.3516 | 0.02 | 1.02 | -0.73 | 0.27 | -0.67 | 0.33 | 75.2 | 34.18
2019-09-04 | 14:17 | 70.4492 | -0.08 | 0.92 | -0.67 | 0.33 | -0.65 | 0.35 | 76.17 | 30.27
2019-09-04 | 14:17 | 70.5625 | -0.1 | 0.9 | -0.62 | 0.38 | -0.65 | 0.35 | 75.2 | 32.23
2019-09-04 | 14:17 | 70.6602 | -0.1 | 0.9 | -0.6 | 0.4 | -0.65 | 0.35 | 75.2 | 33.2
2019-09-04 | 14:17 | 70.7617 | 0.04 | 1.04 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 32.23
2019-09-04 | 14:17 | 70.8594 | 0.05 | 1.05 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 32.23
2019-09-04 | 14:17 | 70.9727 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 71.0703 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:17 | 71.1719 | 0.05 | 1.05 | -0.75 | 0.25 | -0.67 | 0.33 | 76.17 | 32.23
2019-09-04 | 14:17 | 71.2695 | 0.04 | 1.04 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 71.3789 | 0.08 | 1.08 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 31.25
2019-09-04 | 14:17 | 71.4805 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 71.582 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 71.6914 | 0.08 | 1.08 | -0.78 | 0.22 | -0.68 | 0.32 | 76.17 | 35.16
2019-09-04 | 14:17 | 71.7891 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 71.8906 | -0.03 | 0.97 | -0.69 | 0.31 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 71.9922 | -0.1 | 0.9 | -0.63 | 0.37 | -0.66 | 0.34 | 75.2 | 32.23
2019-09-04 | 14:17 | 72.1016 | -0.11 | 0.89 | -0.6 | 0.4 | -0.66 | 0.34 | 77.15 | 33.2
2019-09-04 | 14:17 | 72.1992 | 0.03 | 1.03 | -0.71 | 0.29 | -0.65 | 0.35 | 76.17 | 30.27
2019-09-04 | 14:17 | 72.3008 | 0.04 | 1.04 | -0.75 | 0.25 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 72.4023 | 0.06 | 1.06 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 33.2
2019-09-04 | 14:17 | 72.5117 | 0.06 | 1.06 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 34.18
2019-09-04 | 14:17 | 72.6094 | 0.06 | 1.06 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 33.2
2019-09-04 | 14:17 | 72.7227 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 33.2
2019-09-04 | 14:17 | 72.8203 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 33.2
2019-09-04 | 14:17 | 72.9219 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:17 | 73.0195 | 0.08 | 1.08 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:17 | 73.1211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 73.2305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 76.17 | 35.16
2019-09-04 | 14:17 | 73.332 | 0.06 | 1.06 | -0.76 | 0.24 | -0.68 | 0.32 | 76.17 | 33.2
2019-09-04 | 14:17 | 73.4297 | -0.04 | 0.96 | -0.66 | 0.34 | -0.66 | 0.34 | 75.2 | 33.2
2019-09-04 | 14:17 | 73.5391 | -0.11 | 0.89 | -0.62 | 0.38 | -0.66 | 0.34 | 75.2 | 32.23
2019-09-04 | 14:17 | 73.6406 | -0.13 | 0.87 | -0.61 | 0.39 | -0.64 | 0.36 | 78.12 | 35.16
2019-09-04 | 14:17 | 73.7422 | 0.04 | 1.04 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 32.23
2019-09-04 | 14:17 | 73.8516 | 0.05 | 1.05 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 33.2
2019-09-04 | 14:17 | 73.9492 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 34.18
2019-09-04 | 14:17 | 74.0508 | 0.04 | 1.04 | -0.77 | 0.23 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 74.1523 | 0.07 | 1.07 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:17 | 74.2617 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 76.17 | 33.2
2019-09-04 | 14:17 | 74.3594 | 0.08 | 1.08 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:17 | 74.4609 | 0.08 | 1.08 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 32.23
2019-09-04 | 14:17 | 74.5625 | 0.06 | 1.06 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 74.6719 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 78.12 | 33.2
2019-09-04 | 14:17 | 74.7695 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 74.8711 | -0.02 | 0.98 | -0.69 | 0.31 | -0.66 | 0.34 | 75.2 | 33.2
2019-09-04 | 14:17 | 74.9805 | -0.1 | 0.9 | -0.62 | 0.38 | -0.66 | 0.34 | 75.2 | 33.2
2019-09-04 | 14:17 | 75.082 | -0.1 | 0.9 | -0.6 | 0.4 | -0.65 | 0.35 | 74.22 | 33.2
2019-09-04 | 14:17 | 75.1797 | -0.09 | 0.91 | -0.61 | 0.39 | -0.65 | 0.35 | 76.17 | 33.2
2019-09-04 | 14:17 | 75.2812 | 0.05 | 1.05 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 32.23
2019-09-04 | 14:17 | 75.3906 | 0.06 | 1.06 | -0.75 | 0.25 | -0.66 | 0.34 | 76.17 | 31.25
2019-09-04 | 14:17 | 75.4922 | 0.05 | 1.05 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 32.23
2019-09-04 | 14:17 | 75.5898 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:17 | 75.6914 | 0.05 | 1.05 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 75.8008 | 0.07 | 1.07 | -0.77 | 0.23 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 75.9023 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 76 | 0.09 | 1.09 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 76.1016 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 76.17 | 32.23
2019-09-04 | 14:17 | 76.2109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 76.3125 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:17 | 76.4102 | -0.06 | 0.94 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 33.2
2019-09-04 | 14:17 | 76.5195 | -0.11 | 0.89 | -0.62 | 0.38 | -0.66 | 0.34 | 76.17 | 32.23
2019-09-04 | 14:17 | 76.6211 | -0.1 | 0.9 | -0.61 | 0.39 | -0.65 | 0.35 | 75.2 | 33.2
2019-09-04 | 14:17 | 76.7227 | 0.03 | 1.03 | -0.73 | 0.27 | -0.65 | 0.35 | 74.22 | 33.2
2019-09-04 | 14:17 | 76.8203 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 33.2
2019-09-04 | 14:17 | 76.9297 | 0.04 | 1.04 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 30.27
2019-09-04 | 14:17 | 77.0312 | 0.07 | 1.07 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:17 | 77.1289 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 33.2
2019-09-04 | 14:17 | 77.2305 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:17 | 77.3398 | 0.08 | 1.08 | -0.78 | 0.22 | -0.67 | 0.33 | 77.15 | 34.18
2019-09-04 | 14:17 | 77.4414 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:17 | 77.5391 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:17 | 77.6523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 34.18
2019-09-04 | 14:17 | 77.75 | 0.08 | 1.08 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:17 | 77.8516 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 75.2 | 32.23
2019-09-04 | 14:17 | 77.9492 | -0.05 | 0.95 | -0.66 | 0.34 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:17 | 78.0625 | -0.11 | 0.89 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 33.2
2019-09-04 | 14:17 | 78.1602 | -0.12 | 0.88 | -0.59 | 0.41 | -0.65 | 0.35 | 74.22 | 32.23
2019-09-04 | 14:17 | 78.2617 | 0.04 | 1.04 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 32.23
2019-09-04 | 14:17 | 78.3594 | 0.06 | 1.06 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 33.2
2019-09-04 | 14:17 | 78.4727 | 0.06 | 1.06 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 78.5703 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:17 | 78.6797 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 78.7812 | 0.07 | 1.07 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:17 | 78.8789 | 0.07 | 1.07 | -0.78 | 0.22 | -0.67 | 0.33 | 77.15 | 33.2
2019-09-04 | 14:17 | 78.9805 | 0.07 | 1.07 | -0.78 | 0.22 | -0.68 | 0.32 | 76.17 | 35.16
2019-09-04 | 14:17 | 79.082 | 0.08 | 1.08 | -0.78 | 0.22 | -0.67 | 0.33 | 77.15 | 33.2
2019-09-04 | 14:17 | 79.1914 | 0.07 | 1.07 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 34.18
2019-09-04 | 14:17 | 79.2891 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 76.17 | 31.25
2019-09-04 | 14:17 | 79.3906 | 0 | 1 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:17 | 79.5 | -0.1 | 0.9 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 32.23
2019-09-04 | 14:17 | 79.6016 | -0.11 | 0.89 | -0.6 | 0.4 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 79.6992 | 0.02 | 1.02 | -0.72 | 0.28 | -0.65 | 0.35 | 74.22 | 32.23
2019-09-04 | 14:17 | 79.8125 | 0.04 | 1.04 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 32.23
2019-09-04 | 14:17 | 79.9102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.66 | 0.34 | 76.17 | 34.18
2019-09-04 | 14:17 | 80.0117 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 35.16
2019-09-04 | 14:17 | 80.1094 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 31.25
2019-09-04 | 14:17 | 80.2227 | 0.06 | 1.06 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:17 | 80.3203 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:17 | 80.4219 | 0.07 | 1.07 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:17 | 80.5195 | 0.07 | 1.07 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 80.6289 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:17 | 80.7305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:17 | 80.832 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 30.27
2019-09-04 | 14:17 | 80.9414 | -0.04 | 0.96 | -0.68 | 0.32 | -0.68 | 0.32 | 77.15 | 33.2
2019-09-04 | 14:17 | 81.0391 | -0.11 | 0.89 | -0.62 | 0.38 | -0.66 | 0.34 | 74.22 | 33.2
2019-09-04 | 14:17 | 81.1406 | -0.11 | 0.89 | -0.62 | 0.38 | -0.66 | 0.34 | 75.2 | 34.18
2019-09-04 | 14:17 | 81.2422 | 0.03 | 1.03 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 32.23
2019-09-04 | 14:17 | 81.3516 | 0.05 | 1.05 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 33.2
2019-09-04 | 14:17 | 81.4492 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:17 | 81.5508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:17 | 81.6523 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:17 | 81.7617 | 0.07 | 1.07 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:17 | 81.8594 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:17 | 81.9609 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:17 | 82.0625 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 32.23
2019-09-04 | 14:17 | 82.1719 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:17 | 82.2695 | 0.07 | 1.07 | -0.8 | 0.2 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:17 | 82.3711 | 0 | 1 | -0.73 | 0.27 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:17 | 82.4805 | -0.09 | 0.91 | -0.65 | 0.35 | -0.66 | 0.34 | 75.2 | 33.2
2019-09-04 | 14:17 | 82.582 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:17 | 82.6797 | -0.14 | 0.86 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 32.23
2019-09-04 | 14:17 | 82.7812 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 34.18
2019-09-04 | 14:17 | 82.8906 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 34.18
2019-09-04 | 14:17 | 82.9922 | 0.04 | 1.04 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 83.0898 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:17 | 83.1914 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 31.25
2019-09-04 | 14:17 | 83.3008 | 0.08 | 1.08 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:17 | 83.4023 | 0.05 | 1.05 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:17 | 83.5 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:17 | 83.6094 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:17 | 83.7109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 75.2 | 33.2
2019-09-04 | 14:17 | 83.8125 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:17 | 83.9102 | -0.06 | 0.94 | -0.69 | 0.31 | -0.68 | 0.32 | 76.17 | 31.25
2019-09-04 | 14:17 | 84.0195 | -0.1 | 0.9 | -0.63 | 0.37 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:18 | 84.1211 | -0.12 | 0.88 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 33.2
2019-09-04 | 14:18 | 84.2227 | 0.03 | 1.03 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:18 | 84.3203 | 0.06 | 1.06 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:18 | 84.4297 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:18 | 84.5312 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:18 | 84.6406 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:18 | 84.7422 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 76.17 | 32.23
2019-09-04 | 14:18 | 84.8398 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 84.9414 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:18 | 85.0391 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 85.1523 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:18 | 85.25 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 75.2 | 34.18
2019-09-04 | 14:18 | 85.3516 | 0.02 | 1.02 | -0.75 | 0.25 | -0.69 | 0.31 | 74.22 | 29.3
2019-09-04 | 14:18 | 85.4609 | -0.09 | 0.91 | -0.65 | 0.35 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 85.5625 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:18 | 85.6719 | -0.13 | 0.87 | -0.6 | 0.4 | -0.65 | 0.35 | 74.22 | 33.2
2019-09-04 | 14:18 | 85.7695 | 0.05 | 1.05 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 35.16
2019-09-04 | 14:18 | 85.8711 | 0.05 | 1.05 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:18 | 85.9727 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:18 | 86.0703 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:18 | 86.1797 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 86.2812 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:18 | 86.3789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:18 | 86.4805 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 86.5898 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 86.6914 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 86.7891 | 0.06 | 1.06 | -0.8 | 0.2 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 86.9023 | -0.05 | 0.95 | -0.7 | 0.3 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:18 | 87 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 87.1016 | -0.15 | 0.85 | -0.61 | 0.39 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:18 | 87.1992 | 0.01 | 1.01 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 31.25
2019-09-04 | 14:18 | 87.3125 | 0.03 | 1.03 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 33.2
2019-09-04 | 14:18 | 87.4102 | 0.04 | 1.04 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:18 | 87.5117 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 87.6094 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:18 | 87.7227 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 87.8203 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:18 | 87.9219 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 88.0195 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 75.2 | 31.25
2019-09-04 | 14:18 | 88.1289 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 88.2305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:18 | 88.332 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 88.4414 | -0.08 | 0.92 | -0.68 | 0.32 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:18 | 88.5391 | -0.11 | 0.89 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:18 | 88.6406 | -0.11 | 0.89 | -0.6 | 0.4 | -0.65 | 0.35 | 75.2 | 34.18
2019-09-04 | 14:18 | 88.7422 | 0.02 | 1.02 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:18 | 88.8516 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 88.9492 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:18 | 89.0508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:18 | 89.1523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 89.2617 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 75.2 | 30.27
2019-09-04 | 14:18 | 89.3594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 89.4609 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 89.5703 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:18 | 89.6719 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 76.17 | 33.2
2019-09-04 | 14:18 | 89.7695 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 89.8711 | -0.02 | 0.98 | -0.73 | 0.27 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 89.9805 | -0.12 | 0.88 | -0.64 | 0.36 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:18 | 90.082 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 73.24 | 30.27
2019-09-04 | 14:18 | 90.1914 | -0.15 | 0.85 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 32.23
2019-09-04 | 14:18 | 90.2812 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 90.3906 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:18 | 90.4922 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 90.6016 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 90.6992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 90.8008 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 30.27
2019-09-04 | 14:18 | 90.9023 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 91 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 91.1094 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 91.2109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:18 | 91.3125 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:18 | 91.4219 | -0.05 | 0.95 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:18 | 91.5195 | -0.13 | 0.87 | -0.64 | 0.36 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:18 | 91.6211 | -0.14 | 0.86 | -0.63 | 0.37 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 91.7305 | 0 | 1 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 32.23
2019-09-04 | 14:18 | 91.832 | 0.03 | 1.03 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:18 | 91.9297 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 92.0312 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 92.1406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 92.2422 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:18 | 92.3398 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:18 | 92.4414 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 92.5508 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 92.6523 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 92.75 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 92.8516 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 92.9609 | -0.08 | 0.92 | -0.68 | 0.32 | -0.68 | 0.32 | 75.2 | 33.2
2019-09-04 | 14:18 | 93.0625 | -0.12 | 0.88 | -0.64 | 0.36 | -0.68 | 0.32 | 74.22 | 30.27
2019-09-04 | 14:18 | 93.1602 | -0.14 | 0.86 | -0.61 | 0.39 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:18 | 93.2695 | 0.01 | 1.01 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 33.2
2019-09-04 | 14:18 | 93.3711 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 93.4727 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 93.5703 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 93.6797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 93.7812 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 93.8789 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 93.9805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 94.0898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 94.1914 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 75.2 | 34.18
2019-09-04 | 14:18 | 94.2891 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 75.2 | 33.2
2019-09-04 | 14:18 | 94.4023 | -0.02 | 0.98 | -0.72 | 0.28 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 94.5 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:18 | 94.6016 | -0.15 | 0.85 | -0.61 | 0.39 | -0.67 | 0.33 | 74.22 | 30.27
2019-09-04 | 14:18 | 94.6992 | -0.05 | 0.95 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 34.18
2019-09-04 | 14:18 | 94.8125 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 94.9102 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:18 | 95.0117 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:18 | 95.1094 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:18 | 95.2227 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 95.3203 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 95.4219 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 95.5312 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 95.6289 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 95.7305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 95.832 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 31.25
2019-09-04 | 14:18 | 95.9414 | -0.08 | 0.92 | -0.68 | 0.32 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 96.0391 | -0.13 | 0.87 | -0.63 | 0.37 | -0.68 | 0.32 | 76.17 | 32.23
2019-09-04 | 14:18 | 96.1406 | -0.15 | 0.85 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 30.27
2019-09-04 | 14:18 | 96.2422 | 0.01 | 1.01 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:18 | 96.3516 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:18 | 96.4492 | 0.02 | 1.02 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 96.5508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 96.6602 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 32.23
2019-09-04 | 14:18 | 96.7617 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:18 | 96.8594 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 96.9609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 97.0703 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 97.1719 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 31.25
2019-09-04 | 14:18 | 97.2695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 97.3789 | -0.02 | 0.98 | -0.74 | 0.26 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 97.4805 | -0.13 | 0.87 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 97.582 | -0.14 | 0.86 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:18 | 97.6914 | -0.15 | 0.85 | -0.6 | 0.4 | -0.66 | 0.34 | 73.24 | 30.27
2019-09-04 | 14:18 | 97.7891 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 97.8906 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:18 | 97.9922 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 98.0898 | 0.02 | 1.02 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 98.1992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 98.3008 | 0.02 | 1.02 | -0.78 | 0.22 | -0.71 | 0.29 | 74.22 | 31.25
2019-09-04 | 14:18 | 98.4023 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 98.5 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 98.6094 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 98.7109 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 98.8203 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 98.9219 | -0.05 | 0.95 | -0.72 | 0.28 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 99.0195 | -0.16 | 0.84 | -0.63 | 0.37 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 99.1211 | -0.15 | 0.85 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 99.2305 | -0.02 | 0.98 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 99.332 | 0.01 | 1.01 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 99.4297 | 0.06 | 1.06 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 99.5312 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:18 | 99.6406 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 99.7422 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 99.8398 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 99.9414 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:18 | 100.0508 | 0.03 | 1.03 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 100.1523 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 100.25 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:18 | 100.3594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 33.2
2019-09-04 | 14:18 | 100.4609 | -0.1 | 0.9 | -0.69 | 0.31 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 100.5625 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 100.6719 | -0.16 | 0.84 | -0.61 | 0.39 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:18 | 100.7695 | 0 | 1 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:18 | 100.8711 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 100.9727 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 101.0703 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 101.1797 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 101.2813 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 101.3789 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:18 | 101.4922 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:18 | 101.5898 | 0.04 | 1.04 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:18 | 101.6914 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 101.7891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:18 | 101.9023 | -0.05 | 0.95 | -0.73 | 0.27 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 102 | -0.11 | 0.89 | -0.65 | 0.35 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 102.1094 | -0.15 | 0.85 | -0.62 | 0.38 | -0.66 | 0.34 | 75.2 | 33.2
2019-09-04 | 14:18 | 102.2109 | -0.09 | 0.91 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 33.2
2019-09-04 | 14:18 | 102.3125 | 0 | 1 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:18 | 102.4102 | 0 | 1 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:18 | 102.5195 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 102.6211 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 102.7227 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 102.8203 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 102.9219 | 0.01 | 1.01 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 103.0313 | 0.03 | 1.03 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 103.1289 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:18 | 103.2305 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:18 | 103.332 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 103.4414 | -0.07 | 0.93 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 103.5391 | -0.16 | 0.84 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 103.6523 | -0.13 | 0.87 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:18 | 103.75 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:18 | 103.8516 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 103.9492 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 104.0625 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 104.1602 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 104.2617 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 104.3594 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 104.4609 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 104.5703 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:18 | 104.6719 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 30.27
2019-09-04 | 14:18 | 104.7813 | 0.02 | 1.02 | -0.8 | 0.2 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:18 | 104.8789 | -0.02 | 0.98 | -0.75 | 0.25 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 104.9805 | -0.13 | 0.87 | -0.66 | 0.34 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 105.082 | -0.15 | 0.85 | -0.63 | 0.37 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 105.1914 | -0.16 | 0.84 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 33.2
2019-09-04 | 14:18 | 105.2891 | -0.01 | 0.99 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:18 | 105.3906 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 105.4922 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 105.6016 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 105.6992 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 105.8008 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 105.9102 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 106.0117 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 106.1094 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:18 | 106.2109 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 106.3203 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 75.2 | 32.23
2019-09-04 | 14:18 | 106.4219 | -0.04 | 0.96 | -0.73 | 0.27 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 106.5195 | -0.14 | 0.86 | -0.66 | 0.34 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 106.6211 | -0.17 | 0.83 | -0.61 | 0.39 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 106.7305 | -0.04 | 0.96 | -0.73 | 0.27 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:18 | 106.832 | 0 | 1 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:18 | 106.9297 | 0 | 1 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 107.0313 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 107.1406 | 0.01 | 1.01 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 107.2422 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 107.3398 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 107.4492 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 107.5508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 107.6523 | 0.03 | 1.03 | -0.79 | 0.21 | -0.72 | 0.28 | 73.24 | 30.27
2019-09-04 | 14:18 | 107.75 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 14:18 | 107.8594 | 0.03 | 1.03 | -0.8 | 0.2 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 107.9609 | -0.07 | 0.93 | -0.72 | 0.28 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:18 | 108.0625 | -0.14 | 0.86 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 108.1719 | -0.17 | 0.83 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 108.2695 | 0 | 1 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:18 | 108.3711 | 0 | 1 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 108.4805 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 108.582 | 0 | 1 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 108.6797 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:18 | 108.7813 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 108.8789 | 0.01 | 1.01 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:18 | 108.9922 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 109.0898 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 109.1914 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 109.2891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 109.4023 | -0.02 | 0.98 | -0.74 | 0.26 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 109.5 | -0.15 | 0.85 | -0.66 | 0.34 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 109.6094 | -0.17 | 0.83 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 109.7109 | -0.17 | 0.83 | -0.62 | 0.38 | -0.67 | 0.33 | 71.29 | 31.25
2019-09-04 | 14:18 | 109.8125 | 0 | 1 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:18 | 109.9102 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:18 | 110.0117 | -0.01 | 0.99 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:18 | 110.1211 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 110.2227 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 110.3203 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 110.4219 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 110.5313 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 75.2 | 33.2
2019-09-04 | 14:18 | 110.6406 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 110.7422 | 0.01 | 1.01 | -0.79 | 0.21 | -0.72 | 0.28 | 71.29 | 30.27
2019-09-04 | 14:18 | 110.8398 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 110.9414 | -0.06 | 0.94 | -0.71 | 0.29 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 111.0391 | -0.16 | 0.84 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 111.1523 | -0.19 | 0.81 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 111.25 | -0.04 | 0.96 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 111.3516 | -0.01 | 0.99 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 111.4492 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:18 | 111.5508 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 111.6602 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 111.7617 | 0 | 1 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 111.8711 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:18 | 111.9727 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 112.0703 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:18 | 112.1719 | 0.02 | 1.02 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 32.23
2019-09-04 | 14:18 | 112.2813 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 112.3789 | 0.01 | 1.01 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 112.4805 | -0.11 | 0.89 | -0.67 | 0.33 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 112.582 | -0.18 | 0.82 | -0.62 | 0.38 | -0.69 | 0.31 | 74.22 | 34.18
2019-09-04 | 14:18 | 112.6914 | -0.18 | 0.82 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 112.7891 | -0.01 | 0.99 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 112.8906 | 0 | 1 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 113 | 0 | 1 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:18 | 113.1016 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 113.1992 | 0 | 1 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 113.3008 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 113.4102 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:18 | 113.5117 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 113.6094 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:18 | 113.7109 | 0 | 1 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 30.27
2019-09-04 | 14:18 | 113.8203 | 0.02 | 1.02 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 33.2
2019-09-04 | 14:18 | 113.9219 | -0.05 | 0.95 | -0.74 | 0.26 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 114.0195 | -0.14 | 0.86 | -0.67 | 0.33 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 114.1289 | -0.19 | 0.81 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 114.2305 | -0.05 | 0.95 | -0.73 | 0.27 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 114.332 | -0.01 | 0.99 | -0.77 | 0.23 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:18 | 114.4297 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 114.5391 | 0.01 | 1.01 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:18 | 114.6406 | 0.01 | 1.01 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 114.7422 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:18 | 114.8398 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 114.9492 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 115.0508 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:18 | 115.1523 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 115.2617 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 115.3594 | -0.02 | 0.98 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:18 | 115.4609 | -0.12 | 0.88 | -0.68 | 0.32 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 115.5703 | -0.17 | 0.83 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 115.6719 | -0.18 | 0.82 | -0.61 | 0.39 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:18 | 115.7695 | -0.02 | 0.98 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:18 | 115.8711 | -0.02 | 0.98 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 115.9727 | -0.03 | 0.97 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:18 | 116.082 | 0.02 | 1.02 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 116.1797 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:18 | 116.2891 | -0.01 | 0.99 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:18 | 116.3906 | -0.01 | 0.99 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 116.4922 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 116.5898 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 116.6992 | -0.02 | 0.98 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 116.8008 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:18 | 116.9023 | -0.03 | 0.97 | -0.75 | 0.25 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 117.0117 | -0.11 | 0.89 | -0.66 | 0.34 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 117.1211 | -0.14 | 0.86 | -0.64 | 0.36 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 117.2109 | -0.15 | 0.85 | -0.62 | 0.38 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 117.3125 | -0.02 | 0.98 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 117.4219 | -0.01 | 0.99 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 117.5195 | -0.01 | 0.99 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 117.6211 | -0.01 | 0.99 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 117.7227 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 117.832 | -0.01 | 0.99 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:18 | 117.9297 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:18 | 118.0313 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:18 | 118.1289 | -0.02 | 0.98 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:18 | 118.2422 | -0.01 | 0.99 | -0.78 | 0.22 | -0.72 | 0.28 | 71.29 | 30.27
2019-09-04 | 14:18 | 118.3398 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 118.4414 | -0.09 | 0.91 | -0.7 | 0.3 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 118.5508 | -0.17 | 0.83 | -0.64 | 0.36 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 118.6523 | -0.18 | 0.82 | -0.61 | 0.39 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 118.75 | -0.04 | 0.96 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 118.8516 | -0.02 | 0.98 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 118.9609 | -0.01 | 0.99 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 119.0625 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 119.1602 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 119.2617 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 33.2
2019-09-04 | 14:18 | 119.3711 | -0.01 | 0.99 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 119.4727 | -0.02 | 0.98 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 119.5703 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 119.6719 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 119.7813 | 0 | 1 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:18 | 119.8789 | -0.01 | 0.99 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 119.9805 | -0.11 | 0.89 | -0.7 | 0.3 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 120.0898 | -0.17 | 0.83 | -0.65 | 0.35 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 120.1914 | -0.17 | 0.83 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 120.2891 | -0.03 | 0.97 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 120.3906 | -0.01 | 0.99 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 120.5 | -0.01 | 0.99 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:18 | 120.6016 | -0.01 | 0.99 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 120.6992 | -0.01 | 0.99 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:18 | 120.8125 | -0.01 | 0.99 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:18 | 120.9102 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 121.0195 | 0 | 1 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 121.1211 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 121.2227 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:18 | 121.3203 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:18 | 121.4219 | -0.05 | 0.95 | -0.73 | 0.27 | -0.71 | 0.29 | 72.27 | 33.2
2019-09-04 | 14:18 | 121.5313 | -0.15 | 0.85 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 121.6289 | -0.19 | 0.81 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 121.7305 | -0.05 | 0.95 | -0.71 | 0.29 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:18 | 121.832 | 0 | 1 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 121.9414 | 0 | 1 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 122.0391 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:18 | 122.1406 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 34.18
2019-09-04 | 14:18 | 122.25 | 0.01 | 1.01 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 122.3516 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:18 | 122.4492 | 0.02 | 1.02 | -0.79 | 0.21 | -0.72 | 0.28 | 73.24 | 32.23
2019-09-04 | 14:18 | 122.5508 | 0.01 | 1.01 | -0.78 | 0.22 | -0.71 | 0.29 | 74.22 | 31.25
2019-09-04 | 14:18 | 122.6602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 122.7617 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 122.8594 | 0 | 1 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:18 | 122.9609 | -0.09 | 0.91 | -0.69 | 0.31 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 123.0703 | -0.15 | 0.85 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 123.1719 | -0.16 | 0.84 | -0.62 | 0.38 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 123.2695 | -0.02 | 0.98 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 32.23
2019-09-04 | 14:18 | 123.3789 | 0 | 1 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 123.4805 | 0.02 | 1.02 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:18 | 123.582 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 123.6914 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 123.7891 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 33.2
2019-09-04 | 14:18 | 123.8906 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 123.9922 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 124.0898 | 0.02 | 1.02 | -0.8 | 0.2 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 124.1992 | 0.01 | 1.01 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 32.23
2019-09-04 | 14:18 | 124.3008 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 124.4102 | -0.03 | 0.97 | -0.73 | 0.27 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 124.5117 | -0.16 | 0.84 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 124.6094 | -0.16 | 0.84 | -0.63 | 0.37 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 124.7109 | -0.18 | 0.82 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 34.18
2019-09-04 | 14:18 | 124.8125 | 0 | 1 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 124.9219 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 125.0195 | 0.02 | 1.02 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 125.1211 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 125.2227 | 0.02 | 1.02 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 125.332 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 125.4297 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:18 | 125.5313 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 125.6289 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 125.7422 | 0.03 | 1.03 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 125.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 125.9492 | -0.07 | 0.93 | -0.69 | 0.31 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 126.0508 | -0.14 | 0.86 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 14:18 | 126.1523 | -0.14 | 0.86 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 126.25 | -0.03 | 0.97 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 126.3594 | 0.02 | 1.02 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:18 | 126.4609 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:18 | 126.5625 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 126.6719 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 126.7617 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 126.8711 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 126.9727 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:18 | 127.082 | 0.01 | 1.01 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 127.1797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 127.2813 | 0.04 | 1.04 | -0.79 | 0.21 | -0.73 | 0.27 | 71.29 | 31.25
2019-09-04 | 14:18 | 127.3789 | 0.03 | 1.03 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:18 | 127.4922 | -0.08 | 0.92 | -0.7 | 0.3 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 127.5898 | -0.14 | 0.86 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 127.6914 | -0.14 | 0.86 | -0.61 | 0.39 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:18 | 127.7891 | 0.01 | 1.01 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 127.9023 | 0.01 | 1.01 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 128 | 0.01 | 1.01 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:18 | 128.1016 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 128.2109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 128.3125 | 0.03 | 1.03 | -0.78 | 0.22 | -0.72 | 0.28 | 73.24 | 33.2
2019-09-04 | 14:18 | 128.4102 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:18 | 128.5117 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 128.6211 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 128.7227 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 128.8203 | 0.03 | 1.03 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 32.23
2019-09-04 | 14:18 | 128.9219 | -0.05 | 0.95 | -0.7 | 0.3 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 129.0313 | -0.13 | 0.87 | -0.62 | 0.38 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 129.1289 | -0.15 | 0.85 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:18 | 129.2305 | -0.08 | 0.92 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:18 | 129.3398 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 32.23
2019-09-04 | 14:18 | 129.4414 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 129.5391 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 129.6523 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 129.75 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 129.8516 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 33.2
2019-09-04 | 14:18 | 129.9492 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 130.0508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 130.1602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 130.2617 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 130.3594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 130.4727 | -0.04 | 0.96 | -0.72 | 0.28 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 130.5703 | -0.14 | 0.86 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 34.18
2019-09-04 | 14:18 | 130.6797 | -0.14 | 0.86 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 130.7695 | 0 | 1 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 130.8789 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 130.9805 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:18 | 131.082 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 131.1797 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 131.2891 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 131.3906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 131.4922 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 131.5898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 131.6992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 34.18
2019-09-04 | 14:18 | 131.8008 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 131.9023 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 132.0117 | -0.09 | 0.91 | -0.67 | 0.33 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 132.1094 | -0.13 | 0.87 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 132.2109 | -0.16 | 0.84 | -0.61 | 0.39 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:18 | 132.3125 | 0.02 | 1.02 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 132.4219 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 132.5195 | 0.02 | 1.02 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 132.6211 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 132.7227 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 132.832 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 132.9297 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 133.0391 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 133.1406 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 133.2422 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:18 | 133.3398 | 0.03 | 1.03 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:18 | 133.4492 | -0.04 | 0.96 | -0.71 | 0.29 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:18 | 133.5508 | -0.12 | 0.88 | -0.65 | 0.35 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 133.6523 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 133.7617 | 0 | 1 | -0.74 | 0.26 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:18 | 133.8594 | 0.01 | 1.01 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:18 | 133.9609 | 0.02 | 1.02 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 134.0625 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 134.1719 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 30.27
2019-09-04 | 14:18 | 134.2695 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:18 | 134.3711 | 0.03 | 1.03 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:18 | 134.4727 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 134.582 | 0.02 | 1.02 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 134.6797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:18 | 134.7813 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 134.8789 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 134.9922 | -0.12 | 0.88 | -0.65 | 0.35 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 135.0898 | -0.15 | 0.85 | -0.59 | 0.41 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:18 | 135.1914 | -0.15 | 0.85 | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 135.3008 | 0 | 1 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:18 | 135.4023 | 0.02 | 1.02 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 135.5 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 135.6016 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 135.7109 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 135.8125 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:18 | 135.9102 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 136.0117 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 136.1211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:18 | 136.2227 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 33.2
2019-09-04 | 14:18 | 136.3203 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:18 | 136.4297 | -0.07 | 0.93 | -0.7 | 0.3 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 136.5313 | -0.14 | 0.86 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 136.6289 | -0.16 | 0.84 | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 136.7305 | -0.08 | 0.92 | -0.66 | 0.34 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:18 | 136.8398 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 136.9414 | 0.03 | 1.03 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 137.0391 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:18 | 137.1406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:18 | 137.25 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 137.3516 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 137.4492 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 33.2
2019-09-04 | 14:18 | 137.5625 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:18 | 137.6602 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 137.7617 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 137.8594 | 0.02 | 1.02 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 137.9727 | -0.08 | 0.92 | -0.68 | 0.32 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:18 | 138.0703 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:18 | 138.1719 | -0.15 | 0.85 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 138.2695 | 0.01 | 1.01 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 138.3789 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:18 | 138.4805 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 138.582 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 138.6914 | 0.02 | 1.02 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 138.7891 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:18 | 138.8906 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 139 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 33.2
2019-09-04 | 14:18 | 139.1016 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 139.1992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.72 | 0.28 | 73.24 | 32.23
2019-09-04 | 14:18 | 139.3008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 139.4023 | 0.01 | 1.01 | -0.74 | 0.26 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 139.5117 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 29.3
2019-09-04 | 14:18 | 139.6094 | -0.13 | 0.87 | -0.6 | 0.4 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:18 | 139.7227 | -0.14 | 0.86 | -0.61 | 0.39 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:18 | 139.8125 | 0.02 | 1.02 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:18 | 139.9219 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:18 | 140.0195 | 0.02 | 1.02 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 140.1289 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 140.2305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:18 | 140.332 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:18 | 140.4297 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 140.5391 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 140.6406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 140.7422 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 140.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:18 | 140.9492 | -0.02 | 0.98 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:18 | 141.0508 | -0.12 | 0.88 | -0.62 | 0.38 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 14:18 | 141.1523 | -0.14 | 0.86 | -0.6 | 0.4 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:18 | 141.2617 | 0.01 | 1.01 | -0.72 | 0.28 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:18 | 141.3594 | 0.03 | 1.03 | -0.75 | 0.25 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:18 | 141.4609 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:18 | 141.5625 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 141.6719 | 0.03 | 1.03 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:18 | 141.7695 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:18 | 141.8711 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:18 | 141.9727 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:18 | 142.082 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 142.1797 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:18 | 142.2813 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:18 | 142.3906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:18 | 142.4922 | -0.05 | 0.95 | -0.69 | 0.31 | -0.68 | 0.32 | 72.27 | 34.18
2019-09-04 | 14:18 | 142.5898 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:18 | 142.6914 | -0.14 | 0.86 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 33.2
2019-09-04 | 14:18 | 142.8008 | 0 | 1 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:18 | 142.9023 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:18 | 143 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 143.1016 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:19 | 143.2109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 143.3125 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 29.3
2019-09-04 | 14:19 | 143.4219 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 143.5195 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 143.6211 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 68.36 | 32.23
2019-09-04 | 14:19 | 143.7227 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 143.8203 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:19 | 143.9297 | -0.01 | 0.99 | -0.74 | 0.26 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 144.0313 | -0.1 | 0.9 | -0.65 | 0.35 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 14:19 | 144.1289 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 14:19 | 144.2305 | -0.15 | 0.85 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 144.3398 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:19 | 144.4414 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 144.5391 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 144.6523 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 144.75 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 144.8516 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 144.9609 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 145.0625 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 145.1602 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:19 | 145.2617 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 145.3594 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 145.4727 | -0.1 | 0.9 | -0.68 | 0.32 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 145.5703 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:19 | 145.6797 | -0.15 | 0.85 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:19 | 145.7813 | 0.02 | 1.02 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 145.8789 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 32.23
2019-09-04 | 14:19 | 145.9805 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 146.0898 | 0.01 | 1.01 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 146.1914 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 146.2891 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 146.3906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 146.5 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 146.6016 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 146.6992 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 146.8008 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:19 | 146.9102 | 0 | 1 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 147.0117 | -0.09 | 0.91 | -0.68 | 0.32 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 147.1094 | -0.12 | 0.88 | -0.63 | 0.37 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 147.2227 | -0.14 | 0.86 | -0.61 | 0.39 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:19 | 147.3203 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 147.4219 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 147.5195 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 147.6289 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 147.7305 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 147.832 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:19 | 147.9297 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 148.0391 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 148.1406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 148.2422 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 148.3516 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 148.4492 | -0.04 | 0.96 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 148.5508 | -0.14 | 0.86 | -0.64 | 0.36 | -0.68 | 0.32 | 74.22 | 30.27
2019-09-04 | 14:19 | 148.6602 | -0.15 | 0.85 | -0.6 | 0.4 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:19 | 148.7617 | -0.02 | 0.98 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:19 | 148.8594 | 0.01 | 1.01 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 148.9609 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:19 | 149.0625 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 33.2
2019-09-04 | 14:19 | 149.1719 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 149.2695 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 149.3711 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:19 | 149.4805 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 149.582 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:19 | 149.6797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 149.7813 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 149.8906 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 74.22 | 33.2
2019-09-04 | 14:19 | 149.9922 | -0.08 | 0.92 | -0.67 | 0.33 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 150.0898 | -0.13 | 0.87 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 150.1992 | -0.14 | 0.86 | -0.61 | 0.39 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 150.3008 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 150.4023 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 150.5117 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 150.6094 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 150.7109 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:19 | 150.8125 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 150.9219 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:19 | 151.0195 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 14:19 | 151.1211 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 151.2227 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 151.332 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 151.4297 | -0.02 | 0.98 | -0.72 | 0.28 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 151.5313 | -0.12 | 0.88 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 14:19 | 151.6406 | -0.14 | 0.86 | -0.59 | 0.41 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 151.7422 | -0.15 | 0.85 | -0.6 | 0.4 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:19 | 151.8398 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 151.9414 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 152.0508 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 152.1523 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 14:19 | 152.25 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 152.3516 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 152.4609 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 34.18
2019-09-04 | 14:19 | 152.5625 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 152.6602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 152.7617 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 152.8711 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 152.9727 | -0.08 | 0.92 | -0.65 | 0.35 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 153.0703 | -0.14 | 0.86 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 153.1797 | -0.15 | 0.85 | -0.59 | 0.41 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 153.2813 | 0 | 1 | -0.72 | 0.28 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:19 | 153.3789 | 0.01 | 1.01 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 153.4805 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 153.5898 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:19 | 153.6914 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 153.7891 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 153.8906 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 154 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 154.1016 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 154.1992 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 154.3125 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 154.4102 | -0.02 | 0.98 | -0.71 | 0.29 | -0.69 | 0.31 | 73.24 | 34.18
2019-09-04 | 14:19 | 154.5117 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 154.6211 | -0.13 | 0.87 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 154.7227 | -0.14 | 0.86 | -0.6 | 0.4 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:19 | 154.8203 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 154.9219 | 0.02 | 1.02 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 31.25
2019-09-04 | 14:19 | 155.0195 | 0.04 | 1.04 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 33.2
2019-09-04 | 14:19 | 155.1289 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 155.2305 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 30.27
2019-09-04 | 14:19 | 155.332 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 155.4414 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 155.5391 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 155.6406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 155.7422 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 155.8516 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 155.9492 | -0.02 | 0.98 | -0.72 | 0.28 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 156.0625 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:19 | 156.1602 | -0.13 | 0.87 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 156.2617 | -0.01 | 0.99 | -0.71 | 0.29 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:19 | 156.3594 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 156.4727 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 33.2
2019-09-04 | 14:19 | 156.5703 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 156.6719 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:19 | 156.7695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 156.8789 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 156.9805 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 157.082 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 157.1797 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 157.2813 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 157.3906 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 157.4922 | -0.08 | 0.92 | -0.66 | 0.34 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 157.6016 | -0.14 | 0.86 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 157.6992 | -0.13 | 0.87 | -0.61 | 0.39 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:19 | 157.8008 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:19 | 157.9023 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 158.0117 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 158.1094 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 158.2109 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 158.3125 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 158.4219 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 158.5195 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 158.6211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:19 | 158.7305 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 158.832 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:19 | 158.9297 | -0.01 | 0.99 | -0.74 | 0.26 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:19 | 159.0313 | -0.11 | 0.89 | -0.62 | 0.38 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 159.1406 | -0.11 | 0.89 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 159.2422 | -0.14 | 0.86 | -0.6 | 0.4 | -0.66 | 0.34 | 73.24 | 33.2
2019-09-04 | 14:19 | 159.3398 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:19 | 159.4414 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 159.5508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 159.6523 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 159.75 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 159.8516 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 159.9609 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 160.0625 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 160.1602 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 160.2695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 75.2 | 31.25
2019-09-04 | 14:19 | 160.3711 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 160.4727 | -0.07 | 0.93 | -0.68 | 0.32 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:19 | 160.5703 | -0.12 | 0.88 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 160.6914 | -0.12 | 0.88 | -0.61 | 0.39 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:19 | 160.7813 | 0.01 | 1.01 | -0.73 | 0.27 | -0.67 | 0.33 | 71.29 | 31.25
2019-09-04 | 14:19 | 160.8789 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 160.9805 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:19 | 161.0898 | 0.01 | 1.01 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:19 | 161.1914 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 161.3008 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 75.2 | 32.23
2019-09-04 | 14:19 | 161.4023 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 161.5 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 161.6016 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 161.7109 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 161.8125 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 30.27
2019-09-04 | 14:19 | 161.9102 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 162.0195 | -0.06 | 0.94 | -0.69 | 0.31 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 162.1211 | -0.13 | 0.87 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 162.2227 | -0.13 | 0.87 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 162.3203 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 162.4297 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 34.18
2019-09-04 | 14:19 | 162.5313 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 162.6289 | 0.03 | 1.03 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 162.7305 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 162.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 162.9414 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 163.0391 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 163.1406 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 163.25 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 163.3516 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 163.4492 | 0.02 | 1.02 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 163.5625 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 163.6719 | -0.14 | 0.86 | -0.62 | 0.38 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:19 | 163.7617 | -0.06 | 0.94 | -0.68 | 0.32 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 163.8594 | 0.03 | 1.03 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:19 | 163.9727 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:19 | 164.0703 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:19 | 164.1719 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 164.2695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 164.3789 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 164.4805 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 164.582 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 164.6914 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 164.7891 | 0.08 | 1.08 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 164.8906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 164.9922 | -0.08 | 0.92 | -0.67 | 0.33 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 165.1016 | -0.11 | 0.89 | -0.62 | 0.38 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 165.1992 | -0.14 | 0.86 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:19 | 165.3008 | 0.04 | 1.04 | -0.74 | 0.26 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 165.4023 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 165.5117 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 165.6094 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 165.7109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 165.8203 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:19 | 165.9219 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 166.0195 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 166.1289 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 166.2305 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 166.332 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 166.4297 | 0.01 | 1.01 | -0.74 | 0.26 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 166.5313 | -0.09 | 0.91 | -0.66 | 0.34 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 166.6406 | -0.15 | 0.85 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 166.75 | -0.14 | 0.86 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:19 | 166.8398 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 166.9492 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 167.0508 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 167.1523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 167.25 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 167.3594 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 167.4609 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 167.5625 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 167.6719 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 167.7695 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 167.8711 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 167.9805 | -0.05 | 0.95 | -0.69 | 0.31 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 168.082 | -0.11 | 0.89 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 168.1797 | -0.14 | 0.86 | -0.6 | 0.4 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:19 | 168.2813 | 0 | 1 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 168.3906 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 168.4922 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:19 | 168.5898 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 168.6914 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 168.7891 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 168.9023 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 169 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 169.1016 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 169.2109 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 169.3125 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 169.4102 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 74.22 | 33.2
2019-09-04 | 14:19 | 169.5195 | -0.07 | 0.93 | -0.66 | 0.34 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 169.6211 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 169.7227 | -0.13 | 0.87 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:19 | 169.8203 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 169.9297 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 170.0313 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 170.1289 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 170.2305 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:19 | 170.332 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 170.4414 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 170.5391 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 170.6602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:19 | 170.75 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 170.8516 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 170.9492 | 0.01 | 1.01 | -0.73 | 0.27 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 171.0625 | -0.1 | 0.9 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 171.1602 | -0.15 | 0.85 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 171.2617 | -0.07 | 0.93 | -0.66 | 0.34 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 171.3594 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:19 | 171.4727 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:19 | 171.5703 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 171.6797 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 171.7813 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 14:19 | 171.8789 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 171.9805 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 172.082 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 172.1914 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 172.2891 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 172.3906 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 172.4922 | -0.07 | 0.93 | -0.66 | 0.34 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:19 | 172.6016 | -0.11 | 0.89 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 172.6992 | -0.14 | 0.86 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 172.8008 | 0.02 | 1.02 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 172.9102 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 173.0117 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 173.1094 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 173.2227 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 173.3203 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 173.4219 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 173.5195 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 173.6211 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 173.7305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 173.832 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 173.9297 | 0.02 | 1.02 | -0.76 | 0.24 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 174.0391 | -0.1 | 0.9 | -0.65 | 0.35 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 174.1406 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 33.2
2019-09-04 | 14:19 | 174.2422 | -0.14 | 0.86 | -0.61 | 0.39 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:19 | 174.3516 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:19 | 174.4492 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 174.5508 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 174.6602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 174.7617 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 174.8594 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 174.9609 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 175.0625 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 175.1602 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:19 | 175.2695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 175.3711 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:19 | 175.4805 | 0.01 | 1.01 | -0.72 | 0.28 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 175.582 | -0.13 | 0.87 | -0.63 | 0.37 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:19 | 175.6797 | -0.14 | 0.86 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:19 | 175.7813 | 0.01 | 1.01 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 175.8906 | 0.02 | 1.02 | -0.77 | 0.23 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 14:19 | 175.9922 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 176.0898 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 176.1914 | 0.03 | 1.03 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 33.2
2019-09-04 | 14:19 | 176.3008 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 176.4023 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 176.5 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 176.6094 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 176.7109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 176.8125 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 176.9102 | 0.02 | 1.02 | -0.74 | 0.26 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 177.0195 | -0.1 | 0.9 | -0.66 | 0.34 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 177.1211 | -0.14 | 0.86 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 177.2227 | -0.14 | 0.86 | -0.61 | 0.39 | -0.68 | 0.32 | 75.2 | 34.18
2019-09-04 | 14:19 | 177.332 | 0.01 | 1.01 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 177.4297 | 0.03 | 1.03 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 177.5313 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 177.6289 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 177.7422 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 177.8398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 177.9414 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 178.0391 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 178.1523 | 0.04 | 1.04 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 178.25 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:19 | 178.3516 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 178.4492 | 0.01 | 1.01 | -0.73 | 0.27 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 178.5625 | -0.09 | 0.91 | -0.64 | 0.36 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:19 | 178.6719 | -0.14 | 0.86 | -0.63 | 0.37 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:19 | 178.7617 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:19 | 178.8711 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 178.9727 | 0.03 | 1.03 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 179.0703 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 179.1797 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 14:19 | 179.2813 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 179.3789 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 179.4805 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 179.582 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 14:19 | 179.6914 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 179.7891 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 179.8906 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 180 | -0.06 | 0.94 | -0.68 | 0.32 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 180.1016 | -0.13 | 0.87 | -0.6 | 0.4 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 180.1992 | -0.12 | 0.88 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:19 | 180.3125 | 0.02 | 1.02 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 180.4102 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:19 | 180.5117 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 180.6094 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 14:19 | 180.7227 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 180.8203 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 180.9219 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 181.0313 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 181.1289 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 30.27
2019-09-04 | 14:19 | 181.2305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:19 | 181.332 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 181.4414 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 181.5391 | -0.07 | 0.93 | -0.67 | 0.33 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 181.6406 | -0.13 | 0.87 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 181.7422 | -0.13 | 0.87 | -0.6 | 0.4 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:19 | 181.8516 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 181.9609 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 182.0625 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 182.1523 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 182.2617 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:19 | 182.3594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 182.4609 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 182.582 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 182.6719 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 182.7813 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 182.8789 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 182.9805 | 0 | 1 | -0.72 | 0.28 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 183.082 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 183.1914 | -0.13 | 0.87 | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:19 | 183.2891 | -0.02 | 0.98 | -0.72 | 0.28 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 183.3906 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:19 | 183.4922 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 183.5898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 183.6992 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 183.8008 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 183.9023 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 184 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 184.1094 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 30.27
2019-09-04 | 14:19 | 184.2109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 184.3125 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 184.4219 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:19 | 184.5195 | -0.06 | 0.94 | -0.68 | 0.32 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 184.6211 | -0.11 | 0.89 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 184.7305 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:19 | 184.832 | 0.02 | 1.02 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 184.9297 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:19 | 185.0391 | 0.06 | 1.06 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 185.1406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 185.2422 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 185.3398 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:19 | 185.4414 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 185.5391 | 0.05 | 1.05 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:19 | 185.6523 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 33.2
2019-09-04 | 14:19 | 185.75 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 185.8594 | 0.05 | 1.05 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 185.9609 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:19 | 186.0703 | -0.08 | 0.92 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 34.18
2019-09-04 | 14:19 | 186.1719 | -0.11 | 0.89 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 186.2695 | -0.13 | 0.87 | -0.62 | 0.38 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:19 | 186.3711 | 0.02 | 1.02 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 186.4805 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 186.582 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:19 | 186.6797 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 186.7813 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 186.8789 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 186.9922 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 187.0898 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 187.1914 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 187.2891 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:19 | 187.4023 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 187.5 | -0.02 | 0.98 | -0.71 | 0.29 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 187.6016 | -0.12 | 0.88 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 187.6992 | -0.13 | 0.87 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 187.8125 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:19 | 187.9102 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 188.0117 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 188.1094 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 188.2227 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 188.3203 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:19 | 188.4219 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 188.5313 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 188.6289 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 188.7305 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:19 | 188.832 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 188.9414 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 33.2
2019-09-04 | 14:19 | 189.0391 | -0.08 | 0.92 | -0.66 | 0.34 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 189.1406 | -0.14 | 0.86 | -0.61 | 0.39 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:19 | 189.25 | -0.1 | 0.9 | -0.62 | 0.38 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:19 | 189.3516 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 189.4492 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 189.5508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 189.6602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 189.7617 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 189.8594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 189.9609 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 190.0703 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 75.2 | 32.23
2019-09-04 | 14:19 | 190.1719 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 190.2695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 33.2
2019-09-04 | 14:19 | 190.3711 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 190.4805 | 0 | 1 | -0.73 | 0.27 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:19 | 190.582 | -0.09 | 0.91 | -0.63 | 0.37 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:19 | 190.6992 | -0.1 | 0.9 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:19 | 190.7891 | 0.01 | 1.01 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 190.8906 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 190.9922 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 191.0898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 191.1992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 191.3008 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 191.4023 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:19 | 191.5 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 191.6094 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 191.7109 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 191.8203 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 191.9219 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 192.0195 | -0.06 | 0.94 | -0.68 | 0.32 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 192.1211 | -0.12 | 0.88 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 192.2305 | -0.12 | 0.88 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 192.332 | 0.02 | 1.02 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 192.4297 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 192.5313 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 192.6289 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 192.7422 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 192.8398 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 192.9492 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 193.0508 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:19 | 193.1523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 193.25 | 0.06 | 1.06 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:19 | 193.3594 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 193.4609 | 0.02 | 1.02 | -0.75 | 0.25 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 193.5625 | -0.09 | 0.91 | -0.65 | 0.35 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 193.6719 | -0.14 | 0.86 | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 193.7695 | -0.13 | 0.87 | 1.39 |  | -0.48 |  | 72.27 | 31.25 | anomalous heat exchanger and spray condenser pressures not included analysis
2019-09-04 | 14:19 | 193.8711 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:19 | 193.9727 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 194.082 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 194.1797 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 194.2813 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 194.3789 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 194.4922 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 194.5898 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 194.6914 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 194.7891 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 194.9023 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 195 | -0.03 | 0.97 | -0.7 | 0.3 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 195.1016 | -0.11 | 0.89 | -0.62 | 0.38 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 195.2109 | -0.13 | 0.87 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 195.3125 | 0.02 | 1.02 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 195.4102 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:19 | 195.5117 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 195.6211 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 75.2 | 33.2
2019-09-04 | 14:19 | 195.7227 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:19 | 195.8203 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 195.9219 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 196.0313 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 196.1289 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 196.2305 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 196.332 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:19 | 196.4414 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 196.5391 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 34.18
2019-09-04 | 14:19 | 196.6523 | -0.1 | 0.9 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 196.75 | -0.13 | 0.87 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 196.8516 | 0.02 | 1.02 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 196.9492 | 0.02 | 1.02 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 197.0508 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 197.1602 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 197.2617 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 197.3594 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 197.4609 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 197.5703 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 197.6797 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 197.7813 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 197.8789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 197.9805 | 0 | 1 | -0.72 | 0.28 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 198.082 | -0.1 | 0.9 | -0.65 | 0.35 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 198.1914 | -0.09 | 0.91 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 198.2891 | -0.06 | 0.94 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 31.25
2019-09-04 | 14:19 | 198.3906 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 198.4922 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 198.5898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 198.6992 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 198.8008 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 198.9102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 199.0117 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:19 | 199.1094 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:19 | 199.2109 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:19 | 199.3203 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 199.4219 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:19 | 199.5195 | -0.04 | 0.96 | -0.7 | 0.3 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:19 | 199.6211 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 14:19 | 199.7305 | -0.14 | 0.86 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 199.832 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 199.9297 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:19 | 200.0391 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 200.1406 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:19 | 200.2422 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:19 | 200.3516 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 200.4492 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 200.5508 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:19 | 200.6523 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 200.75 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 200.8594 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 200.9609 | 0.01 | 1.01 | -0.73 | 0.27 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:19 | 201.0625 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:19 | 201.1719 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 33.2
2019-09-04 | 14:19 | 201.2695 | -0.15 | 0.85 | -0.59 | 0.41 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:19 | 201.3711 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:19 | 201.4727 | 0.05 | 1.05 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:19 | 201.582 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:19 | 201.6797 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 30.27
2019-09-04 | 14:19 | 201.7813 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 201.8789 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 201.9922 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 202.0898 | 0.06 | 1.06 | -0.77 | 0.23 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:19 | 202.1914 | 0.05 | 1.05 | -0.77 | 0.23 | -0.72 | 0.28 | 73.24 | 31.25
2019-09-04 | 14:19 | 202.3008 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 202.4023 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:19 | 202.5 | -0.07 | 0.93 | -0.68 | 0.32 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 202.6094 | -0.11 | 0.89 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:19 | 202.7109 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:19 | 202.8125 | 0.02 | 1.02 | -0.74 | 0.26 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:19 | 202.9102 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:19 | 203.0195 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:19 | 203.1211 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:19 | 203.2227 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 203.3203 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:19 | 203.4297 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:19 | 203.5313 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:19 | 203.6289 | 0.06 | 1.06 | -0.79 | 0.21 | -0.72 | 0.28 | 73.24 | 32.23
2019-09-04 | 14:19 | 203.7422 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:19 | 203.8398 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:19 | 203.9414 | 0.04 | 1.04 | -0.74 | 0.26 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:19 | 204.0391 | -0.08 | 0.92 | -0.66 | 0.34 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 204.1523 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 204.25 | -0.13 | 0.87 | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 204.3516 | 0.04 | 1.04 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 204.4492 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 204.5508 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 204.6719 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 204.7617 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 204.8711 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 204.9727 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 205.0703 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:20 | 205.1797 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 205.2813 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 205.3789 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 205.4805 | -0.03 | 0.97 | -0.71 | 0.29 | -0.71 | 0.29 | 74.22 | 31.25
2019-09-04 | 14:20 | 205.5898 | -0.1 | 0.9 | -0.63 | 0.37 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:20 | 205.6914 | -0.14 | 0.86 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 205.7891 | -0.06 | 0.94 | -0.64 | 0.36 | -0.66 | 0.34 | 72.27 | 32.23
2019-09-04 | 14:20 | 205.8906 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:20 | 206 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 206.1016 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 206.1992 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:20 | 206.3008 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 29.3
2019-09-04 | 14:20 | 206.4102 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 206.5117 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 206.6094 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 206.7109 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 206.8203 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:20 | 206.9219 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 207.0195 | -0.04 | 0.96 | -0.69 | 0.31 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:20 | 207.1289 | -0.11 | 0.89 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:20 | 207.2305 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 34.18
2019-09-04 | 14:20 | 207.332 | 0.03 | 1.03 | -0.74 | 0.26 | -0.69 | 0.31 | 72.27 | 34.18
2019-09-04 | 14:20 | 207.4297 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 207.5391 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 207.6406 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 207.7422 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:20 | 207.8398 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 207.9492 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 208.0508 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:20 | 208.1523 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 208.2617 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:20 | 208.3594 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:20 | 208.4609 | 0 | 1 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 208.5703 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 208.6719 | -0.1 | 0.9 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:20 | 208.7695 | -0.1 | 0.9 | -0.61 | 0.39 | -0.69 | 0.31 | 74.22 | 34.18
2019-09-04 | 14:20 | 208.8711 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 208.9727 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 209.082 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 34.18
2019-09-04 | 14:20 | 209.1797 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 209.2813 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 209.3906 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 209.4922 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 209.5898 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:20 | 209.6992 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 209.8008 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 209.9023 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 210 | -0.03 | 0.97 | -0.71 | 0.29 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 210.1016 | -0.1 | 0.9 | -0.62 | 0.38 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 210.2109 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 210.3125 | 0.03 | 1.03 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:20 | 210.4102 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 210.5117 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 210.6211 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 210.7305 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 210.832 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 210.9297 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 211.0313 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 211.1289 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 211.2422 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 211.3398 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 211.4414 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 211.5508 | -0.07 | 0.93 | -0.65 | 0.35 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 211.6523 | -0.12 | 0.88 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 211.75 | -0.14 | 0.86 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 211.8516 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 211.9609 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 212.0625 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 212.1602 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 212.2617 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 212.3711 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 212.4727 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 212.5703 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 212.6797 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 212.7813 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 212.8789 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 212.9922 | -0.01 | 0.99 | -0.72 | 0.28 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 213.0898 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 213.1914 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:20 | 213.2891 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 213.3906 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 213.5 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 213.6016 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 213.6992 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 213.8125 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 213.9102 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 214.0117 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 214.1094 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 214.2227 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 214.3203 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 75.2 | 34.18
2019-09-04 | 14:20 | 214.4219 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 214.5195 | 0 | 1 | -0.69 | 0.31 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:20 | 214.6289 | -0.11 | 0.89 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:20 | 214.7305 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 214.832 | 0.03 | 1.03 | -0.74 | 0.26 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:20 | 214.9297 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 215.0391 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 215.1406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 215.2422 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 215.3516 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 215.4492 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 215.5508 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:20 | 215.6602 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 215.7617 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 215.8594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 215.9609 | 0.01 | 1.01 | -0.74 | 0.26 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 216.0703 | -0.1 | 0.9 | -0.64 | 0.36 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:20 | 216.1719 | -0.1 | 0.9 | -0.6 | 0.4 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:20 | 216.2695 | -0.11 | 0.89 | -0.59 | 0.41 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:20 | 216.3711 | 0.03 | 1.03 | -0.74 | 0.26 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 216.4805 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 216.582 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 216.6914 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 216.7891 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 216.8906 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 216.9922 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:20 | 217.0898 | 0.06 | 1.06 | -0.76 | 0.24 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:20 | 217.1992 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 217.3008 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 217.4023 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 217.5117 | 0 | 1 | -0.7 | 0.3 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:20 | 217.6094 | -0.07 | 0.93 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 217.7109 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 217.8125 | 0.02 | 1.02 | -0.72 | 0.28 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:20 | 217.9219 | 0.02 | 1.02 | -0.75 | 0.25 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:20 | 218.0195 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 218.1211 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:20 | 218.2227 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 218.332 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 218.4297 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:20 | 218.5313 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 75.2 | 32.23
2019-09-04 | 14:20 | 218.6289 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 218.7422 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 218.8398 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 218.9492 | 0.03 | 1.03 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 219.0508 | -0.08 | 0.92 | -0.66 | 0.34 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 219.1523 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 14:20 | 219.25 | -0.13 | 0.87 | -0.6 | 0.4 | -0.67 | 0.33 | 74.22 | 31.25
2019-09-04 | 14:20 | 219.3516 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 219.4609 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 219.5625 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 219.6719 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 219.7617 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 219.8711 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 219.9727 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 220.082 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 220.1797 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 220.2813 | 0.05 | 1.05 | -0.79 | 0.21 | -0.72 | 0.28 | 73.24 | 31.25
2019-09-04 | 14:20 | 220.3789 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 220.4805 | 0 | 1 | -0.71 | 0.29 | -0.7 | 0.3 | 75.2 | 32.23
2019-09-04 | 14:20 | 220.5898 | -0.11 | 0.89 | -0.64 | 0.36 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:20 | 220.6992 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 71.29 | 30.27
2019-09-04 | 14:20 | 220.7891 | -0.14 | 0.86 | -0.58 | 0.42 | -0.66 | 0.34 | 72.27 | 31.25
2019-09-04 | 14:20 | 220.9023 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 221 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 221.1016 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 221.2109 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 221.3125 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 221.4102 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 221.5117 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:20 | 221.6211 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 221.7227 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:20 | 221.8203 | 0.06 | 1.06 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 221.9219 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 222.0313 | -0.03 | 0.97 | -0.69 | 0.31 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 222.1289 | -0.1 | 0.9 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 222.2305 | -0.1 | 0.9 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:20 | 222.3398 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 222.4414 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:20 | 222.5391 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 222.6523 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 222.75 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:20 | 222.8516 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:20 | 222.9492 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 29.3
2019-09-04 | 14:20 | 223.0508 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 223.1602 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 223.2617 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:20 | 223.3594 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 223.4609 | 0.04 | 1.04 | -0.75 | 0.25 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 223.5703 | -0.08 | 0.92 | -0.66 | 0.34 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 223.6719 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:20 | 223.7813 | -0.14 | 0.86 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 223.8789 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 223.9805 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 224.082 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 224.1914 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 224.2891 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 224.3906 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 224.4922 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:20 | 224.5898 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 224.6992 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 224.8008 | 0.08 | 1.08 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 224.9023 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 225.0117 | 0 | 1 | -0.73 | 0.27 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 225.1094 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 225.2109 | -0.09 | 0.91 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 225.3203 | 0.01 | 1.01 | -0.71 | 0.29 | -0.67 | 0.33 | 71.29 | 29.3
2019-09-04 | 14:20 | 225.4219 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:20 | 225.5195 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 225.6211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 225.7305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 225.832 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 225.9297 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 226.0391 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 226.1406 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 226.2422 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:20 | 226.3398 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:20 | 226.4492 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 226.5508 | -0.06 | 0.94 | -0.68 | 0.32 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 226.6523 | -0.11 | 0.89 | -0.62 | 0.38 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 226.7617 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 226.8594 | 0.02 | 1.02 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 29.3
2019-09-04 | 14:20 | 226.9609 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 227.0625 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 227.1719 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 227.2695 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 227.3711 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 227.4727 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 227.582 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 227.6797 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 227.7813 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 227.8789 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 227.9922 | 0.02 | 1.02 | -0.74 | 0.26 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 228.0898 | -0.09 | 0.91 | -0.65 | 0.35 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 228.1914 | -0.13 | 0.87 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 228.3008 | -0.14 | 0.86 | -0.59 | 0.41 | -0.67 | 0.33 | 71.29 | 31.25
2019-09-04 | 14:20 | 228.4023 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:20 | 228.5 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 228.6016 | 0.06 | 1.06 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 31.25
2019-09-04 | 14:20 | 228.7109 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:20 | 228.8125 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 228.9102 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 229.0117 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 229.1211 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:20 | 229.2227 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 229.332 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 229.4297 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 229.5313 | -0.03 | 0.97 | -0.69 | 0.31 | -0.7 | 0.3 | 73.24 | 34.18
2019-09-04 | 14:20 | 229.6289 | -0.11 | 0.89 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 229.7305 | -0.12 | 0.88 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 229.8398 | 0.02 | 1.02 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:20 | 229.9414 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:20 | 230.0391 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:20 | 230.1406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 230.25 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 230.3516 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 230.4492 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 230.5625 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 230.6719 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 230.7617 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:20 | 230.8594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 230.9727 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 231.0703 | -0.04 | 0.96 | -0.68 | 0.32 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 231.1719 | -0.1 | 0.9 | -0.63 | 0.37 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 231.2695 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:20 | 231.3789 | 0.01 | 1.01 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 231.4805 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 231.582 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 231.6914 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:20 | 231.7891 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 231.8906 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 231.9922 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 232.1016 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 232.1992 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 232.3008 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 30.27
2019-09-04 | 14:20 | 232.4102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:20 | 232.5117 | 0 | 1 | -0.71 | 0.29 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 232.6094 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 232.7227 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 232.8203 | -0.02 | 0.98 | -0.68 | 0.32 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 232.9219 | 0.02 | 1.02 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 233.0195 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 233.1289 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 233.2305 | 0.06 | 1.06 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 233.332 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 233.4297 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 233.5391 | 0.06 | 1.06 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:20 | 233.6406 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 233.7422 | 0.06 | 1.06 | -0.78 | 0.22 | -0.72 | 0.28 | 73.24 | 32.23
2019-09-04 | 14:20 | 233.8398 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 233.9414 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 234.0508 | -0.05 | 0.95 | -0.67 | 0.33 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 234.1523 | -0.12 | 0.88 | -0.64 | 0.36 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 234.2617 | -0.12 | 0.88 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 234.3594 | 0.02 | 1.02 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 234.4609 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 75.2 | 32.23
2019-09-04 | 14:20 | 234.5625 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:20 | 234.6719 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 234.7695 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 234.8711 | 0.06 | 1.06 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 234.9727 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 235.082 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 235.1797 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 235.2813 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 235.3906 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 235.4922 | 0.01 | 1.01 | -0.74 | 0.26 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 235.5898 | -0.09 | 0.91 | -0.65 | 0.35 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 235.6914 | -0.11 | 0.89 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:20 | 235.8008 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:20 | 235.9023 | 0.03 | 1.03 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 236 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 236.1016 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:20 | 236.2109 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:20 | 236.3125 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 236.4102 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 236.5195 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 236.6211 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 236.7227 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 236.832 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 30.27
2019-09-04 | 14:20 | 236.9297 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:20 | 237.0313 | -0.01 | 0.99 | -0.72 | 0.28 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 237.1289 | -0.08 | 0.92 | -0.64 | 0.36 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 237.2305 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 237.3398 | 0 | 1 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 237.4414 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 237.5508 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 237.6602 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 237.7617 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 237.8516 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 237.9609 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 238.0625 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 238.1602 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 238.2617 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 238.3594 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 75.2 | 31.25
2019-09-04 | 14:20 | 238.4727 | 0.08 | 1.08 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 238.5703 | -0.06 | 0.94 | -0.67 | 0.33 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:20 | 238.6797 | -0.12 | 0.88 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 238.7813 | -0.12 | 0.88 | -0.6 | 0.4 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 238.8789 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 238.9805 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 239.0898 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 239.1914 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 239.2891 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 239.3906 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 239.5 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 239.6016 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 239.6992 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 239.8008 | 0.08 | 1.08 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 239.9102 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 30.27
2019-09-04 | 14:20 | 240.0117 | 0.04 | 1.04 | -0.74 | 0.26 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 240.1094 | -0.07 | 0.93 | -0.65 | 0.35 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 240.2227 | -0.1 | 0.9 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 240.3203 | -0.07 | 0.93 | -0.67 | 0.33 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 240.4219 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 240.5195 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 240.6289 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 240.7305 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 240.832 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 240.9297 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 241.0391 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 241.1406 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 241.2422 | 0.06 | 1.06 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 32.23
2019-09-04 | 14:20 | 241.3516 | 0.06 | 1.06 | -0.79 | 0.21 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:20 | 241.4492 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 30.27
2019-09-04 | 14:20 | 241.5508 | 0 | 1 | -0.73 | 0.27 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 241.6602 | -0.09 | 0.91 | -0.65 | 0.35 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 241.7617 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:20 | 241.8594 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 241.9609 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 242.0625 | 0.07 | 1.07 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:20 | 242.1719 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 242.2695 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 242.3711 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 242.4805 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 242.582 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 242.6797 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 242.7813 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 242.8906 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 242.9922 | 0.06 | 1.06 | -0.76 | 0.24 | -0.72 | 0.28 | 71.29 | 31.25
2019-09-04 | 14:20 | 243.0898 | -0.05 | 0.95 | -0.67 | 0.33 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 243.1992 | -0.12 | 0.88 | -0.62 | 0.38 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 243.3008 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 243.4023 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 243.5 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 243.6094 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 243.7109 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 243.8125 | 0.07 | 1.07 | -0.76 | 0.24 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 243.9102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 244.0195 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 244.1211 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 244.2227 | 0.04 | 1.04 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:20 | 244.332 | 0.08 | 1.08 | -0.78 | 0.22 | -0.72 | 0.28 | 72.27 | 31.25
2019-09-04 | 14:20 | 244.4297 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 244.5313 | -0.02 | 0.98 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:20 | 244.6406 | -0.1 | 0.9 | -0.63 | 0.37 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:20 | 244.7422 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 71.29 | 32.23
2019-09-04 | 14:20 | 244.8398 | 0.02 | 1.02 | -0.72 | 0.28 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 244.9414 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 245.0508 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 245.1523 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:20 | 245.25 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 32.23
2019-09-04 | 14:20 | 245.3516 | 0.07 | 1.07 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 245.4492 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 245.5625 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 245.6602 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 245.7617 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 245.8711 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 245.9727 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 33.2
2019-09-04 | 14:20 | 246.0703 | -0.06 | 0.94 | -0.67 | 0.33 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 246.1797 | -0.12 | 0.88 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 246.2813 | -0.11 | 0.89 | -0.6 | 0.4 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 246.3789 | 0.04 | 1.04 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:20 | 246.4805 | 0.06 | 1.06 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 246.5898 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 246.6914 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 246.7891 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 246.8906 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 247 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 247.1016 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 247.2109 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 247.3125 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:20 | 247.4219 | 0.04 | 1.04 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 247.5117 | 0.01 | 1.01 | -0.72 | 0.28 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:20 | 247.6211 | -0.08 | 0.92 | -0.63 | 0.37 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 247.7227 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 247.8203 | -0.12 | 0.88 | -0.6 | 0.4 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:20 | 247.9219 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 248.0195 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 248.1289 | 0.04 | 1.04 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:20 | 248.2305 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 248.332 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 248.4414 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:20 | 248.5391 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 248.6406 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:20 | 248.75 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 248.8516 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 248.9492 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 249.0625 | -0.05 | 0.95 | -0.69 | 0.31 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 249.1602 | -0.08 | 0.92 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 249.2617 | -0.12 | 0.88 | -0.6 | 0.4 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 249.3594 | 0.03 | 1.03 | -0.73 | 0.27 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:20 | 249.4727 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 249.5703 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 249.6797 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 249.7695 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 249.8711 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 32.23
2019-09-04 | 14:20 | 249.9805 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:20 | 250.082 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:20 | 250.1797 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 250.2813 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 250.3906 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 250.4922 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 250.6016 | -0.04 | 0.96 | -0.67 | 0.33 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 250.6992 | -0.09 | 0.91 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 250.8008 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 250.9023 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 251.0117 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:20 | 251.1094 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 251.2109 | 0.07 | 1.07 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 251.3125 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 251.4219 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 251.5195 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 251.6211 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:20 | 251.7305 | 0.09 | 1.09 | -0.79 | 0.21 | -0.7 | 0.3 | 71.29 | 31.25
2019-09-04 | 14:20 | 251.832 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 251.9297 | 0.05 | 1.05 | -0.78 | 0.22 | -0.72 | 0.28 | 73.24 | 33.2
2019-09-04 | 14:20 | 252.0313 | 0 | 1 | -0.72 | 0.28 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:20 | 252.1406 | -0.11 | 0.89 | -0.62 | 0.38 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:20 | 252.2422 | -0.11 | 0.89 | -0.62 | 0.38 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 252.3398 | 0.03 | 1.03 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 31.25
2019-09-04 | 14:20 | 252.4414 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 252.5508 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 252.6523 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 252.75 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 252.8594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 252.9609 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 253.0625 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 253.1602 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:20 | 253.2695 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 253.3711 | 0.08 | 1.08 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:20 | 253.4727 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 74.22 | 33.2
2019-09-04 | 14:20 | 253.5703 | -0.05 | 0.95 | -0.68 | 0.32 | -0.7 | 0.3 | 73.24 | 34.18
2019-09-04 | 14:20 | 253.6797 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 253.7813 | -0.11 | 0.89 | -0.6 | 0.4 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:20 | 253.8789 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 253.9805 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 254.0898 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 254.1914 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 254.3008 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:20 | 254.4023 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 254.5 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 254.6016 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 254.6992 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 254.8125 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 254.9102 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:20 | 255.0117 | 0.04 | 1.04 | -0.73 | 0.27 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:20 | 255.1211 | -0.08 | 0.92 | -0.65 | 0.35 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:20 | 255.2227 | -0.11 | 0.89 | -0.61 | 0.39 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 255.3203 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:20 | 255.4297 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 255.5313 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:20 | 255.6289 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 255.7305 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 255.8398 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 255.9414 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 256.0391 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 256.1406 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 256.25 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:20 | 256.3516 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 256.4492 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 256.5625 | -0.01 | 0.99 | -0.72 | 0.28 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 256.6602 | -0.08 | 0.92 | -0.64 | 0.36 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 256.7617 | -0.12 | 0.88 | -0.63 | 0.37 | -0.67 | 0.33 | 73.24 | 33.2
2019-09-04 | 14:20 | 256.8594 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 256.9727 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 257.0703 | 0.06 | 1.06 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:20 | 257.1719 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:20 | 257.2695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 257.3789 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 257.4805 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:20 | 257.582 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 257.6914 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 257.7891 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:20 | 257.8906 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:20 | 257.9922 | 0.02 | 1.02 | -0.75 | 0.25 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 258.1016 | -0.1 | 0.9 | -0.66 | 0.34 | -0.68 | 0.32 | 71.29 | 32.23
2019-09-04 | 14:20 | 258.1992 | -0.09 | 0.91 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 258.3008 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:20 | 258.4023 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 258.5117 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:20 | 258.6094 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:20 | 258.7109 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 32.23
2019-09-04 | 14:20 | 258.8203 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 258.9219 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 259.0195 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:20 | 259.1211 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 259.2305 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 32.23
2019-09-04 | 14:20 | 259.332 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:20 | 259.4297 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 259.5313 | 0.01 | 1.01 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 259.6406 | -0.09 | 0.91 | -0.63 | 0.37 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 259.7422 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:20 | 259.8398 | 0.01 | 1.01 | -0.7 | 0.3 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:20 | 259.9492 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:20 | 260.0508 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 260.1523 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:20 | 260.25 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 260.3594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 260.4609 | 0.06 | 1.06 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:20 | 260.5625 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:20 | 260.6719 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:20 | 260.7695 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:20 | 260.8711 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:20 | 260.9727 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 30.27
2019-09-04 | 14:20 | 261.082 | -0.07 | 0.93 | -0.67 | 0.33 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 261.1797 | -0.11 | 0.89 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 261.2813 | -0.13 | 0.87 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:20 | 261.3906 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:20 | 261.4922 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 261.5898 | 0.06 | 1.06 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:20 | 261.6914 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 30.27
2019-09-04 | 14:20 | 261.8008 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 261.9023 | 0.07 | 1.07 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:20 | 262 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:20 | 262.1016 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 262.1992 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 262.3125 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 262.4102 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:20 | 262.5195 | 0.01 | 1.01 | -0.73 | 0.27 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:20 | 262.6211 | -0.08 | 0.92 | -0.64 | 0.36 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:20 | 262.7227 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:20 | 262.8203 | -0.34 |  | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 33.2 | anomalous boiler pressure not cinluded in the analysis
2019-09-04 | 14:20 | 262.9297 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:20 | 263.0313 | 0.04 | 1.04 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:21 | 263.1289 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 263.2305 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 263.332 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 263.4414 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 263.5391 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 263.6523 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 263.75 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 263.8516 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 263.9492 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 264.0625 | -0.05 | 0.95 | -0.68 | 0.32 | -0.7 | 0.3 | 73.24 | 29.3
2019-09-04 | 14:21 | 264.1602 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 264.2617 | -0.1 | 0.9 | -0.62 | 0.38 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:21 | 264.3594 | 0.03 | 1.03 | -0.72 | 0.28 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:21 | 264.4727 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 264.5703 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 264.6797 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 264.7813 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 264.8789 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 264.9805 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 265.082 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 265.1914 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 265.2891 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:21 | 265.3906 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 265.4922 | 0.05 | 1.05 | -0.74 | 0.26 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:21 | 265.6016 | -0.07 | 0.93 | -0.65 | 0.35 | -0.68 | 0.32 | 74.22 | 31.25
2019-09-04 | 14:21 | 265.6992 | -0.12 | 0.88 | -0.6 | 0.4 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 265.8125 | -0.13 | 0.87 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:21 | 265.9102 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 266.0117 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 266.1094 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:21 | 266.2109 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 266.3203 | 0.08 | 1.08 | -0.76 | 0.24 | -0.68 | 0.32 | 71.29 | 32.23
2019-09-04 | 14:21 | 266.4219 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:21 | 266.5195 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 266.6211 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 266.7305 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 266.832 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 266.9297 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 267.0391 | -0.02 | 0.98 | -0.7 | 0.3 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 267.1406 | -0.1 | 0.9 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:21 | 267.2422 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:21 | 267.3398 | -0.02 | 0.98 | -0.67 | 0.33 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:21 | 267.4492 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 267.5508 | 0.03 | 1.03 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 267.6602 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:21 | 267.75 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 267.8594 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 33.2
2019-09-04 | 14:21 | 267.9609 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:21 | 268.0625 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 268.1719 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 36.13
2019-09-04 | 14:21 | 268.2695 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 34.18
2019-09-04 | 14:21 | 268.3711 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 268.4805 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 268.582 | -0.03 | 0.97 | -0.71 | 0.29 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:21 | 268.6797 | -0.1 | 0.9 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 268.7813 | -0.1 | 0.9 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:21 | 268.8906 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 268.9922 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.0898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.1914 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.2891 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.4023 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.5 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.6094 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.7109 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 269.8125 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 269.9102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 270.0195 | 0.01 | 1.01 | -0.73 | 0.27 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 270.1211 | -0.07 | 0.93 | -0.65 | 0.35 | -0.67 | 0.33 | 75.2 | 32.23
2019-09-04 | 14:21 | 270.2227 | -0.11 | 0.89 | -0.62 | 0.38 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:21 | 270.332 | -0.12 | 0.88 | -0.58 | 0.42 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:21 | 270.4297 | 0.03 | 1.03 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 270.5313 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 270.6406 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 270.7422 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 71.29 | 31.25
2019-09-04 | 14:21 | 270.8398 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 270.9414 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 271.0391 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 271.1523 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:21 | 271.25 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 271.3516 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 271.4492 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 271.5625 | 0.01 | 1.01 | -0.72 | 0.28 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 271.6719 | -0.09 | 0.91 | -0.64 | 0.36 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:21 | 271.7617 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 271.8711 | 0.02 | 1.02 | -0.73 | 0.27 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 271.9727 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 272.0703 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 272.1719 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 272.2813 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 272.3789 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:21 | 272.4805 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 272.582 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 272.6914 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:21 | 272.7891 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 272.9023 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 273 | 0.03 | 1.03 | -0.74 | 0.26 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 273.1016 | -0.08 | 0.92 | -0.65 | 0.35 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 273.1992 | -0.12 | 0.88 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 273.3125 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:21 | 273.4102 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 273.5117 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 273.6094 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:21 | 273.7109 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 273.8203 | 0.06 | 1.06 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:21 | 273.9219 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 274.0195 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 274.1289 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 274.2305 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 274.3398 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 75.2 | 32.23
2019-09-04 | 14:21 | 274.4414 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 274.5391 | -0.02 | 0.98 | -0.71 | 0.29 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 274.6406 | -0.1 | 0.9 | -0.62 | 0.38 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 274.7422 | -0.12 | 0.88 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 274.8516 | -0.06 | 0.94 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:21 | 274.9492 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:21 | 275.0508 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 275.1523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 275.2617 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 275.3594 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 75.2 | 32.23
2019-09-04 | 14:21 | 275.4609 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 275.5703 | 0.05 | 1.05 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 275.6719 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 275.7695 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:21 | 275.8711 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 275.9805 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 276.082 | -0.07 | 0.93 | -0.66 | 0.34 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 276.1914 | -0.12 | 0.88 | -0.62 | 0.38 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 276.2891 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:21 | 276.3906 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:21 | 276.4922 | 0.05 | 1.05 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 276.5898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 31.25
2019-09-04 | 14:21 | 276.6992 | 0.06 | 1.06 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 276.8008 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 276.9023 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:21 | 277 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 277.1094 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 277.2109 | 0.06 | 1.06 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 277.3125 | 0.08 | 1.08 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:21 | 277.4102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:21 | 277.5195 | 0.01 | 1.01 | -0.73 | 0.27 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 277.6211 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 277.7305 | -0.11 | 0.89 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 277.832 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 73.24 | 33.2
2019-09-04 | 14:21 | 277.9297 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 278.0313 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:21 | 278.1289 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:21 | 278.2422 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 278.3398 | 0.04 | 1.04 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 278.4414 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:21 | 278.5391 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 278.6523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:21 | 278.75 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 278.8594 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 30.27
2019-09-04 | 14:21 | 278.9609 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 279.0625 | -0.04 | 0.96 | -0.69 | 0.31 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 279.1602 | -0.11 | 0.89 | -0.63 | 0.37 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 279.2617 | -0.12 | 0.88 | -0.62 | 0.38 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:21 | 279.3711 | 0.01 | 1.01 | -0.73 | 0.27 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 279.4727 | 0.02 | 1.02 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 31.25
2019-09-04 | 14:21 | 279.5703 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 30.27
2019-09-04 | 14:21 | 279.6797 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:21 | 279.7813 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 279.8789 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 279.9922 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 280.0898 | 0.05 | 1.05 | -0.77 | 0.23 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 280.1914 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 280.2891 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:21 | 280.4023 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 280.5 | 0.07 | 1.07 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 280.6016 | -0.08 | 0.92 | -0.66 | 0.34 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 280.7109 | -0.13 | 0.87 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 280.8008 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 33.2
2019-09-04 | 14:21 | 280.9102 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:21 | 281.0117 | 0.04 | 1.04 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 281.1211 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 281.2227 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:21 | 281.3203 | 0.08 | 1.08 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:21 | 281.4219 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 281.5313 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 281.6289 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 281.7305 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 281.832 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 281.9414 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:21 | 282.0391 | 0.01 | 1.01 | -0.71 | 0.29 | -0.69 | 0.31 | 74.22 | 30.27
2019-09-04 | 14:21 | 282.1523 | -0.1 | 0.9 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 282.25 | -0.11 | 0.89 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 32.23
2019-09-04 | 14:21 | 282.3516 | -0.09 | 0.91 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 32.23
2019-09-04 | 14:21 | 282.4492 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 282.5508 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 282.6602 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 282.7617 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 282.8594 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 282.9609 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 283.0703 | 0.08 | 1.08 | -0.76 | 0.24 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:21 | 283.1719 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 34.18
2019-09-04 | 14:21 | 283.2695 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 283.3711 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 283.4805 | 0.04 | 1.04 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:21 | 283.582 | -0.03 | 0.97 | -0.69 | 0.31 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 283.6914 | -0.1 | 0.9 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 283.7891 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 31.25
2019-09-04 | 14:21 | 283.8906 | 0.02 | 1.02 | -0.74 | 0.26 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 283.9922 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 284.0898 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 284.1992 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 284.3008 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 284.4023 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 284.5 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 284.6094 | 0.07 | 1.07 | -0.76 | 0.24 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:21 | 284.7109 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 284.8203 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 284.9219 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 285.0195 | 0.02 | 1.02 | -0.74 | 0.26 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 285.1289 | -0.09 | 0.91 | -0.65 | 0.35 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:21 | 285.2227 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 285.332 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 72.27 | 30.27
2019-09-04 | 14:21 | 285.4297 | 0.04 | 1.04 | -0.75 | 0.25 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 285.5313 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 285.6406 | 0.06 | 1.06 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 285.7422 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 285.8398 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:21 | 285.9492 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 286.0508 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 286.1523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 286.25 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 286.3594 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:21 | 286.4609 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:21 | 286.5625 | 0 | 1 | -0.71 | 0.29 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 286.6719 | -0.11 | 0.89 | -0.63 | 0.37 | -0.68 | 0.32 | 73.24 | 31.25
2019-09-04 | 14:21 | 286.7695 | -0.11 | 0.89 | -0.6 | 0.4 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 286.8711 | 0.01 | 1.01 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 32.23
2019-09-04 | 14:21 | 286.9727 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 287.082 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:21 | 287.1797 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 287.2813 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:21 | 287.3789 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 287.4922 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 287.5898 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 287.6914 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 287.7891 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 287.9023 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 288 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 288.1016 | -0.05 | 0.95 | -0.68 | 0.32 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 288.2109 | -0.11 | 0.89 | -0.61 | 0.39 | -0.68 | 0.32 | 72.27 | 33.2
2019-09-04 | 14:21 | 288.3125 | -0.13 | 0.87 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 288.4102 | 0.03 | 1.03 | -0.75 | 0.25 | -0.69 | 0.31 | 72.27 | 33.2
2019-09-04 | 14:21 | 288.5195 | 0.03 | 1.03 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 288.6211 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:21 | 288.7227 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 288.8203 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 34.18
2019-09-04 | 14:21 | 288.9219 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:21 | 289.0313 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 289.1289 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 289.2305 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:21 | 289.3398 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 289.4414 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 74.22 | 34.18
2019-09-04 | 14:21 | 289.5391 | 0.04 | 1.04 | -0.73 | 0.27 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 289.6523 | -0.08 | 0.92 | -0.64 | 0.36 | -0.69 | 0.31 | 75.2 | 34.18
2019-09-04 | 14:21 | 289.75 | -0.12 | 0.88 | -0.61 | 0.39 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:21 | 289.8516 | -0.1 | 0.9 | -0.59 | 0.41 | -0.67 | 0.33 | 74.22 | 30.27
2019-09-04 | 14:21 | 289.9492 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 75.2 | 32.23
2019-09-04 | 14:21 | 290.0508 | 0.08 | 1.08 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 290.1602 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 290.2617 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 290.3594 | 0.06 | 1.06 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 290.4609 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 33.2
2019-09-04 | 14:21 | 290.5703 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 290.6797 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:21 | 290.7813 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 290.8789 | 0.07 | 1.07 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 290.9805 | 0.09 | 1.09 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:21 | 291.082 | -0.03 | 0.97 | -0.71 | 0.29 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 291.1797 | -0.1 | 0.9 | -0.63 | 0.37 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:21 | 291.2891 | -0.13 | 0.87 | -0.59 | 0.41 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:21 | 291.3906 | 0.04 | 1.04 | -0.74 | 0.26 | -0.68 | 0.32 | 72.27 | 30.27
2019-09-04 | 14:21 | 291.4922 | 0.03 | 1.03 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 291.5898 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 291.6992 | 0.06 | 1.06 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 31.25
2019-09-04 | 14:21 | 291.8008 | 0.07 | 1.07 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 291.9102 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:21 | 292.0117 | 0.06 | 1.06 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 292.1094 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 292.2109 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 292.3203 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 292.4219 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:21 | 292.5195 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 75.2 | 32.23
2019-09-04 | 14:21 | 292.6289 | -0.08 | 0.92 | -0.64 | 0.36 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 292.7305 | -0.1 | 0.9 | -0.63 | 0.37 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:21 | 292.832 | -0.13 | 0.87 | -0.6 | 0.4 | -0.67 | 0.33 | 74.22 | 33.2
2019-09-04 | 14:21 | 292.9414 | 0.04 | 1.04 | -0.76 | 0.24 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 293.0391 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 293.1406 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 293.2422 | 0.06 | 1.06 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 33.2
2019-09-04 | 14:21 | 293.3398 | 0.05 | 1.05 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 32.23
2019-09-04 | 14:21 | 293.4492 | 0.05 | 1.05 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 293.5508 | 0.09 | 1.09 | -0.77 | 0.23 | -0.7 | 0.3 | 75.2 | 33.2
2019-09-04 | 14:21 | 293.6602 | 0.05 | 1.05 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:21 | 293.75 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 293.8594 | 0.07 | 1.07 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:21 | 293.9609 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 34.18
2019-09-04 | 14:21 | 294.0625 | 0.01 | 1.01 | -0.71 | 0.29 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 294.1719 | -0.08 | 0.92 | -0.63 | 0.37 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 294.2695 | -0.1 | 0.9 | -0.61 | 0.39 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 294.3711 | 0.03 | 1.03 | -0.7 | 0.3 | -0.68 | 0.32 | 73.24 | 32.23
2019-09-04 | 14:21 | 294.4727 | 0.05 | 1.05 | -0.76 | 0.24 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 294.582 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 72.27 | 30.27
2019-09-04 | 14:21 | 294.6797 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 294.7813 | 0.05 | 1.05 | -0.78 | 0.22 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 294.8789 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 294.9922 | 0.05 | 1.05 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 32.23
2019-09-04 | 14:21 | 295.0898 | 0.06 | 1.06 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 31.25
2019-09-04 | 14:21 | 295.1914 | 0.07 | 1.07 | -0.78 | 0.22 | -0.71 | 0.29 | 71.29 | 31.25
2019-09-04 | 14:21 | 295.3008 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 30.27
2019-09-04 | 14:21 | 295.4023 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 295.5 | 0.07 | 1.07 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 295.6094 | -0.04 | 0.96 | -0.69 | 0.31 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 295.7109 | -0.1 | 0.9 | -0.63 | 0.37 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 295.8125 | -0.1 | 0.9 | -0.62 | 0.38 | -0.69 | 0.31 | 75.2 | 33.2
2019-09-04 | 14:21 | 295.9102 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:21 | 296.0117 | 0.04 | 1.04 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:21 | 296.1211 | 0.06 | 1.06 | -0.76 | 0.24 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 296.2227 | 0.04 | 1.04 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 296.3203 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 296.4219 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 296.5313 | 0.08 | 1.08 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 296.6289 | 0.09 | 1.09 | -0.79 | 0.21 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 296.7305 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 72.27 | 31.25
2019-09-04 | 14:21 | 296.8398 | 0.08 | 1.08 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 296.9414 | 0.08 | 1.08 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 297.0391 | 0.04 | 1.04 | -0.74 | 0.26 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 297.1406 | -0.07 | 0.93 | -0.64 | 0.36 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 297.25 | -0.11 | 0.89 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 297.3516 | -0.12 | 0.88 | -0.59 | 0.41 | -0.68 | 0.32 | 72.27 | 32.23
2019-09-04 | 14:21 | 297.4492 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 297.5508 | 0.04 | 1.04 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 297.6602 | 0.06 | 1.06 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 297.7813 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 33.2
2019-09-04 | 14:21 | 297.8711 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 297.9727 | 0.06 | 1.06 | -0.77 | 0.23 | -0.71 | 0.29 | 74.22 | 32.23
2019-09-04 | 14:21 | 298.0703 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 31.25
2019-09-04 | 14:21 | 298.1719 | 0.06 | 1.06 | -0.79 | 0.21 | -0.7 | 0.3 | 73.24 | 34.18
2019-09-04 | 14:21 | 298.2813 | 0.07 | 1.07 | -0.77 | 0.23 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:21 | 298.3789 | 0.07 | 1.07 | -0.77 | 0.23 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 298.4805 | 0.08 | 1.08 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 298.5898 | -0.04 | 0.96 | -0.68 | 0.32 | -0.7 | 0.3 | 72.27 | 31.25
2019-09-04 | 14:21 | 298.6914 | -0.07 | 0.93 | -0.62 | 0.38 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 298.7891 | -0.12 | 0.88 | -0.61 | 0.39 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 298.8906 | 0.02 | 1.02 | -0.73 | 0.27 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 299 | 0.04 | 1.04 | -0.76 | 0.24 | -0.7 | 0.3 | 73.24 | 34.18
2019-09-04 | 14:21 | 299.1016 | 0.05 | 1.05 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 299.1992 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 31.25
2019-09-04 | 14:21 | 299.3008 | 0.09 | 1.09 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:21 | 299.4102 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 299.5117 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 299.6094 | 0.07 | 1.07 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 32.23
2019-09-04 | 14:21 | 299.7109 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 33.2
2019-09-04 | 14:21 | 299.8203 | 0.06 | 1.06 | -0.78 | 0.22 | -0.71 | 0.29 | 73.24 | 31.25
2019-09-04 | 14:21 | 299.9219 | 0.06 | 1.06 | -0.79 | 0.21 | -0.71 | 0.29 | 73.24 | 32.23
2019-09-04 | 14:21 | 300.0313 | 0.04 | 1.04 | -0.75 | 0.25 | -0.7 | 0.3 | 71.29 | 30.27
2019-09-04 | 14:21 | 300.1406 | -0.09 | 0.91 | -0.64 | 0.36 | -0.69 | 0.31 | 73.24 | 32.23
2019-09-04 | 14:21 | 300.2305 | -0.12 | 0.88 | -0.6 | 0.4 | -0.67 | 0.33 | 73.24 | 33.2
2019-09-04 | 14:21 | 300.332 | -0.13 | 0.87 | -0.6 | 0.4 | -0.69 | 0.31 | 74.22 | 32.23
2019-09-04 | 14:21 | 300.4414 | 0.04 | 1.04 | -0.75 | 0.25 | -0.69 | 0.31 | 73.24 | 33.2
2019-09-04 | 14:21 | 300.5391 | 0.04 | 1.04 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 31.25
2019-09-04 | 14:21 | 300.6523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 32.23
2019-09-04 | 14:21 | 300.75 | 0.05 | 1.05 | -0.78 | 0.22 | -0.69 | 0.31 | 72.27 | 31.25
2019-09-04 | 14:21 | 300.8398 | 0.06 | 1.06 | -0.77 | 0.23 | -0.7 | 0.3 | 74.22 | 32.23
2019-09-04 | 14:21 | 300.9492 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 72.27 | 32.23
2019-09-04 | 14:21 | 301.0508 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 74.22 | 33.2
2019-09-04 | 14:21 | 301.1602 | 0.06 | 1.06 | -0.78 | 0.22 | -0.7 | 0.3 | 73.24 | 31.25

## 10.5mL s
|  |  |  | BoilerPressure |  | HEPressure |  | SCPressure
Date | Clock | Timer |  | Gauge (raw) | Absolute (analysis) | Gauge (raw) | Absolute (analysis) | Gauge (raw) | Absolute (analysis) | HETemperature | SCTemperature
2019-10-01 | 9:32 | 1.0703 | 1.0703 | 0.04 | 1.04 | -0.25 | 0.75 | -0.22 | 0.78 | 31.25 | 22.46
2019-10-01 | 9:32 | 1.1602 | 1.1602 | 0.03 | 1.03 | -0.26 | 0.74 | -0.23 | 0.77 | 30.27 | 23.44 |  | Volume | Seconds
2019-10-01 | 9:32 | 1.2695 | 1.2695 | 0.02 | 1.02 | -0.27 | 0.73 | -0.23 | 0.77 | 31.25 | 23.44 |  | 100 | 9 | start
2019-10-01 | 9:32 | 1.3711 | 1.3711 | 0.04 | 1.04 | -0.27 | 0.73 | -0.24 | 0.76 | 30.27 | 23.44 |  | 100 | 9
2019-10-01 | 9:32 | 1.4805 | 1.4805 | 0.04 | 1.04 | -0.27 | 0.73 | -0.22 | 0.78 | 30.27 | 23.44 |  | 100 | 9
2019-10-01 | 9:32 | 1.5781 | 1.5781 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 32.23 | 25.39
2019-10-01 | 9:32 | 1.6797 | 1.6797 | -0.02 | 0.98 | -0.24 | 0.76 | -0.23 | 0.77 | 31.25 | 24.41 |  | 100 | 10 | end
2019-10-01 | 9:32 | 1.7812 | 1.7812 | -0.04 | 0.96 | -0.23 | 0.77 | -0.22 | 0.78 | 30.27 | 24.41 |  | 100 | 10
2019-10-01 | 9:32 | 1.8906 | 1.8906 | -0.05 | 0.95 | -0.23 | 0.77 | -0.21 | 0.79 | 30.27 | 24.41 |  | 100 | 10
2019-10-01 | 9:32 | 1.9883 | 1.9883 | -0.04 | 0.96 | -0.22 | 0.78 | -0.2 | 0.8 | 30.27 | 24.41
2019-10-01 | 9:32 | 2.0898 | 2.0898 | -0.04 | 0.96 | -0.21 | 0.79 | -0.21 | 0.79 | 30.27 | 24.41
2019-10-01 | 9:32 | 2.1875 | 2.1875 | 0.02 | 1.02 | -0.25 | 0.75 | -0.22 | 0.78 | 31.25 | 25.39
2019-10-01 | 9:32 | 2.3008 | 2.3008 | 0.01 | 1.01 | -0.26 | 0.74 | -0.22 | 0.78 | 32.23 | 24.41
2019-10-01 | 9:32 | 2.3984 | 2.3984 | 0.03 | 1.03 | -0.26 | 0.74 | -0.22 | 0.78 | 30.27 | 24.41
2019-10-01 | 9:32 | 2.5 | 2.5 | 0.02 | 1.02 | -0.26 | 0.74 | -0.21 | 0.79 | 30.27 | 25.39
2019-10-01 | 9:32 | 2.5977 | 2.5977 | 0.04 | 1.04 | -0.26 | 0.74 | -0.23 | 0.77 | 30.27 | 24.41
2019-10-01 | 9:32 | 2.7109 | 2.7109 | 0.04 | 1.04 | -0.26 | 0.74 | -0.23 | 0.77 | 30.27 | 24.41
2019-10-01 | 9:32 | 2.8086 | 2.8086 | 0.03 | 1.03 | -0.26 | 0.74 | -0.23 | 0.77 | 31.25 | 24.41
2019-10-01 | 9:32 | 2.9102 | 2.9102 | 0.04 | 1.04 | -0.27 | 0.73 | -0.23 | 0.77 | 30.27 | 24.41
2019-10-01 | 9:32 | 3.0195 | 3.0195 | 0.04 | 1.04 | -0.27 | 0.73 | -0.24 | 0.76 | 30.27 | 24.41
2019-10-01 | 9:32 | 3.1211 | 3.1211 | 0.02 | 1.02 | -0.27 | 0.73 | -0.23 | 0.77 | 30.27 | 24.41
2019-10-01 | 9:32 | 3.2188 | 3.2188 | -0.03 | 0.97 | -0.24 | 0.76 | -0.22 | 0.78 | 30.27 | 24.41
2019-10-01 | 9:32 | 3.3203 | 3.3203 | -0.04 | 0.96 | -0.22 | 0.78 | -0.21 | 0.79 | 31.25 | 25.39
2019-10-01 | 9:32 | 3.4297 | 3.4297 | -0.06 | 0.94 | -0.22 | 0.78 | -0.2 | 0.8 | 31.25 | 25.39
2019-10-01 | 9:32 | 3.5312 | 3.5312 | -0.05 | 0.95 | -0.21 | 0.79 | -0.21 | 0.79 | 30.27 | 26.37
2019-10-01 | 9:32 | 3.6289 | 3.6289 | 0.02 | 1.02 | -0.23 | 0.77 | -0.2 | 0.8 | 31.25 | 25.39
2019-10-01 | 9:32 | 3.7305 | 3.7305 | 0.02 | 1.02 | -0.24 | 0.76 | -0.21 | 0.79 | 30.27 | 24.41
2019-10-01 | 9:32 | 3.8398 | 3.8398 | 0.03 | 1.03 | -0.26 | 0.74 | -0.2 | 0.8 | 31.25 | 26.37
2019-10-01 | 9:32 | 3.9375 | 3.9375 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 32.23 | 25.39
2019-10-01 | 9:32 | 4.0391 | 4.0391 | 0.03 | 1.03 | -0.27 | 0.73 | -0.23 | 0.77 | 31.25 | 25.39
2019-10-01 | 9:32 | 4.1484 | 4.1484 | 0.04 | 1.04 | -0.25 | 0.75 | -0.23 | 0.77 | 30.27 | 27.34 |  | Take equilibrium pressures from 200 seconds
2019-10-01 | 9:32 | 4.25 | 4.25 | 0.03 | 1.03 | -0.28 | 0.72 | -0.23 | 0.77 | 31.25 | 25.39
2019-10-01 | 9:32 | 4.3477 | 4.3477 | 0.03 | 1.03 | -0.27 | 0.73 | -0.23 | 0.77 | 31.25 | 27.34 |  | minimum boiler pressure from 200 seconds is: |  |  |  | 0.76 |  | average Pb | 0.92332
2019-10-01 | 9:32 | 4.4492 | 4.4492 | 0.03 | 1.03 | -0.27 | 0.73 | -0.24 | 0.76 | 31.25 | 25.39 |  | maximum boiler pressure from 200 seconds is: |  |  |  | 1
2019-10-01 | 9:32 | 4.5586 | 4.5586 | 0.03 | 1.03 | -0.28 | 0.72 | -0.24 | 0.76 | 30.27 | 27.34
2019-10-01 | 9:32 | 4.6602 | 4.6602 | 0 | 1 | -0.23 | 0.77 | -0.22 | 0.78 | 30.27 | 26.37 |  | minimum heat exchanger pressure from 200 seconds is: |  |  |  | 0.22 |  | average Phe | 0.27686
2019-10-01 | 9:32 | 4.7578 | 4.7578 | -0.04 | 0.96 | -0.21 | 0.79 | -0.22 | 0.78 | 30.27 | 25.39 |  | maximum heat exchanger pressure from 200 seconds is: |  |  |  | 0.42
2019-10-01 | 9:32 | 4.8711 | 4.8711 | -0.05 | 0.95 | -0.22 | 0.78 | -0.21 | 0.79 | 30.27 | 25.39
2019-10-01 | 9:32 | 4.9688 | 4.9688 | -0.03 | 0.97 | -0.22 | 0.78 | -0.22 | 0.78 | 31.25 | 27.34
2019-10-01 | 9:32 | 5.0703 | 5.0703 | -0.04 | 0.96 | -0.21 | 0.79 | -0.2 | 0.8 | 31.25 | 26.37
2019-10-01 | 9:32 | 5.168 | 5.168 | 0.01 | 1.01 | -0.26 | 0.74 | -0.2 | 0.8 | 32.23 | 28.32
2019-10-01 | 9:32 | 5.2812 | 5.2812 | 0.03 | 1.03 | -0.25 | 0.75 | -0.21 | 0.79 | 32.23 | 29.3
2019-10-01 | 9:32 | 5.3789 | 5.3789 | 0.03 | 1.03 | -0.26 | 0.74 | -0.22 | 0.78 | 31.25 | 27.34
2019-10-01 | 9:32 | 5.4805 | 5.4805 | 0.01 | 1.01 | -0.26 | 0.74 | -0.22 | 0.78 | 30.27 | 27.34
2019-10-01 | 9:32 | 5.5781 | 5.5781 | 0.03 | 1.03 | -0.25 | 0.75 | -0.23 | 0.77 | 31.25 | 27.34
2019-10-01 | 9:32 | 5.6875 | 5.6875 | 0.03 | 1.03 | -0.25 | 0.75 | -0.22 | 0.78 | 30.27 | 26.37
2019-10-01 | 9:32 | 5.7891 | 5.7891 | 0.02 | 1.02 | -0.26 | 0.74 | -0.23 | 0.77 | 30.27 | 26.37
2019-10-01 | 9:32 | 5.8906 | 5.8906 | 0.02 | 1.02 | -0.28 | 0.72 | -0.23 | 0.77 | 30.27 | 27.34
2019-10-01 | 9:32 | 5.9883 | 5.9883 | 0.03 | 1.03 | -0.26 | 0.74 | -0.23 | 0.77 | 31.25 | 26.37
2019-10-01 | 9:32 | 6.0977 | 6.0977 | 0.02 | 1.02 | -0.27 | 0.73 | -0.25 | 0.75 | 30.27 | 26.37
2019-10-01 | 9:32 | 6.1992 | 6.1992 | -0.02 | 0.98 | -0.24 | 0.76 | -0.22 | 0.78 | 30.27 | 26.37
2019-10-01 | 9:32 | 6.3008 | 6.3008 | -0.02 | 0.98 | -0.22 | 0.78 | -0.21 | 0.79 | 30.27 | 27.34
2019-10-01 | 9:32 | 6.4102 | 6.4102 | -0.05 | 0.95 | -0.22 | 0.78 | -0.22 | 0.78 | 31.25 | 26.37
2019-10-01 | 9:32 | 6.5078 | 6.5078 | -0.06 | 0.94 | -0.21 | 0.79 | -0.2 | 0.8 | 33.2 | 28.32
2019-10-01 | 9:32 | 6.6094 | 6.6094 | 0 | 1 | -0.24 | 0.76 | -0.2 | 0.8 | 32.23 | 29.3
2019-10-01 | 9:32 | 6.7109 | 6.7109 | 0.03 | 1.03 | -0.25 | 0.75 | -0.21 | 0.79 | 31.25 | 26.37
2019-10-01 | 9:32 | 6.8203 | 6.8203 | 0.02 | 1.02 | -0.24 | 0.76 | -0.22 | 0.78 | 31.25 | 29.3
2019-10-01 | 9:32 | 6.918 | 6.918 | 0.03 | 1.03 | -0.25 | 0.75 | -0.22 | 0.78 | 31.25 | 30.27
2019-10-01 | 9:32 | 7.0195 | 7.0195 | 0.01 | 1.01 | -0.26 | 0.74 | -0.23 | 0.77 | 31.25 | 27.34
2019-10-01 | 9:32 | 7.1211 | 7.1211 | 0.03 | 1.03 | -0.26 | 0.74 | -0.23 | 0.77 | 30.27 | 27.34 |  | temperature equilibrium from 125 seconds
2019-10-01 | 9:32 | 7.2305 | 7.2305 | 0.03 | 1.03 | -0.26 | 0.74 | -0.22 | 0.78 | 30.27 | 27.34
2019-10-01 | 9:32 | 7.3281 | 7.3281 | 0.02 | 1.02 | -0.27 | 0.73 | -0.23 | 0.77 | 32.23 | 28.32 |  | minimum heat exchanger outlet temperature is: |  |  | 68.36 |  | average SC bath temp |  | 24.9894
2019-10-01 | 9:32 | 7.4297 | 7.4297 | 0.03 | 1.03 | -0.27 | 0.73 | -0.21 | 0.79 | 31.25 | 28.32 |  | maximum heat exchanger outlet temperature is: |  |  | 76.17
2019-10-01 | 9:32 | 7.5312 | 7.5312 | 0.04 | 1.04 | -0.28 | 0.72 | -0.24 | 0.76 | 31.25 | 28.32
2019-10-01 | 9:32 | 7.6406 | 7.6406 | 0 | 1 | -0.26 | 0.74 | -0.24 | 0.76 | 30.27 | 28.32 |  | average HE outlet temperature is: |  |  | 73.5734
2019-10-01 | 9:32 | 7.7383 | 7.7383 | -0.03 | 0.97 | -0.23 | 0.77 | -0.22 | 0.78 | 31.25 | 29.3
2019-10-01 | 9:32 | 7.8477 | 7.8477 | -0.03 | 0.97 | -0.24 | 0.76 | -0.21 | 0.79 | 32.23 | 28.32 |  | number of temperature points measured is: |  |  | 1752
2019-10-01 | 9:32 | 7.9492 | 7.9492 | -0.05 | 0.95 | -0.22 | 0.78 | -0.21 | 0.79 | 30.27 | 28.32
2019-10-01 | 9:32 | 8.0508 | 8.0508 | -0.04 | 0.96 | -0.22 | 0.78 | -0.2 | 0.8 | 30.27 | 29.3 |  | st dev he temp |  |  | 0.91322
2019-10-01 | 9:32 | 8.1484 | 8.1484 | 0.01 | 1.01 | -0.25 | 0.75 | -0.21 | 0.79 | 30.27 | 28.32
2019-10-01 | 9:32 | 8.25 | 8.25 | 0.02 | 1.02 | -0.26 | 0.74 | -0.22 | 0.78 | 30.27 | 28.32
2019-10-01 | 9:32 | 8.3594 | 8.3594 | 0.03 | 1.03 | -0.25 | 0.75 | -0.22 | 0.78 | 32.23 | 28.32
2019-10-01 | 9:32 | 8.4609 | 8.4609 | 0.04 | 1.04 | -0.26 | 0.74 | -0.22 | 0.78 | 30.27 | 29.3
2019-10-01 | 9:32 | 8.5586 | 8.5586 | 0.03 | 1.03 | -0.26 | 0.74 | -0.21 | 0.79 | 32.23 | 29.3
2019-10-01 | 9:32 | 8.6602 | 8.6602 | 0.03 | 1.03 | -0.26 | 0.74 | -0.23 | 0.77 | 30.27 | 28.32
2019-10-01 | 9:32 | 8.7695 | 8.7695 | 0.03 | 1.03 | -0.26 | 0.74 | -0.24 | 0.76 | 32.23 | 30.27
2019-10-01 | 9:32 | 8.8711 | 8.8711 | 0.03 | 1.03 | -0.26 | 0.74 | -0.22 | 0.78 | 31.25 | 28.32
2019-10-01 | 9:32 | 8.9805 | 8.9805 | 0.03 | 1.03 | -0.27 | 0.73 | -0.23 | 0.77 | 31.25 | 28.32
2019-10-01 | 9:32 | 9.0781 | 9.0781 | 0.02 | 1.02 | -0.29 | 0.71 | -0.24 | 0.76 | 30.27 | 28.32
2019-10-01 | 9:32 | 9.1797 | 9.1797 | -0.02 | 0.98 | -0.26 | 0.74 | -0.24 | 0.76 | 31.25 | 28.32
2019-10-01 | 9:32 | 9.2812 | 9.2812 | -0.04 | 0.96 | -0.23 | 0.77 | -0.23 | 0.77 | 31.25 | 29.3
2019-10-01 | 9:32 | 9.3906 | 9.3906 | -0.04 | 0.96 | -0.24 | 0.76 | -0.23 | 0.77 | 31.25 | 28.32
2019-10-01 | 9:32 | 9.4883 | 9.4883 | -0.05 | 0.95 | -0.23 | 0.77 | -0.24 | 0.76 | 32.23 | 30.27
2019-10-01 | 9:32 | 9.5898 | 9.5898 | -0.05 | 0.95 | -0.25 | 0.75 | -0.22 | 0.78 | 34.18 | 29.3
2019-10-01 | 9:32 | 9.6875 | 9.6875 | 0.03 | 1.03 | -0.29 | 0.71 | -0.25 | 0.75 | 35.16 | 29.3
2019-10-01 | 9:32 | 9.7891 | 9.7891 | 0.02 | 1.02 | -0.31 | 0.69 | -0.27 | 0.73 | 36.13 | 29.3
2019-10-01 | 9:32 | 9.8984 | 9.8984 | 0.02 | 1.02 | -0.32 | 0.68 | -0.28 | 0.72 | 38.09 | 30.27
2019-10-01 | 9:32 | 10 | 10 | 0.03 | 1.03 | -0.33 | 0.67 | -0.3 | 0.7 | 40.04 | 29.3
2019-10-01 | 9:32 | 10.1094 | 10.1094 | 0.04 | 1.04 | -0.34 | 0.66 | -0.3 | 0.7 | 42.97 | 28.32
2019-10-01 | 9:32 | 10.2109 | 10.2109 | 0.03 | 1.03 | -0.36 | 0.64 | -0.32 | 0.68 | 44.92 | 29.3
2019-10-01 | 9:32 | 10.3086 | 10.3086 | 0.04 | 1.04 | -0.37 | 0.63 | -0.33 | 0.67 | 46.88 | 29.3
2019-10-01 | 9:32 | 10.4102 | 10.4102 | 0.02 | 1.02 | -0.37 | 0.63 | -0.34 | 0.66 | 48.83 | 29.3
2019-10-01 | 9:32 | 10.5195 | 10.5195 | 0.03 | 1.03 | -0.38 | 0.62 | -0.33 | 0.67 | 50.78 | 29.3
2019-10-01 | 9:32 | 10.6211 | 10.6211 | 0.03 | 1.03 | -0.39 | 0.61 | -0.36 | 0.64 | 52.73 | 29.3
2019-10-01 | 9:32 | 10.7188 | 10.7188 | -0.04 | 0.96 | -0.33 | 0.67 | -0.34 | 0.66 | 56.64 | 29.3
2019-10-01 | 9:32 | 10.8203 | 10.8203 | -0.06 | 0.94 | -0.33 | 0.67 | -0.34 | 0.66 | 57.62 | 29.3
2019-10-01 | 9:32 | 10.9297 | 10.9297 | -0.07 | 0.93 | -0.32 | 0.68 | -0.34 | 0.66 | 59.57 | 30.27
2019-10-01 | 9:32 | 11.0312 | 11.0312 | -0.07 | 0.93 | -0.32 | 0.68 | -0.32 | 0.68 | 60.55 | 29.3
2019-10-01 | 9:32 | 11.1289 | 11.1289 | 0 | 1 | -0.39 | 0.61 | -0.34 | 0.66 | 62.5 | 30.27
2019-10-01 | 9:32 | 11.2383 | 11.2383 | 0.03 | 1.03 | -0.42 | 0.58 | -0.37 | 0.63 | 63.48 | 29.3
2019-10-01 | 9:32 | 11.3398 | 11.3398 | 0.02 | 1.02 | -0.42 | 0.58 | -0.37 | 0.63 | 64.45 | 31.25
2019-10-01 | 9:32 | 11.4375 | 11.4375 | 0.02 | 1.02 | -0.43 | 0.57 | -0.39 | 0.61 | 66.41 | 29.3
2019-10-01 | 9:32 | 11.5391 | 11.5391 | 0.04 | 1.04 | -0.44 | 0.56 | -0.38 | 0.62 | 67.38 | 29.3
2019-10-01 | 9:32 | 11.6484 | 11.6484 | 0.02 | 1.02 | -0.44 | 0.56 | -0.39 | 0.61 | 69.34 | 29.3
2019-10-01 | 9:32 | 11.75 | 11.75 | 0.03 | 1.03 | -0.44 | 0.56 | -0.41 | 0.59 | 69.34 | 30.27
2019-10-01 | 9:32 | 11.8477 | 11.8477 | 0.03 | 1.03 | -0.45 | 0.55 | -0.43 | 0.57 | 69.34 | 29.3
2019-10-01 | 9:32 | 11.9492 | 11.9492 | 0.01 | 1.01 | -0.47 | 0.53 | -0.42 | 0.58 | 69.34 | 30.27
2019-10-01 | 9:32 | 12.0586 | 12.0586 | 0.03 | 1.03 | -0.47 | 0.53 | -0.42 | 0.58 | 70.31 | 29.3
2019-10-01 | 9:32 | 12.1602 | 12.1602 | 0.01 | 1.01 | -0.43 | 0.57 | -0.41 | 0.59 | 71.29 | 29.3
2019-10-01 | 9:32 | 12.2578 | 12.2578 | -0.06 | 0.94 | -0.38 | 0.62 | -0.39 | 0.61 | 71.29 | 30.27
2019-10-01 | 9:32 | 12.3711 | 12.3711 | -0.08 | 0.92 | -0.37 | 0.63 | -0.39 | 0.61 | 72.27 | 30.27
2019-10-01 | 9:32 | 12.4688 | 12.4688 | -0.08 | 0.92 | -0.37 | 0.63 | -0.38 | 0.62 | 72.27 | 31.25
2019-10-01 | 9:32 | 12.5703 | 12.5703 | -0.1 | 0.9 | -0.36 | 0.64 | -0.39 | 0.61 | 72.27 | 30.27
2019-10-01 | 9:32 | 12.668 | 12.668 | 0.02 | 1.02 | -0.45 | 0.55 | -0.41 | 0.59 | 71.29 | 30.27
2019-10-01 | 9:32 | 12.7812 | 12.7812 | 0.03 | 1.03 | -0.47 | 0.53 | -0.42 | 0.58 | 71.29 | 31.25
2019-10-01 | 9:32 | 12.8789 | 12.8789 | 0.02 | 1.02 | -0.47 | 0.53 | -0.43 | 0.57 | 73.24 | 30.27
2019-10-01 | 9:32 | 12.9805 | 12.9805 | 0.04 | 1.04 | -0.49 | 0.51 | -0.44 | 0.56 | 72.27 | 30.27
2019-10-01 | 9:32 | 13.0781 | 13.0781 | 0.04 | 1.04 | -0.49 | 0.51 | -0.44 | 0.56 | 72.27 | 31.25
2019-10-01 | 9:32 | 13.1875 | 13.1875 | 0.03 | 1.03 | -0.49 | 0.51 | -0.44 | 0.56 | 71.29 | 30.27
2019-10-01 | 9:32 | 13.2891 | 13.2891 | 0.02 | 1.02 | -0.49 | 0.51 | -0.43 | 0.57 | 72.27 | 31.25
2019-10-01 | 9:32 | 13.3906 | 13.3906 | 0.03 | 1.03 | -0.48 | 0.52 | -0.45 | 0.55 | 70.31 | 30.27
2019-10-01 | 9:32 | 13.4883 | 13.4883 | 0.03 | 1.03 | -0.5 | 0.5 | -0.46 | 0.54 | 71.29 | 30.27
2019-10-01 | 9:32 | 13.5977 | 13.5977 | 0.04 | 1.04 | -0.5 | 0.5 | -0.45 | 0.55 | 70.31 | 29.3
2019-10-01 | 9:32 | 13.6992 | 13.6992 | -0.04 | 0.96 | -0.44 | 0.56 | -0.44 | 0.56 | 70.31 | 29.3
2019-10-01 | 9:32 | 13.8086 | 13.8086 | -0.08 | 0.92 | -0.4 | 0.6 | -0.44 | 0.56 | 70.31 | 30.27
2019-10-01 | 9:32 | 13.9102 | 13.9102 | -0.11 | 0.89 | -0.39 | 0.61 | -0.42 | 0.58 | 70.31 | 30.27
2019-10-01 | 9:32 | 14.0078 | 14.0078 | -0.1 | 0.9 | -0.39 | 0.61 | -0.43 | 0.57 | 71.29 | 30.27
2019-10-01 | 9:32 | 14.1094 | 14.1094 | -0.04 | 0.96 | -0.44 | 0.56 | -0.44 | 0.56 | 70.31 | 29.3
2019-10-01 | 9:32 | 14.2109 | 14.2109 | 0.02 | 1.02 | -0.5 | 0.5 | -0.46 | 0.54 | 69.34 | 30.27
2019-10-01 | 9:32 | 14.3203 | 14.3203 | 0.03 | 1.03 | -0.51 | 0.49 | -0.47 | 0.53 | 70.31 | 29.3
2019-10-01 | 9:32 | 14.418 | 14.418 | 0.02 | 1.02 | -0.51 | 0.49 | -0.47 | 0.53 | 71.29 | 30.27
2019-10-01 | 9:32 | 14.5195 | 14.5195 | 0.02 | 1.02 | -0.52 | 0.48 | -0.48 | 0.52 | 70.31 | 30.27
2019-10-01 | 9:32 | 14.6211 | 14.6211 | 0.03 | 1.03 | -0.53 | 0.47 | -0.49 | 0.51 | 71.29 | 31.25
2019-10-01 | 9:32 | 14.7305 | 14.7305 | 0.04 | 1.04 | -0.54 | 0.46 | -0.49 | 0.51 | 70.31 | 30.27
2019-10-01 | 9:32 | 14.8281 | 14.8281 | 0.02 | 1.02 | -0.54 | 0.46 | -0.49 | 0.51 | 71.29 | 32.23
2019-10-01 | 9:32 | 14.9297 | 14.9297 | 0.03 | 1.03 | -0.55 | 0.45 | -0.49 | 0.51 | 71.29 | 30.27
2019-10-01 | 9:32 | 15.0391 | 15.0391 | 0.03 | 1.03 | -0.52 | 0.48 | -0.5 | 0.5 | 72.27 | 31.25
2019-10-01 | 9:32 | 15.1406 | 15.1406 | 0.03 | 1.03 | -0.54 | 0.46 | -0.5 | 0.5 | 70.31 | 29.3
2019-10-01 | 9:32 | 15.2383 | 15.2383 | -0.06 | 0.94 | -0.46 | 0.54 | -0.48 | 0.52 | 70.31 | 31.25
2019-10-01 | 9:32 | 15.3477 | 15.3477 | -0.1 | 0.9 | -0.43 | 0.57 | -0.48 | 0.52 | 70.31 | 30.27
2019-10-01 | 9:32 | 15.4492 | 15.4492 | -0.11 | 0.89 | -0.42 | 0.58 | -0.47 | 0.53 | 71.29 | 31.25
2019-10-01 | 9:32 | 15.5508 | 15.5508 | -0.12 | 0.88 | -0.4 | 0.6 | -0.47 | 0.53 | 70.31 | 30.27
2019-10-01 | 9:32 | 15.6484 | 15.6484 | 0 | 1 | -0.53 | 0.47 | -0.48 | 0.52 | 70.31 | 29.3
2019-10-01 | 9:32 | 15.75 | 15.75 | 0.01 | 1.01 | -0.54 | 0.46 | -0.49 | 0.51 | 70.31 | 29.3
2019-10-01 | 9:32 | 15.8594 | 15.8594 | 0.02 | 1.02 | -0.57 | 0.43 | -0.5 | 0.5 | 70.31 | 30.27
2019-10-01 | 9:32 | 15.9609 | 15.9609 | 0.02 | 1.02 | -0.56 | 0.44 | -0.52 | 0.48 | 69.34 | 29.3
2019-10-01 | 9:32 | 16.0586 | 16.0586 | 0.02 | 1.02 | -0.57 | 0.43 | -0.53 | 0.47 | 70.31 | 30.27
2019-10-01 | 9:32 | 16.1602 | 16.1602 | 0.03 | 1.03 | -0.56 | 0.44 | -0.52 | 0.48 | 70.31 | 30.27
2019-10-01 | 9:32 | 16.2695 | 16.2695 | 0.02 | 1.02 | -0.57 | 0.43 | -0.53 | 0.47 | 71.29 | 29.3
2019-10-01 | 9:32 | 16.3711 | 16.3711 | 0.02 | 1.02 | -0.57 | 0.43 | -0.53 | 0.47 | 70.31 | 30.27
2019-10-01 | 9:32 | 16.4805 | 16.4805 | 0.02 | 1.02 | -0.59 | 0.41 | -0.54 | 0.46 | 70.31 | 30.27
2019-10-01 | 9:32 | 16.5781 | 16.5781 | 0.01 | 1.01 | -0.59 | 0.41 | -0.53 | 0.47 | 70.31 | 30.27
2019-10-01 | 9:32 | 16.6797 | 16.6797 | 0 | 1 | -0.56 | 0.44 | -0.53 | 0.47 | 69.34 | 30.27
2019-10-01 | 9:32 | 16.7812 | 16.7812 | -0.09 | 0.91 | -0.46 | 0.54 | -0.5 | 0.5 | 70.31 | 31.25
2019-10-01 | 9:32 | 16.8906 | 16.8906 | -0.11 | 0.89 | -0.44 | 0.56 | -0.51 | 0.49 | 69.34 | 29.3
2019-10-01 | 9:32 | 16.9883 | 16.9883 | -0.12 | 0.88 | -0.44 | 0.56 | -0.52 | 0.48 | 70.31 | 29.3
2019-10-01 | 9:32 | 17.0898 | 17.0898 | -0.13 | 0.87 | -0.42 | 0.58 | -0.5 | 0.5 | 70.31 | 31.25
2019-10-01 | 9:32 | 17.1875 | 17.1875 | 0.02 | 1.02 | -0.56 | 0.44 | -0.53 | 0.47 | 71.29 | 32.23
2019-10-01 | 9:32 | 17.3008 | 17.3008 | 0.02 | 1.02 | -0.58 | 0.42 | -0.53 | 0.47 | 70.31 | 31.25
2019-10-01 | 9:32 | 17.3984 | 17.3984 | 0.01 | 1.01 | -0.59 | 0.41 | -0.53 | 0.47 | 70.31 | 30.27
2019-10-01 | 9:32 | 17.5 | 17.5 | 0.03 | 1.03 | -0.6 | 0.4 | -0.54 | 0.46 | 69.34 | 31.25
2019-10-01 | 9:32 | 17.6094 | 17.6094 | 0.02 | 1.02 | -0.59 | 0.41 | -0.55 | 0.45 | 70.31 | 29.3
2019-10-01 | 9:32 | 17.7109 | 17.7109 | 0.02 | 1.02 | -0.59 | 0.41 | -0.57 | 0.43 | 70.31 | 29.3
2019-10-01 | 9:32 | 17.8086 | 17.8086 | 0.03 | 1.03 | -0.6 | 0.4 | -0.55 | 0.45 | 70.31 | 29.3
2019-10-01 | 9:32 | 17.9102 | 17.9102 | 0.03 | 1.03 | -0.61 | 0.39 | -0.56 | 0.44 | 70.31 | 30.27
2019-10-01 | 9:32 | 18.0195 | 18.0195 | 0.04 | 1.04 | -0.61 | 0.39 | -0.57 | 0.43 | 69.34 | 30.27
2019-10-01 | 9:32 | 18.1211 | 18.1211 | 0.04 | 1.04 | -0.61 | 0.39 | -0.57 | 0.43 | 69.34 | 29.3
2019-10-01 | 9:32 | 18.2188 | 18.2188 | -0.05 | 0.95 | -0.53 | 0.47 | -0.56 | 0.44 | 71.29 | 30.27
2019-10-01 | 9:32 | 18.3281 | 18.3281 | -0.1 | 0.9 | -0.47 | 0.53 | -0.54 | 0.46 | 70.31 | 29.3
2019-10-01 | 9:32 | 18.4297 | 18.4297 | -0.13 | 0.87 | -0.46 | 0.54 | -0.52 | 0.48 | 71.29 | 29.3
2019-10-01 | 9:32 | 18.5312 | 18.5312 | -0.13 | 0.87 | -0.46 | 0.54 | -0.53 | 0.47 | 70.31 | 29.3
2019-10-01 | 9:32 | 18.6289 | 18.6289 | 0 | 1 | -0.57 | 0.43 | -0.53 | 0.47 | 69.34 | 29.3
2019-10-01 | 9:32 | 18.7383 | 18.7383 | 0.01 | 1.01 | -0.61 | 0.39 | -0.55 | 0.45 | 69.34 | 29.3
2019-10-01 | 9:32 | 18.8398 | 18.8398 | 0.01 | 1.01 | -0.61 | 0.39 | -0.55 | 0.45 | 69.34 | 30.27
2019-10-01 | 9:32 | 18.9375 | 18.9375 | 0.01 | 1.01 | -0.6 | 0.4 | -0.57 | 0.43 | 69.34 | 30.27
2019-10-01 | 9:32 | 19.0391 | 19.0391 | 0.03 | 1.03 | -0.6 | 0.4 | -0.56 | 0.44 | 69.34 | 30.27
2019-10-01 | 9:32 | 19.1484 | 19.1484 | 0.01 | 1.01 | -0.61 | 0.39 | -0.57 | 0.43 | 69.34 | 29.3
2019-10-01 | 9:32 | 19.25 | 19.25 | 0.02 | 1.02 | -0.62 | 0.38 | -0.57 | 0.43 | 69.34 | 30.27
2019-10-01 | 9:32 | 19.3477 | 19.3477 | 0.04 | 1.04 | -0.63 | 0.37 | -0.59 | 0.41 | 69.34 | 30.27
2019-10-01 | 9:32 | 19.4492 | 19.4492 | 0.02 | 1.02 | -0.62 | 0.38 | -0.6 | 0.4 | 69.34 | 30.27
2019-10-01 | 9:32 | 19.5586 | 19.5586 | 0.04 | 1.04 | -0.64 | 0.36 | -0.59 | 0.41 | 69.34 | 31.25
2019-10-01 | 9:32 | 19.6602 | 19.6602 | 0.03 | 1.03 | -0.63 | 0.37 | -0.59 | 0.41 | 69.34 | 30.27
2019-10-01 | 9:32 | 19.7578 | 19.7578 | -0.06 | 0.94 | -0.52 | 0.48 | -0.57 | 0.43 | 68.36 | 30.27
2019-10-01 | 9:32 | 19.8711 | 19.8711 | -0.12 | 0.88 | -0.48 | 0.52 | -0.57 | 0.43 | 68.36 | 29.3
2019-10-01 | 9:32 | 19.9688 | 19.9688 | -0.14 | 0.86 | -0.46 | 0.54 | -0.55 | 0.45 | 69.34 | 29.3
2019-10-01 | 9:32 | 20.0703 | 20.0703 | -0.15 | 0.85 | -0.47 | 0.53 | -0.53 | 0.47 | 70.31 | 29.3
2019-10-01 | 9:32 | 20.168 | 20.168 | 0.02 | 1.02 | -0.6 | 0.4 | -0.58 | 0.42 | 69.34 | 29.3
2019-10-01 | 9:32 | 20.2812 | 20.2812 | 0.02 | 1.02 | -0.62 | 0.38 | -0.58 | 0.42 | 70.31 | 30.27
2019-10-01 | 9:32 | 20.3789 | 20.3789 | 0.02 | 1.02 | -0.63 | 0.37 | -0.58 | 0.42 | 69.34 | 30.27
2019-10-01 | 9:32 | 20.4805 | 20.4805 | 0.03 | 1.03 | -0.64 | 0.36 | -0.59 | 0.41 | 69.34 | 30.27
2019-10-01 | 9:32 | 20.5781 | 20.5781 | 0.04 | 1.04 | -0.63 | 0.37 | -0.58 | 0.42 | 70.31 | 29.3
2019-10-01 | 9:32 | 20.6875 | 20.6875 | 0.02 | 1.02 | -0.63 | 0.37 | -0.59 | 0.41 | 68.36 | 29.3
2019-10-01 | 9:32 | 20.7891 | 20.7891 | 0.03 | 1.03 | -0.65 | 0.35 | -0.61 | 0.39 | 69.34 | 29.3
2019-10-01 | 9:32 | 20.8906 | 20.8906 | 0.02 | 1.02 | -0.65 | 0.35 | -0.6 | 0.4 | 69.34 | 29.3
2019-10-01 | 9:32 | 20.9883 | 20.9883 | 0.03 | 1.03 | -0.65 | 0.35 | -0.61 | 0.39 | 68.36 | 29.3
2019-10-01 | 9:32 | 21.0977 | 21.0977 | 0.03 | 1.03 | -0.66 | 0.34 | -0.62 | 0.38 | 69.34 | 30.27
2019-10-01 | 9:32 | 21.1992 | 21.1992 | 0 | 1 | -0.62 | 0.38 | -0.61 | 0.39 | 69.34 | 29.3
2019-10-01 | 9:32 | 21.3086 | 21.3086 | -0.08 | 0.92 | -0.53 | 0.47 | -0.59 | 0.41 | 68.36 | 30.27
2019-10-01 | 9:32 | 21.4102 | 21.4102 | -0.14 | 0.86 | -0.5 | 0.5 | -0.59 | 0.41 | 69.34 | 30.27
2019-10-01 | 9:32 | 21.5078 | 21.5078 | -0.14 | 0.86 | -0.47 | 0.53 | -0.56 | 0.44 | 68.36 | 29.3
2019-10-01 | 9:32 | 21.6094 | 21.6094 | -0.08 | 0.92 | -0.52 | 0.48 | -0.56 | 0.44 | 69.34 | 29.3
2019-10-01 | 9:32 | 21.7188 | 21.7188 | 0 | 1 | -0.62 | 0.38 | -0.59 | 0.41 | 68.36 | 29.3
2019-10-01 | 9:32 | 21.8203 | 21.8203 | 0.01 | 1.01 | -0.63 | 0.37 | -0.6 | 0.4 | 69.34 | 30.27
2019-10-01 | 9:32 | 21.918 | 21.918 | 0.03 | 1.03 | -0.65 | 0.35 | -0.61 | 0.39 | 69.34 | 29.3
2019-10-01 | 9:32 | 22.0195 | 22.0195 | 0.03 | 1.03 | -0.66 | 0.34 | -0.6 | 0.4 | 68.36 | 29.3
2019-10-01 | 9:32 | 22.1211 | 22.1211 | 0.03 | 1.03 | -0.67 | 0.33 | -0.62 | 0.38 | 68.36 | 30.27
2019-10-01 | 9:32 | 22.2305 | 22.2305 | 0.03 | 1.03 | -0.66 | 0.34 | -0.62 | 0.38 | 68.36 | 29.3
2019-10-01 | 9:32 | 22.3281 | 22.3281 | 0.04 | 1.04 | -0.67 | 0.33 | -0.63 | 0.37 | 68.36 | 30.27
2019-10-01 | 9:32 | 22.4375 | 22.4375 | 0.02 | 1.02 | -0.66 | 0.34 | -0.62 | 0.38 | 68.36 | 29.3
2019-10-01 | 9:32 | 22.5391 | 22.5391 | 0.03 | 1.03 | -0.67 | 0.33 | -0.63 | 0.37 | 68.36 | 30.27
2019-10-01 | 9:32 | 22.6406 | 22.6406 | 0.02 | 1.02 | -0.67 | 0.33 | -0.63 | 0.37 | 68.36 | 29.3
2019-10-01 | 9:32 | 22.7383 | 22.7383 | -0.05 | 0.95 | -0.58 | 0.42 | -0.61 | 0.39 | 68.36 | 29.3
2019-10-01 | 9:32 | 22.8477 | 22.8477 | -0.12 | 0.88 | -0.52 | 0.48 | -0.6 | 0.4 | 68.36 | 28.32
2019-10-01 | 9:32 | 22.9492 | 22.9492 | -0.14 | 0.86 | -0.51 | 0.49 | -0.58 | 0.42 | 68.36 | 29.3
2019-10-01 | 9:32 | 23.0508 | 23.0508 | -0.15 | 0.85 | -0.5 | 0.5 | -0.6 | 0.4 | 69.34 | 30.27
2019-10-01 | 9:32 | 23.1484 | 23.1484 | 0.01 | 1.01 | -0.64 | 0.36 | -0.58 | 0.42 | 69.34 | 30.27
2019-10-01 | 9:32 | 23.2578 | 23.2578 | 0.01 | 1.01 | -0.65 | 0.35 | -0.62 | 0.38 | 68.36 | 29.3
2019-10-01 | 9:32 | 23.3594 | 23.3594 | 0.02 | 1.02 | -0.66 | 0.34 | -0.61 | 0.39 | 70.31 | 30.27
2019-10-01 | 9:32 | 23.4609 | 23.4609 | 0.03 | 1.03 | -0.67 | 0.33 | -0.63 | 0.37 | 68.36 | 29.3
2019-10-01 | 9:32 | 23.5703 | 23.5703 | 0.03 | 1.03 | -0.67 | 0.33 | -0.62 | 0.38 | 68.36 | 29.3
2019-10-01 | 9:32 | 23.668 | 23.668 | 0.03 | 1.03 | -0.66 | 0.34 | -0.63 | 0.37 | 68.36 | 28.32
2019-10-01 | 9:32 | 23.7695 | 23.7695 | 0.03 | 1.03 | -0.68 | 0.32 | -0.64 | 0.36 | 67.38 | 29.3
2019-10-01 | 9:32 | 23.8711 | 23.8711 | 0.03 | 1.03 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 29.3
2019-10-01 | 9:32 | 23.9805 | 23.9805 | 0.02 | 1.02 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 28.32
2019-10-01 | 9:32 | 24.0781 | 24.0781 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 67.38 | 28.32
2019-10-01 | 9:32 | 24.1797 | 24.1797 | 0.03 | 1.03 | -0.69 | 0.31 | -0.64 | 0.36 | 69.34 | 29.3
2019-10-01 | 9:32 | 24.2812 | 24.2812 | -0.05 | 0.95 | -0.6 | 0.4 | -0.64 | 0.36 | 67.38 | 28.32
2019-10-01 | 9:32 | 24.3906 | 24.3906 | -0.11 | 0.89 | -0.55 | 0.45 | -0.61 | 0.39 | 67.38 | 28.32
2019-10-01 | 9:32 | 24.4883 | 24.4883 | -0.14 | 0.86 | -0.53 | 0.47 | -0.61 | 0.39 | 67.38 | 28.32
2019-10-01 | 9:32 | 24.5898 | 24.5898 | -0.16 | 0.84 | -0.51 | 0.49 | -0.6 | 0.4 | 67.38 | 30.27
2019-10-01 | 9:32 | 24.6992 | 24.6992 | 0.01 | 1.01 | -0.66 | 0.34 | -0.62 | 0.38 | 67.38 | 30.27
2019-10-01 | 9:32 | 24.8008 | 24.8008 | 0.02 | 1.02 | -0.68 | 0.32 | -0.62 | 0.38 | 67.38 | 30.27
2019-10-01 | 9:32 | 24.8984 | 24.8984 | 0 | 1 | -0.68 | 0.32 | -0.63 | 0.37 | 67.38 | 29.3
2019-10-01 | 9:32 | 25 | 25 | 0.02 | 1.02 | -0.68 | 0.32 | -0.63 | 0.37 | 67.38 | 29.3
2019-10-01 | 9:32 | 25.1094 | 25.1094 | 0.01 | 1.01 | -0.68 | 0.32 | -0.62 | 0.38 | 67.38 | 29.3
2019-10-01 | 9:32 | 25.2109 | 25.2109 | 0.02 | 1.02 | -0.68 | 0.32 | -0.64 | 0.36 | 66.41 | 28.32
2019-10-01 | 9:32 | 25.3086 | 25.3086 | 0.03 | 1.03 | -0.7 | 0.3 | -0.66 | 0.34 | 68.36 | 29.3
2019-10-01 | 9:32 | 25.4102 | 25.4102 | 0.03 | 1.03 | -0.7 | 0.3 | -0.65 | 0.35 | 68.36 | 30.27
2019-10-01 | 9:32 | 25.5195 | 25.5195 | 0.03 | 1.03 | -0.71 | 0.29 | -0.65 | 0.35 | 67.38 | 29.3
2019-10-01 | 9:32 | 25.6211 | 25.6211 | 0.02 | 1.02 | -0.71 | 0.29 | -0.65 | 0.35 | 66.41 | 28.32
2019-10-01 | 9:32 | 25.7188 | 25.7188 | 0.01 | 1.01 | -0.68 | 0.32 | -0.65 | 0.35 | 67.38 | 28.32
2019-10-01 | 9:32 | 25.8281 | 25.8281 | -0.1 | 0.9 | -0.56 | 0.44 | -0.64 | 0.36 | 67.38 | 28.32
2019-10-01 | 9:32 | 25.9297 | 25.9297 | -0.14 | 0.86 | -0.54 | 0.46 | -0.62 | 0.38 | 67.38 | 29.3
2019-10-01 | 9:32 | 26.0312 | 26.0312 | -0.15 | 0.85 | -0.52 | 0.48 | -0.63 | 0.37 | 67.38 | 29.3
2019-10-01 | 9:32 | 26.1289 | 26.1289 | -0.01 | 0.99 | -0.64 | 0.36 | -0.63 | 0.37 | 68.36 | 29.3
2019-10-01 | 9:32 | 26.2383 | 26.2383 | 0.01 | 1.01 | -0.69 | 0.31 | -0.64 | 0.36 | 67.38 | 28.32
2019-10-01 | 9:32 | 26.3398 | 26.3398 | 0.02 | 1.02 | -0.7 | 0.3 | -0.65 | 0.35 | 68.36 | 29.3
2019-10-01 | 9:32 | 26.4375 | 26.4375 | 0.02 | 1.02 | -0.69 | 0.31 | -0.64 | 0.36 | 67.38 | 29.3
2019-10-01 | 9:32 | 26.5391 | 26.5391 | 0.01 | 1.01 | -0.7 | 0.3 | -0.65 | 0.35 | 67.38 | 29.3
2019-10-01 | 9:32 | 26.6484 | 26.6484 | 0.03 | 1.03 | -0.7 | 0.3 | -0.65 | 0.35 | 67.38 | 30.27
2019-10-01 | 9:32 | 26.75 | 26.75 | 0.02 | 1.02 | -0.71 | 0.29 | -0.65 | 0.35 | 68.36 | 31.25
2019-10-01 | 9:32 | 26.8477 | 26.8477 | 0.01 | 1.01 | -0.71 | 0.29 | -0.67 | 0.33 | 67.38 | 29.3
2019-10-01 | 9:32 | 26.9492 | 26.9492 | 0.01 | 1.01 | -0.71 | 0.29 | -0.66 | 0.34 | 66.41 | 28.32
2019-10-01 | 9:32 | 27.0586 | 27.0586 | 0.02 | 1.02 | -0.7 | 0.3 | -0.67 | 0.33 | 68.36 | 28.32
2019-10-01 | 9:32 | 27.1602 | 27.1602 | 0.03 | 1.03 | -0.73 | 0.27 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 27.2578 | 27.2578 | -0.03 | 0.97 | -0.66 | 0.34 | -0.65 | 0.35 | 66.41 | 29.3
2019-10-01 | 9:32 | 27.3711 | 27.3711 | -0.11 | 0.89 | -0.57 | 0.43 | -0.65 | 0.35 | 67.38 | 29.3
2019-10-01 | 9:32 | 27.4688 | 27.4688 | -0.15 | 0.85 | -0.54 | 0.46 | -0.63 | 0.37 | 66.41 | 28.32
2019-10-01 | 9:32 | 27.5703 | 27.5703 | -0.15 | 0.85 | -0.52 | 0.48 | -0.62 | 0.38 | 68.36 | 28.32
2019-10-01 | 9:32 | 27.6797 | 27.6797 | 0 | 1 | -0.69 | 0.31 | -0.63 | 0.37 | 68.36 | 28.32
2019-10-01 | 9:32 | 27.7812 | 27.7812 | 0.01 | 1.01 | -0.69 | 0.31 | -0.65 | 0.35 | 66.41 | 28.32
2019-10-01 | 9:32 | 27.8789 | 27.8789 | 0.03 | 1.03 | -0.7 | 0.3 | -0.65 | 0.35 | 66.41 | 28.32
2019-10-01 | 9:32 | 27.9805 | 27.9805 | 0.03 | 1.03 | -0.71 | 0.29 | -0.65 | 0.35 | 66.41 | 28.32
2019-10-01 | 9:32 | 28.0781 | 28.0781 | 0.02 | 1.02 | -0.71 | 0.29 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 28.1875 | 28.1875 | 0.02 | 1.02 | -0.72 | 0.28 | -0.66 | 0.34 | 66.41 | 27.34
2019-10-01 | 9:32 | 28.2891 | 28.2891 | 0.03 | 1.03 | -0.71 | 0.29 | -0.67 | 0.33 | 67.38 | 28.32
2019-10-01 | 9:32 | 28.3984 | 28.3984 | 0.03 | 1.03 | -0.72 | 0.28 | -0.68 | 0.32 | 67.38 | 28.32
2019-10-01 | 9:32 | 28.5 | 28.5 | 0.04 | 1.04 | -0.73 | 0.27 | -0.68 | 0.32 | 66.41 | 28.32
2019-10-01 | 9:32 | 28.5977 | 28.5977 | 0.03 | 1.03 | -0.72 | 0.28 | -0.67 | 0.33 | 66.41 | 29.3
2019-10-01 | 9:32 | 28.6992 | 28.6992 | 0.02 | 1.02 | -0.72 | 0.28 | -0.67 | 0.33 | 66.41 | 28.32
2019-10-01 | 9:32 | 28.8086 | 28.8086 | -0.07 | 0.93 | -0.63 | 0.37 | -0.66 | 0.34 | 67.38 | 29.3
2019-10-01 | 9:32 | 28.9102 | 28.9102 | -0.14 | 0.86 | -0.55 | 0.45 | -0.65 | 0.35 | 66.41 | 28.32
2019-10-01 | 9:32 | 29.0078 | 29.0078 | -0.14 | 0.86 | -0.56 | 0.44 | -0.63 | 0.37 | 67.38 | 29.3
2019-10-01 | 9:32 | 29.1094 | 29.1094 | -0.12 | 0.88 | -0.58 | 0.42 | -0.62 | 0.38 | 67.38 | 27.34
2019-10-01 | 9:32 | 29.2188 | 29.2188 | 0.01 | 1.01 | -0.73 | 0.27 | -0.65 | 0.35 | 67.38 | 28.32
2019-10-01 | 9:32 | 29.3203 | 29.3203 | 0.01 | 1.01 | -0.72 | 0.28 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 29.418 | 29.418 | 0.01 | 1.01 | -0.72 | 0.28 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 29.5312 | 29.5312 | 0.02 | 1.02 | -0.72 | 0.28 | -0.66 | 0.34 | 67.38 | 25.39
2019-10-01 | 9:32 | 29.6289 | 29.6289 | 0.02 | 1.02 | -0.73 | 0.27 | -0.65 | 0.35 | 67.38 | 28.32
2019-10-01 | 9:32 | 29.7305 | 29.7305 | 0.01 | 1.01 | -0.73 | 0.27 | -0.67 | 0.33 | 66.41 | 27.34
2019-10-01 | 9:32 | 29.8281 | 29.8281 | 0.02 | 1.02 | -0.72 | 0.28 | -0.66 | 0.34 | 66.41 | 27.34
2019-10-01 | 9:32 | 29.9375 | 29.9375 | 0.02 | 1.02 | -0.72 | 0.28 | -0.68 | 0.32 | 66.41 | 28.32
2019-10-01 | 9:32 | 30.0391 | 30.0391 | 0.02 | 1.02 | -0.74 | 0.26 | -0.68 | 0.32 | 67.38 | 29.3
2019-10-01 | 9:32 | 30.1406 | 30.1406 | 0.02 | 1.02 | -0.74 | 0.26 | -0.67 | 0.33 | 66.41 | 29.3
2019-10-01 | 9:32 | 30.2383 | 30.2383 | 0.01 | 1.01 | -0.71 | 0.29 | -0.67 | 0.33 | 67.38 | 29.3
2019-10-01 | 9:32 | 30.3477 | 30.3477 | -0.12 | 0.88 | -0.59 | 0.41 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 30.4492 | 30.4492 | -0.14 | 0.86 | -0.57 | 0.43 | -0.63 | 0.37 | 66.41 | 29.3
2019-10-01 | 9:32 | 30.5508 | 30.5508 | -0.17 | 0.83 | -0.55 | 0.45 | -0.64 | 0.36 | 66.41 | 28.32
2019-10-01 | 9:32 | 30.6602 | 30.6602 | 0 | 1 | -0.7 | 0.3 | -0.63 | 0.37 | 66.41 | 27.34
2019-10-01 | 9:32 | 30.7578 | 30.7578 | 0.02 | 1.02 | -0.72 | 0.28 | -0.66 | 0.34 | 68.36 | 28.32
2019-10-01 | 9:32 | 30.8594 | 30.8594 | 0.03 | 1.03 | -0.72 | 0.28 | -0.66 | 0.34 | 68.36 | 28.32
2019-10-01 | 9:32 | 30.9609 | 30.9609 | 0.04 | 1.04 | -0.75 | 0.25 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 31.0703 | 31.0703 | 0.01 | 1.01 | -0.73 | 0.27 | -0.67 | 0.33 | 66.41 | 28.32
2019-10-01 | 9:32 | 31.168 | 31.168 | 0.01 | 1.01 | -0.73 | 0.27 | -0.67 | 0.33 | 67.38 | 28.32
2019-10-01 | 9:32 | 31.2695 | 31.2695 | 0.02 | 1.02 | -0.73 | 0.27 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 31.3711 | 31.3711 | 0.02 | 1.02 | -0.73 | 0.27 | -0.67 | 0.33 | 68.36 | 29.3
2019-10-01 | 9:32 | 31.4805 | 31.4805 | 0.03 | 1.03 | -0.74 | 0.26 | -0.67 | 0.33 | 68.36 | 28.32
2019-10-01 | 9:32 | 31.5781 | 31.5781 | 0.03 | 1.03 | -0.75 | 0.25 | -0.67 | 0.33 | 67.38 | 28.32
2019-10-01 | 9:32 | 31.6797 | 31.6797 | 0.03 | 1.03 | -0.73 | 0.27 | -0.69 | 0.31 | 67.38 | 28.32
2019-10-01 | 9:32 | 31.7891 | 31.7891 | -0.05 | 0.95 | -0.65 | 0.35 | -0.67 | 0.33 | 67.38 | 29.3
2019-10-01 | 9:32 | 31.8906 | 31.8906 | -0.11 | 0.89 | -0.59 | 0.41 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 31.9883 | 31.9883 | -0.16 | 0.84 | -0.56 | 0.44 | -0.65 | 0.35 | 67.38 | 28.32
2019-10-01 | 9:32 | 32.0898 | 32.0898 | -0.18 | 0.82 | -0.57 | 0.43 | -0.64 | 0.36 | 67.38 | 28.32
2019-10-01 | 9:32 | 32.1992 | 32.1992 | 0.01 | 1.01 | -0.74 | 0.26 | -0.64 | 0.36 | 68.36 | 28.32
2019-10-01 | 9:32 | 32.3008 | 32.3008 | 0 | 1 | -0.74 | 0.26 | -0.65 | 0.35 | 68.36 | 28.32
2019-10-01 | 9:32 | 32.3984 | 32.3984 | 0 | 1 | -0.73 | 0.27 | -0.64 | 0.36 | 69.34 | 27.34
2019-10-01 | 9:32 | 32.5 | 32.5 | 0.02 | 1.02 | -0.74 | 0.26 | -0.66 | 0.34 | 69.34 | 29.3
2019-10-01 | 9:32 | 32.6094 | 32.6094 | 0.01 | 1.01 | -0.74 | 0.26 | -0.66 | 0.34 | 67.38 | 28.32
2019-10-01 | 9:32 | 32.7109 | 32.7109 | 0.01 | 1.01 | -0.74 | 0.26 | -0.67 | 0.33 | 67.38 | 28.32
2019-10-01 | 9:32 | 32.8086 | 32.8086 | 0.02 | 1.02 | -0.74 | 0.26 | -0.66 | 0.34 | 68.36 | 28.32
2019-10-01 | 9:32 | 32.9102 | 32.9102 | 0.01 | 1.01 | -0.75 | 0.25 | -0.68 | 0.32 | 69.34 | 29.3
2019-10-01 | 9:32 | 33.0195 | 33.0195 | 0.03 | 1.03 | -0.74 | 0.26 | -0.68 | 0.32 | 68.36 | 27.34
2019-10-01 | 9:32 | 33.1211 | 33.1211 | 0.03 | 1.03 | -0.74 | 0.26 | -0.67 | 0.33 | 68.36 | 28.32
2019-10-01 | 9:32 | 33.2305 | 33.2305 | 0.02 | 1.02 | -0.74 | 0.26 | -0.69 | 0.31 | 68.36 | 28.32
2019-10-01 | 9:32 | 33.3281 | 33.3281 | -0.06 | 0.94 | -0.65 | 0.35 | -0.66 | 0.34 | 69.34 | 29.3
2019-10-01 | 9:32 | 33.4297 | 33.4297 | -0.13 | 0.87 | -0.6 | 0.4 | -0.65 | 0.35 | 68.36 | 28.32
2019-10-01 | 9:32 | 33.5312 | 33.5312 | -0.16 | 0.84 | -0.6 | 0.4 | -0.63 | 0.37 | 69.34 | 28.32
2019-10-01 | 9:32 | 33.6289 | 33.6289 | -0.03 | 0.97 | -0.71 | 0.29 | -0.65 | 0.35 | 68.36 | 27.34
2019-10-01 | 9:32 | 33.7383 | 33.7383 | 0 | 1 | -0.76 | 0.24 | -0.65 | 0.35 | 68.36 | 29.3
2019-10-01 | 9:32 | 33.8398 | 33.8398 | 0.01 | 1.01 | -0.77 | 0.23 | -0.66 | 0.34 | 69.34 | 28.32
2019-10-01 | 9:32 | 33.9375 | 33.9375 | 0.03 | 1.03 | -0.76 | 0.24 | -0.66 | 0.34 | 68.36 | 26.37
2019-10-01 | 9:32 | 34.0391 | 34.0391 | 0.02 | 1.02 | -0.76 | 0.24 | -0.67 | 0.33 | 69.34 | 27.34
2019-10-01 | 9:32 | 34.1484 | 34.1484 | 0.02 | 1.02 | -0.76 | 0.24 | -0.65 | 0.35 | 69.34 | 27.34
2019-10-01 | 9:32 | 34.25 | 34.25 | 0.02 | 1.02 | -0.75 | 0.25 | -0.66 | 0.34 | 70.31 | 27.34
2019-10-01 | 9:32 | 34.3594 | 34.3594 | 0.04 | 1.04 | -0.75 | 0.25 | -0.67 | 0.33 | 70.31 | 29.3
2019-10-01 | 9:32 | 34.4609 | 34.4609 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 69.34 | 25.39
2019-10-01 | 9:32 | 34.5586 | 34.5586 | 0.02 | 1.02 | -0.76 | 0.24 | -0.68 | 0.32 | 69.34 | 29.3
2019-10-01 | 9:32 | 34.6602 | 34.6602 | 0.02 | 1.02 | -0.75 | 0.25 | -0.68 | 0.32 | 69.34 | 28.32
2019-10-01 | 9:32 | 34.7578 | 34.7578 | -0.01 | 0.99 | -0.71 | 0.29 | -0.67 | 0.33 | 69.34 | 28.32
2019-10-01 | 9:32 | 34.8711 | 34.8711 | -0.12 | 0.88 | -0.62 | 0.38 | -0.65 | 0.35 | 70.31 | 27.34
2019-10-01 | 9:32 | 34.9688 | 34.9688 | -0.16 | 0.84 | -0.6 | 0.4 | -0.65 | 0.35 | 69.34 | 27.34
2019-10-01 | 9:32 | 35.0703 | 35.0703 | -0.16 | 0.84 | -0.6 | 0.4 | -0.63 | 0.37 | 70.31 | 28.32
2019-10-01 | 9:32 | 35.1797 | 35.1797 | -0.02 | 0.98 | -0.74 | 0.26 | -0.63 | 0.37 | 70.31 | 27.34
2019-10-01 | 9:32 | 35.2812 | 35.2812 | 0 | 1 | -0.75 | 0.25 | -0.64 | 0.36 | 71.29 | 28.32
2019-10-01 | 9:32 | 35.3789 | 35.3789 | 0.01 | 1.01 | -0.74 | 0.26 | -0.65 | 0.35 | 70.31 | 27.34
2019-10-01 | 9:32 | 35.4883 | 35.4883 | 0.01 | 1.01 | -0.76 | 0.24 | -0.65 | 0.35 | 70.31 | 27.34
2019-10-01 | 9:32 | 35.5898 | 35.5898 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 71.29 | 28.32
2019-10-01 | 9:32 | 35.6875 | 35.6875 | 0.02 | 1.02 | -0.76 | 0.24 | -0.66 | 0.34 | 70.31 | 28.32
2019-10-01 | 9:32 | 35.7891 | 35.7891 | 0.03 | 1.03 | -0.75 | 0.25 | -0.66 | 0.34 | 70.31 | 28.32
2019-10-01 | 9:32 | 35.8984 | 35.8984 | 0.03 | 1.03 | -0.76 | 0.24 | -0.67 | 0.33 | 70.31 | 27.34
2019-10-01 | 9:32 | 36 | 36 | 0.03 | 1.03 | -0.76 | 0.24 | -0.66 | 0.34 | 70.31 | 28.32
2019-10-01 | 9:32 | 36.0977 | 36.0977 | 0.03 | 1.03 | -0.76 | 0.24 | -0.67 | 0.33 | 70.31 | 28.32
2019-10-01 | 9:32 | 36.1992 | 36.1992 | 0.02 | 1.02 | -0.76 | 0.24 | -0.69 | 0.31 | 71.29 | 28.32
2019-10-01 | 9:32 | 36.3086 | 36.3086 | -0.07 | 0.93 | -0.67 | 0.33 | -0.67 | 0.33 | 71.29 | 29.3
2019-10-01 | 9:32 | 36.4102 | 36.4102 | -0.15 | 0.85 | -0.61 | 0.39 | -0.64 | 0.36 | 70.31 | 27.34
2019-10-01 | 9:32 | 36.5078 | 36.5078 | -0.17 | 0.83 | -0.62 | 0.38 | -0.64 | 0.36 | 70.31 | 28.32
2019-10-01 | 9:32 | 36.6211 | 36.6211 | -0.16 | 0.84 | -0.62 | 0.38 | -0.64 | 0.36 | 70.31 | 27.34
2019-10-01 | 9:32 | 36.7188 | 36.7188 | 0 | 1 | -0.78 | 0.22 | -0.66 | 0.34 | 70.31 | 28.32
2019-10-01 | 9:32 | 36.8203 | 36.8203 | 0.01 | 1.01 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 36.918 | 36.918 | 0.02 | 1.02 | -0.77 | 0.23 | -0.64 | 0.36 | 71.29 | 28.32
2019-10-01 | 9:32 | 37.0312 | 37.0312 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 71.29 | 27.34
2019-10-01 | 9:32 | 37.1289 | 37.1289 | 0.03 | 1.03 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 29.3
2019-10-01 | 9:32 | 37.2305 | 37.2305 | 0.02 | 1.02 | -0.78 | 0.22 | -0.65 | 0.35 | 70.31 | 27.34
2019-10-01 | 9:32 | 37.3281 | 37.3281 | 0.01 | 1.01 | -0.77 | 0.23 | -0.66 | 0.34 | 71.29 | 28.32
2019-10-01 | 9:32 | 37.4375 | 37.4375 | 0.02 | 1.02 | -0.76 | 0.24 | -0.65 | 0.35 | 70.31 | 28.32
2019-10-01 | 9:32 | 37.5391 | 37.5391 | 0.02 | 1.02 | -0.78 | 0.22 | -0.67 | 0.33 | 70.31 | 27.34
2019-10-01 | 9:32 | 37.6406 | 37.6406 | 0.02 | 1.02 | -0.77 | 0.23 | -0.66 | 0.34 | 70.31 | 28.32
2019-10-01 | 9:32 | 37.75 | 37.75 | -0.01 | 0.99 | -0.73 | 0.27 | -0.66 | 0.34 | 70.31 | 27.34
2019-10-01 | 9:32 | 37.8477 | 37.8477 | -0.13 | 0.87 | -0.63 | 0.37 | -0.64 | 0.36 | 71.29 | 28.32
2019-10-01 | 9:32 | 37.9492 | 37.9492 | -0.15 | 0.85 | -0.62 | 0.38 | -0.63 | 0.37 | 71.29 | 27.34
2019-10-01 | 9:32 | 38.0508 | 38.0508 | -0.16 | 0.84 | -0.63 | 0.37 | -0.63 | 0.37 | 72.27 | 29.3
2019-10-01 | 9:32 | 38.1602 | 38.1602 | -0.02 | 0.98 | -0.75 | 0.25 | -0.63 | 0.37 | 72.27 | 29.3
2019-10-01 | 9:32 | 38.2578 | 38.2578 | 0.02 | 1.02 | -0.78 | 0.22 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:32 | 38.3594 | 38.3594 | 0.01 | 1.01 | -0.77 | 0.23 | -0.65 | 0.35 | 70.31 | 27.34
2019-10-01 | 9:32 | 38.4609 | 38.4609 | 0.01 | 1.01 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 29.3
2019-10-01 | 9:32 | 38.5703 | 38.5703 | 0.01 | 1.01 | -0.78 | 0.22 | -0.65 | 0.35 | 71.29 | 28.32
2019-10-01 | 9:32 | 38.668 | 38.668 | 0.01 | 1.01 | -0.79 | 0.21 | -0.65 | 0.35 | 70.31 | 27.34
2019-10-01 | 9:32 | 38.7695 | 38.7695 | 0.02 | 1.02 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 27.34
2019-10-01 | 9:32 | 38.8711 | 38.8711 | 0.01 | 1.01 | -0.77 | 0.23 | -0.67 | 0.33 | 70.31 | 27.34
2019-10-01 | 9:32 | 38.9805 | 38.9805 | 0.02 | 1.02 | -0.77 | 0.23 | -0.67 | 0.33 | 71.29 | 28.32
2019-10-01 | 9:32 | 39.0781 | 39.0781 | 0.02 | 1.02 | -0.78 | 0.22 | -0.67 | 0.33 | 71.29 | 28.32
2019-10-01 | 9:32 | 39.1875 | 39.1875 | 0.03 | 1.03 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 27.34
2019-10-01 | 9:32 | 39.2891 | 39.2891 | -0.07 | 0.93 | -0.69 | 0.31 | -0.65 | 0.35 | 71.29 | 28.32
2019-10-01 | 9:32 | 39.3906 | 39.3906 | -0.15 | 0.85 | -0.62 | 0.38 | -0.64 | 0.36 | 71.29 | 27.34
2019-10-01 | 9:32 | 39.4883 | 39.4883 | -0.16 | 0.84 | -0.62 | 0.38 | -0.64 | 0.36 | 72.27 | 29.3
2019-10-01 | 9:32 | 39.5898 | 39.5898 | -0.15 | 0.85 | -0.63 | 0.37 | -0.63 | 0.37 | 72.27 | 28.32
2019-10-01 | 9:32 | 39.6992 | 39.6992 | -0.01 | 0.99 | -0.76 | 0.24 | -0.64 | 0.36 | 71.29 | 28.32
2019-10-01 | 9:32 | 39.8008 | 39.8008 | 0 | 1 | -0.79 | 0.21 | -0.64 | 0.36 | 71.29 | 27.34
2019-10-01 | 9:32 | 39.8984 | 39.8984 | 0 | 1 | -0.78 | 0.22 | -0.64 | 0.36 | 72.27 | 28.32
2019-10-01 | 9:32 | 40 | 40 | 0.02 | 1.02 | -0.78 | 0.22 | -0.65 | 0.35 | 71.29 | 28.32
2019-10-01 | 9:32 | 40.1094 | 40.1094 | 0.03 | 1.03 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 28.32
2019-10-01 | 9:32 | 40.2109 | 40.2109 | 0.02 | 1.02 | -0.79 | 0.21 | -0.65 | 0.35 | 71.29 | 28.32
2019-10-01 | 9:32 | 40.3203 | 40.3203 | 0.02 | 1.02 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 29.3
2019-10-01 | 9:32 | 40.418 | 40.418 | 0.03 | 1.03 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 28.32
2019-10-01 | 9:32 | 40.5195 | 40.5195 | 0.01 | 1.01 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 28.32
2019-10-01 | 9:32 | 40.6211 | 40.6211 | 0.03 | 1.03 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 27.34
2019-10-01 | 9:32 | 40.7305 | 40.7305 | 0.01 | 1.01 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 29.3
2019-10-01 | 9:32 | 40.8281 | 40.8281 | -0.12 | 0.88 | -0.66 | 0.34 | -0.64 | 0.36 | 71.29 | 27.34
2019-10-01 | 9:32 | 40.9297 | 40.9297 | -0.15 | 0.85 | -0.64 | 0.36 | -0.63 | 0.37 | 72.27 | 28.32
2019-10-01 | 9:32 | 41.0312 | 41.0312 | -0.17 | 0.83 | -0.62 | 0.38 | -0.63 | 0.37 | 72.27 | 29.3
2019-10-01 | 9:32 | 41.1406 | 41.1406 | -0.03 | 0.97 | -0.73 | 0.27 | -0.63 | 0.37 | 71.29 | 28.32
2019-10-01 | 9:32 | 41.2383 | 41.2383 | -0.01 | 0.99 | -0.78 | 0.22 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:32 | 41.3398 | 41.3398 | 0.02 | 1.02 | -0.78 | 0.22 | -0.65 | 0.35 | 71.29 | 27.34
2019-10-01 | 9:32 | 41.4492 | 41.4492 | 0.01 | 1.01 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 28.32
2019-10-01 | 9:32 | 41.5508 | 41.5508 | 0.02 | 1.02 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 28.32
2019-10-01 | 9:32 | 41.6484 | 41.6484 | 0.01 | 1.01 | -0.78 | 0.22 | -0.67 | 0.33 | 71.29 | 28.32
2019-10-01 | 9:32 | 41.75 | 41.75 | 0.02 | 1.02 | -0.79 | 0.21 | -0.65 | 0.35 | 71.29 | 27.34
2019-10-01 | 9:32 | 41.8594 | 41.8594 | 0.03 | 1.03 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 28.32
2019-10-01 | 9:32 | 41.9609 | 41.9609 | 0.01 | 1.01 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 28.32
2019-10-01 | 9:32 | 42.0586 | 42.0586 | 0.02 | 1.02 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 28.32
2019-10-01 | 9:32 | 42.1602 | 42.1602 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 28.32
2019-10-01 | 9:32 | 42.2695 | 42.2695 | -0.02 | 0.98 | -0.74 | 0.26 | -0.65 | 0.35 | 71.29 | 28.32
2019-10-01 | 9:32 | 42.3711 | 42.3711 | -0.13 | 0.87 | -0.64 | 0.36 | -0.66 | 0.34 | 71.29 | 28.32
2019-10-01 | 9:32 | 42.4688 | 42.4688 | -0.16 | 0.84 | -0.61 | 0.39 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:32 | 42.5781 | 42.5781 | -0.17 | 0.83 | -0.61 | 0.39 | -0.64 | 0.36 | 71.29 | 28.32
2019-10-01 | 9:32 | 42.6797 | 42.6797 | 0 | 1 | -0.76 | 0.24 | -0.64 | 0.36 | 71.29 | 27.34
2019-10-01 | 9:32 | 42.7812 | 42.7812 | 0.01 | 1.01 | -0.79 | 0.21 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:32 | 42.8789 | 42.8789 | 0 | 1 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 42.9883 | 42.9883 | 0.01 | 1.01 | -0.78 | 0.22 | -0.64 | 0.36 | 74.22 | 28.32
2019-10-01 | 9:32 | 43.0898 | 43.0898 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 72.27 | 28.32
2019-10-01 | 9:32 | 43.1875 | 43.1875 | 0.03 | 1.03 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 29.3
2019-10-01 | 9:32 | 43.3008 | 43.3008 | 0.02 | 1.02 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 28.32
2019-10-01 | 9:32 | 43.3984 | 43.3984 | 0.01 | 1.01 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 9:32 | 43.5 | 43.5 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 29.3
2019-10-01 | 9:32 | 43.5977 | 43.5977 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:32 | 43.6992 | 43.6992 | 0.02 | 1.02 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 9:32 | 43.8086 | 43.8086 | -0.1 | 0.9 | -0.66 | 0.34 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 9:32 | 43.9102 | 43.9102 | -0.14 | 0.86 | -0.63 | 0.37 | -0.64 | 0.36 | 72.27 | 28.32
2019-10-01 | 9:32 | 44.0078 | 44.0078 | -0.17 | 0.83 | -0.61 | 0.39 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:32 | 44.1211 | 44.1211 | -0.15 | 0.85 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 27.34
2019-10-01 | 9:32 | 44.2188 | 44.2188 | -0.01 | 0.99 | -0.75 | 0.25 | -0.64 | 0.36 | 72.27 | 28.32
2019-10-01 | 9:32 | 44.3203 | 44.3203 | 0.01 | 1.01 | -0.77 | 0.23 | -0.64 | 0.36 | 72.27 | 28.32
2019-10-01 | 9:32 | 44.418 | 44.418 | 0.01 | 1.01 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 9:32 | 44.5312 | 44.5312 | 0.01 | 1.01 | -0.78 | 0.22 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:32 | 44.6289 | 44.6289 | 0.03 | 1.03 | -0.78 | 0.22 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 9:32 | 44.7305 | 44.7305 | 0.01 | 1.01 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 28.32
2019-10-01 | 9:32 | 44.8281 | 44.8281 | 0.03 | 1.03 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 44.9375 | 44.9375 | 0.02 | 1.02 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:32 | 45.0391 | 45.0391 | 0.02 | 1.02 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 9:32 | 45.1406 | 45.1406 | 0.02 | 1.02 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 9:32 | 45.25 | 45.25 | -0.01 | 0.99 | -0.74 | 0.26 | -0.65 | 0.35 | 72.27 | 28.32
2019-10-01 | 9:32 | 45.3477 | 45.3477 | -0.11 | 0.89 | -0.64 | 0.36 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:32 | 45.4492 | 45.4492 | -0.16 | 0.84 | -0.61 | 0.39 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 45.5508 | 45.5508 | -0.16 | 0.84 | -0.6 | 0.4 | -0.63 | 0.37 | 72.27 | 30.27
2019-10-01 | 9:32 | 45.6602 | 45.6602 | -0.02 | 0.98 | -0.74 | 0.26 | -0.62 | 0.38 | 74.22 | 27.34
2019-10-01 | 9:32 | 45.7578 | 45.7578 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:32 | 45.8594 | 45.8594 | 0.02 | 1.02 | -0.76 | 0.24 | -0.64 | 0.36 | 73.24 | 28.32
2019-10-01 | 9:32 | 45.9609 | 45.9609 | 0.02 | 1.02 | -0.78 | 0.22 | -0.64 | 0.36 | 73.24 | 28.32
2019-10-01 | 9:32 | 46.0703 | 46.0703 | 0.01 | 1.01 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:32 | 46.168 | 46.168 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:32 | 46.2812 | 46.2812 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 28.32
2019-10-01 | 9:32 | 46.3789 | 46.3789 | 0.01 | 1.01 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 46.4805 | 46.4805 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:32 | 46.5781 | 46.5781 | 0.03 | 1.03 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 28.32
2019-10-01 | 9:32 | 46.6875 | 46.6875 | 0.03 | 1.03 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 29.3
2019-10-01 | 9:32 | 46.7891 | 46.7891 | -0.04 | 0.96 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:32 | 46.8906 | 46.8906 | -0.13 | 0.87 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 46.9883 | 46.9883 | -0.15 | 0.85 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:32 | 47.0977 | 47.0977 | -0.16 | 0.84 | -0.61 | 0.39 | -0.63 | 0.37 | 74.22 | 28.32
2019-10-01 | 9:32 | 47.1992 | 47.1992 | -0.01 | 0.99 | -0.76 | 0.24 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 47.3008 | 47.3008 | 0 | 1 | -0.77 | 0.23 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 9:32 | 47.4102 | 47.4102 | 0.01 | 1.01 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 47.5078 | 47.5078 | 0.01 | 1.01 | -0.78 | 0.22 | -0.63 | 0.37 | 72.27 | 28.32
2019-10-01 | 9:32 | 47.6094 | 47.6094 | 0.01 | 1.01 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 47.7109 | 47.7109 | 0.02 | 1.02 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 47.8203 | 47.8203 | 0.01 | 1.01 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:32 | 47.918 | 47.918 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:32 | 48.0195 | 48.0195 | 0.03 | 1.03 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:32 | 48.1211 | 48.1211 | 0.03 | 1.03 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:32 | 48.2305 | 48.2305 | 0.01 | 1.01 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:32 | 48.3281 | 48.3281 | -0.09 | 0.91 | -0.67 | 0.33 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 48.4297 | 48.4297 | -0.15 | 0.85 | -0.65 | 0.35 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 48.5391 | 48.5391 | -0.16 | 0.84 | -0.6 | 0.4 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 9:32 | 48.6406 | 48.6406 | -0.08 | 0.92 | -0.68 | 0.32 | -0.62 | 0.38 | 72.27 | 26.37
2019-10-01 | 9:32 | 48.7383 | 48.7383 | -0.01 | 0.99 | -0.78 | 0.22 | -0.65 | 0.35 | 74.22 | 27.34
2019-10-01 | 9:32 | 48.8398 | 48.8398 | 0.01 | 1.01 | -0.78 | 0.22 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:32 | 48.9492 | 48.9492 | 0.01 | 1.01 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 49.0508 | 49.0508 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 49.1484 | 49.1484 | 0.02 | 1.02 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 49.25 | 49.25 | 0.03 | 1.03 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:32 | 49.3594 | 49.3594 | 0.03 | 1.03 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 28.32
2019-10-01 | 9:32 | 49.4609 | 49.4609 | 0.02 | 1.02 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:32 | 49.5586 | 49.5586 | 0.01 | 1.01 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:32 | 49.668 | 49.668 | 0.02 | 1.02 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:32 | 49.7695 | 49.7695 | -0.03 | 0.97 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:32 | 49.8711 | 49.8711 | -0.13 | 0.87 | -0.67 | 0.33 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 49.9688 | 49.9688 | -0.15 | 0.85 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 50.0781 | 50.0781 | -0.16 | 0.84 | -0.62 | 0.38 | -0.63 | 0.37 | 72.27 | 26.37
2019-10-01 | 9:32 | 50.1797 | 50.1797 | -0.02 | 0.98 | -0.76 | 0.24 | -0.65 | 0.35 | 71.29 | 27.34
2019-10-01 | 9:32 | 50.2812 | 50.2812 | 0 | 1 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 50.3789 | 50.3789 | 0.01 | 1.01 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 50.4883 | 50.4883 | 0.01 | 1.01 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 50.5898 | 50.5898 | 0.02 | 1.02 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:32 | 50.6875 | 50.6875 | 0.03 | 1.03 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:32 | 50.7891 | 50.7891 | 0.02 | 1.02 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 27.34
2019-10-01 | 9:32 | 50.8984 | 50.8984 | 0.02 | 1.02 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:32 | 51 | 51 | 0.01 | 1.01 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 51.0977 | 51.0977 | 0.03 | 1.03 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:32 | 51.2109 | 51.2109 | 0.02 | 1.02 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:32 | 51.3086 | 51.3086 | -0.07 | 0.93 | -0.73 | 0.27 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 51.4102 | 51.4102 | -0.13 | 0.87 | -0.66 | 0.34 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 9:32 | 51.5078 | 51.5078 | -0.16 | 0.84 | -0.65 | 0.35 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:32 | 51.6211 | 51.6211 | -0.15 | 0.85 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:32 | 51.7188 | 51.7188 | 0 | 1 | -0.8 | 0.2 | -0.64 | 0.36 | 71.29 | 26.37
2019-10-01 | 9:32 | 51.8203 | 51.8203 | 0.01 | 1.01 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:32 | 51.9297 | 51.9297 | 0 | 1 | -0.8 | 0.2 | -0.65 | 0.35 | 71.29 | 27.34
2019-10-01 | 9:32 | 52.0312 | 52.0312 | 0.01 | 1.01 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:32 | 52.1289 | 52.1289 | 0.01 | 1.01 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 52.2383 | 52.2383 | 0.01 | 1.01 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 52.3398 | 52.3398 | 0.02 | 1.02 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 52.4375 | 52.4375 | 0.02 | 1.02 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:32 | 52.5391 | 52.5391 | 0.01 | 1.01 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:32 | 52.6406 | 52.6406 | 0.03 | 1.03 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 9:32 | 52.75 | 52.75 | 0 | 1 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:32 | 52.8477 | 52.8477 | -0.12 | 0.88 | -0.68 | 0.32 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:32 | 52.9609 | 52.9609 | -0.15 | 0.85 | -0.64 | 0.36 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 9:32 | 53.0586 | 53.0586 | -0.17 | 0.83 | -0.65 | 0.35 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:32 | 53.1602 | 53.1602 | -0.03 | 0.97 | -0.77 | 0.23 | -0.63 | 0.37 | 73.24 | 27.34
2019-10-01 | 9:32 | 53.2578 | 53.2578 | 0 | 1 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 53.3711 | 53.3711 | 0 | 1 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:32 | 53.4688 | 53.4688 | 0.01 | 1.01 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:32 | 53.5703 | 53.5703 | 0.02 | 1.02 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 53.668 | 53.668 | 0 | 1 | -0.81 | 0.19 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:32 | 53.7812 | 53.7812 | 0.02 | 1.02 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 53.8789 | 53.8789 | 0.02 | 1.02 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:32 | 53.9805 | 53.9805 | 0.02 | 1.02 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 54.0781 | 54.0781 | 0.02 | 1.02 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 9:32 | 54.1797 | 54.1797 | 0.03 | 1.03 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:32 | 54.2891 | 54.2891 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:32 | 54.3906 | 54.3906 | -0.14 | 0.86 | -0.68 | 0.32 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 54.5 | 54.5 | -0.16 | 0.84 | -0.66 | 0.34 | -0.64 | 0.36 | 73.24 | 27.34
2019-10-01 | 9:33 | 54.5977 | 54.5977 | -0.15 | 0.85 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 54.6992 | 54.6992 | -0.01 | 0.99 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 54.8008 | 54.8008 | 0 | 1 | -0.8 | 0.2 | -0.64 | 0.36 | 73.24 | 27.34
2019-10-01 | 9:33 | 54.9102 | 54.9102 | 0 | 1 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 55.0078 | 55.0078 | 0.01 | 1.01 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 55.1094 | 55.1094 | 0.01 | 1.01 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:33 | 55.2109 | 55.2109 | 0.01 | 1.01 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 55.3203 | 55.3203 | 0.02 | 1.02 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 55.418 | 55.418 | 0.02 | 1.02 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 55.5195 | 55.5195 | 0.02 | 1.02 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 28.32
2019-10-01 | 9:33 | 55.6289 | 55.6289 | 0.02 | 1.02 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 55.7305 | 55.7305 | 0.02 | 1.02 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:33 | 55.8281 | 55.8281 | -0.12 | 0.88 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:33 | 55.9297 | 55.9297 | -0.15 | 0.85 | -0.67 | 0.33 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 56.0391 | 56.0391 | -0.18 | 0.82 | -0.64 | 0.36 | -0.63 | 0.37 | 72.27 | 26.37
2019-10-01 | 9:33 | 56.1406 | 56.1406 | -0.1 | 0.9 | -0.7 | 0.3 | -0.62 | 0.38 | 72.27 | 25.39
2019-10-01 | 9:33 | 56.2383 | 56.2383 | 0.01 | 1.01 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 56.3398 | 56.3398 | -0.01 | 0.99 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 56.4492 | 56.4492 | 0.01 | 1.01 | -0.82 | 0.18 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 56.5508 | 56.5508 | 0.01 | 1.01 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 56.6484 | 56.6484 | 0.02 | 1.02 | -0.8 | 0.2 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:33 | 56.75 | 56.75 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 56.8594 | 56.8594 | 0.02 | 1.02 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:33 | 56.9609 | 56.9609 | 0.01 | 1.01 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:33 | 57.0703 | 57.0703 | 0.01 | 1.01 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 57.168 | 57.168 | 0.02 | 1.02 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 57.2695 | 57.2695 | -0.01 | 0.99 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 57.3711 | 57.3711 | -0.13 | 0.87 | -0.68 | 0.32 | -0.64 | 0.36 | 74.22 | 28.32
2019-10-01 | 9:33 | 57.4688 | 57.4688 | -0.15 | 0.85 | -0.65 | 0.35 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 57.5781 | 57.5781 | -0.16 | 0.84 | -0.63 | 0.37 | -0.63 | 0.37 | 72.27 | 25.39
2019-10-01 | 9:33 | 57.6797 | 57.6797 | -0.03 | 0.97 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 57.7891 | 57.7891 | -0.01 | 0.99 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 57.8906 | 57.8906 | 0 | 1 | -0.81 | 0.19 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 9:33 | 57.9883 | 57.9883 | 0.01 | 1.01 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 58.0898 | 58.0898 | 0.01 | 1.01 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 58.1992 | 58.1992 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 9:33 | 58.3008 | 58.3008 | 0.02 | 1.02 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 58.3984 | 58.3984 | 0.02 | 1.02 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 58.5 | 58.5 | 0 | 1 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 58.6094 | 58.6094 | 0.02 | 1.02 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 58.7109 | 58.7109 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 58.8086 | 58.8086 | -0.07 | 0.93 | -0.73 | 0.27 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 58.918 | 58.918 | -0.16 | 0.84 | -0.67 | 0.33 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:33 | 59.0195 | 59.0195 | -0.15 | 0.85 | -0.65 | 0.35 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 59.1211 | 59.1211 | -0.15 | 0.85 | -0.66 | 0.34 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 59.2188 | 59.2188 | -0.03 | 0.97 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 59.3281 | 59.3281 | -0.01 | 0.99 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 59.4297 | 59.4297 | 0.01 | 1.01 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 59.5312 | 59.5312 | 0.01 | 1.01 | -0.82 | 0.18 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 9:33 | 59.6289 | 59.6289 | 0.01 | 1.01 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 59.7383 | 59.7383 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 28.32
2019-10-01 | 9:33 | 59.8398 | 59.8398 | 0.01 | 1.01 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 59.9375 | 59.9375 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 60.0391 | 60.0391 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 60.1484 | 60.1484 | 0 | 1 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 60.25 | 60.25 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 60.3477 | 60.3477 | -0.11 | 0.89 | -0.7 | 0.3 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 60.4609 | 60.4609 | -0.17 | 0.83 | -0.66 | 0.34 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:33 | 60.5586 | 60.5586 | -0.15 | 0.85 | -0.67 | 0.33 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:33 | 60.6602 | 60.6602 | -0.04 | 0.96 | -0.78 | 0.22 | -0.63 | 0.37 | 72.27 | 26.37
2019-10-01 | 9:33 | 60.7695 | 60.7695 | -0.01 | 0.99 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 60.8711 | 60.8711 | 0 | 1 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 60.9688 | 60.9688 | -0.01 | 0.99 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 61.0703 | 61.0703 | 0 | 1 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 61.168 | 61.168 | 0.01 | 1.01 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 61.2812 | 61.2812 | 0 | 1 | -0.82 | 0.18 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 61.3789 | 61.3789 | 0 | 1 | -0.82 | 0.18 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 61.4805 | 61.4805 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 61.5898 | 61.5898 | 0.02 | 1.02 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 61.6875 | 61.6875 | 0 | 1 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:33 | 61.7891 | 61.7891 | -0.03 | 0.97 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:33 | 61.8906 | 61.8906 | -0.13 | 0.87 | -0.7 | 0.3 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 62 | 62 | -0.16 | 0.84 | -0.66 | 0.34 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:33 | 62.0977 | 62.0977 | -0.18 | 0.82 | -0.66 | 0.34 | -0.63 | 0.37 | 72.27 | 25.39
2019-10-01 | 9:33 | 62.1992 | 62.1992 | -0.03 | 0.97 | -0.79 | 0.21 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 9:33 | 62.3008 | 62.3008 | 0.01 | 1.01 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 62.4102 | 62.4102 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 62.5078 | 62.5078 | 0 | 1 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 62.6094 | 62.6094 | 0 | 1 | -0.82 | 0.18 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 9:33 | 62.7188 | 62.7188 | 0 | 1 | -0.82 | 0.18 | -0.66 | 0.34 | 74.22 | 27.34
2019-10-01 | 9:33 | 62.8203 | 62.8203 | 0.01 | 1.01 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:33 | 62.918 | 62.918 | 0.01 | 1.01 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 63.0195 | 63.0195 | 0.02 | 1.02 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 63.1289 | 63.1289 | 0.03 | 1.03 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 27.34
2019-10-01 | 9:33 | 63.2305 | 63.2305 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 9:33 | 63.3281 | 63.3281 | -0.09 | 0.91 | -0.74 | 0.26 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 63.4297 | 63.4297 | -0.15 | 0.85 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:33 | 63.5391 | 63.5391 | -0.15 | 0.85 | -0.67 | 0.33 | -0.64 | 0.36 | 71.29 | 25.39
2019-10-01 | 9:33 | 63.6406 | 63.6406 | -0.16 | 0.84 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:33 | 63.75 | 63.75 | -0.01 | 0.99 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 63.8398 | 63.8398 | 0.01 | 1.01 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 63.9492 | 63.9492 | 0 | 1 | -0.82 | 0.18 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 9:33 | 64.0508 | 64.0508 | 0 | 1 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 64.1484 | 64.1484 | 0 | 1 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 64.2578 | 64.2578 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 64.3594 | 64.3594 | 0.02 | 1.02 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 64.4609 | 64.4609 | 0.02 | 1.02 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 64.5586 | 64.5586 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 64.668 | 64.668 | 0.01 | 1.01 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 64.7695 | 64.7695 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 9:33 | 64.8789 | 64.8789 | -0.13 | 0.87 | -0.68 | 0.32 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:33 | 64.9805 | 64.9805 | -0.17 | 0.83 | -0.67 | 0.33 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 65.0781 | 65.0781 | -0.17 | 0.83 | -0.65 | 0.35 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 65.1797 | 65.1797 | -0.03 | 0.97 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 65.2891 | 65.2891 | 0 | 1 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 65.3906 | 65.3906 | -0.01 | 0.99 | -0.8 | 0.2 | -0.66 | 0.34 | 71.29 | 24.41
2019-10-01 | 9:33 | 65.4883 | 65.4883 | 0 | 1 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 65.5898 | 65.5898 | -0.01 | 0.99 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 65.6992 | 65.6992 | 0 | 1 | -0.82 | 0.18 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 9:33 | 65.8008 | 65.8008 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 65.8984 | 65.8984 | 0.01 | 1.01 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 66 | 66 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 66.1094 | 66.1094 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 66.2109 | 66.2109 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 66.3086 | 66.3086 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 66.418 | 66.418 | -0.14 | 0.86 | -0.69 | 0.31 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 66.5195 | 66.5195 | -0.17 | 0.83 | -0.66 | 0.34 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:33 | 66.6211 | 66.6211 | -0.18 | 0.82 | -0.65 | 0.35 | -0.63 | 0.37 | 72.27 | 26.37
2019-10-01 | 9:33 | 66.7188 | 66.7188 | -0.01 | 0.99 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 66.8281 | 66.8281 | -0.01 | 0.99 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 66.9297 | 66.9297 | -0.01 | 0.99 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 67.0312 | 67.0312 | -0.01 | 0.99 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 67.1406 | 67.1406 | -0.01 | 0.99 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:33 | 67.2383 | 67.2383 | 0.01 | 1.01 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 67.3398 | 67.3398 | 0.01 | 1.01 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 67.4375 | 67.4375 | 0.02 | 1.02 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 67.5508 | 67.5508 | 0.01 | 1.01 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-10-01 | 9:33 | 67.6484 | 67.6484 | 0.02 | 1.02 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 67.75 | 67.75 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 67.8477 | 67.8477 | -0.13 | 0.87 | -0.71 | 0.29 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 67.9609 | 67.9609 | -0.16 | 0.84 | -0.66 | 0.34 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 68.0586 | 68.0586 | -0.15 | 0.85 | -0.68 | 0.32 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 68.1602 | 68.1602 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:33 | 68.2578 | 68.2578 | -0.01 | 0.99 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 9:33 | 68.3711 | 68.3711 | 0 | 1 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 68.4688 | 68.4688 | -0.01 | 0.99 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 68.5781 | 68.5781 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 9:33 | 68.6797 | 68.6797 | 0 | 1 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 68.7812 | 68.7812 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 68.8789 | 68.8789 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 68.9805 | 68.9805 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 69.0898 | 69.0898 | 0 | 1 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 9:33 | 69.1875 | 69.1875 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 69.2891 | 69.2891 | -0.04 | 0.96 | -0.78 | 0.22 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 9:33 | 69.3906 | 69.3906 | -0.14 | 0.86 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:33 | 69.5 | 69.5 | -0.18 | 0.82 | -0.67 | 0.33 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 69.5977 | 69.5977 | -0.19 | 0.81 | -0.65 | 0.35 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 69.7109 | 69.7109 | -0.03 | 0.97 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 69.8086 | 69.8086 | -0.03 | 0.97 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 69.9102 | 69.9102 | 0 | 1 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 70.0078 | 70.0078 | -0.02 | 0.98 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 70.1211 | 70.1211 | -0.01 | 0.99 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 70.2188 | 70.2188 | 0.02 | 1.02 | -0.82 | 0.18 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 9:33 | 70.3203 | 70.3203 | 0 | 1 | -0.82 | 0.18 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 9:33 | 70.4297 | 70.4297 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 70.5195 | 70.5195 | 0.01 | 1.01 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 70.6289 | 70.6289 | 0 | 1 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:33 | 70.7305 | 70.7305 | 0.01 | 1.01 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 70.8398 | 70.8398 | -0.1 | 0.9 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 70.9375 | 70.9375 | -0.16 | 0.84 | -0.68 | 0.32 | -0.64 | 0.36 | 73.24 | 27.34
2019-10-01 | 9:33 | 71.0391 | 71.0391 | -0.17 | 0.83 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 71.1406 | 71.1406 | -0.19 | 0.81 | -0.65 | 0.35 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 71.25 | 71.25 | -0.02 | 0.98 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 71.3477 | 71.3477 | -0.01 | 0.99 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 71.4492 | 71.4492 | -0.01 | 0.99 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 71.5586 | 71.5586 | -0.01 | 0.99 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 71.6602 | 71.6602 | -0.01 | 0.99 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 71.7578 | 71.7578 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 71.8594 | 71.8594 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 71.9688 | 71.9688 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 72.0703 | 72.0703 | 0.01 | 1.01 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 72.168 | 72.168 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 72.2695 | 72.2695 | -0.01 | 0.99 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 72.3789 | 72.3789 | -0.14 | 0.86 | -0.7 | 0.3 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 72.4805 | 72.4805 | -0.18 | 0.82 | -0.67 | 0.33 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:33 | 72.5781 | 72.5781 | -0.17 | 0.83 | -0.67 | 0.33 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 72.6797 | 72.6797 | -0.04 | 0.96 | -0.78 | 0.22 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:33 | 72.7891 | 72.7891 | -0.01 | 0.99 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 72.8906 | 72.8906 | -0.01 | 0.99 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 72.9883 | 72.9883 | 0 | 1 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:33 | 73.0977 | 73.0977 | -0.01 | 0.99 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 73.1992 | 73.1992 | -0.01 | 0.99 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 73.3008 | 73.3008 | 0 | 1 | -0.83 | 0.17 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 73.3984 | 73.3984 | 0 | 1 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 28.32
2019-10-01 | 9:33 | 73.5078 | 73.5078 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 73.6094 | 73.6094 | 0.02 | 1.02 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 73.7109 | 73.7109 | 0 | 1 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 73.8086 | 73.8086 | -0.09 | 0.91 | -0.74 | 0.26 | -0.67 | 0.33 | 75.2 | 27.34
2019-10-01 | 9:33 | 73.918 | 73.918 | -0.17 | 0.83 | -0.67 | 0.33 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 74.0195 | 74.0195 | -0.15 | 0.85 | -0.68 | 0.32 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 74.1211 | 74.1211 | -0.18 | 0.82 | -0.64 | 0.36 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:33 | 74.2305 | 74.2305 | -0.02 | 0.98 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 74.3281 | 74.3281 | -0.01 | 0.99 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 74.4297 | 74.4297 | -0.01 | 0.99 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 74.5391 | 74.5391 | 0 | 1 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 74.6406 | 74.6406 | 0.01 | 1.01 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 74.7383 | 74.7383 | 0 | 1 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:33 | 74.8398 | 74.8398 | 0.01 | 1.01 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 74.9375 | 74.9375 | 0 | 1 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 75.0508 | 75.0508 | 0.01 | 1.01 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 75.1484 | 75.1484 | 0 | 1 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 75.25 | 75.25 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 75.3477 | 75.3477 | -0.11 | 0.89 | -0.73 | 0.27 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 75.4609 | 75.4609 | -0.17 | 0.83 | -0.71 | 0.29 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 75.5703 | 75.5703 | -0.18 | 0.82 | -0.72 | 0.28 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 75.668 | 75.668 | -0.07 | 0.93 | -0.81 | 0.19 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:33 | 75.7695 | 75.7695 | -0.02 | 0.98 | -0.85 | 0.15 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 75.8711 | 75.8711 | -0.02 | 0.98 | -0.84 | 0.16 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 75.9688 | 75.9688 | -0.01 | 0.99 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 76.0781 | 76.0781 | 0 | 1 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 76.1797 | 76.1797 | -0.01 | 0.99 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 76.2812 | 76.2812 | -0.01 | 0.99 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 76.3789 | 76.3789 | 0 | 1 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 76.4805 | 76.4805 | -0.01 | 0.99 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 24.41
2019-10-01 | 9:33 | 76.5898 | 76.5898 | 0 | 1 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 76.6992 | 76.6992 | -0.01 | 0.99 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 76.8008 | 76.8008 | -0.06 | 0.94 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 76.8984 | 76.8984 | -0.16 | 0.84 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 77 | 77 | -0.18 | 0.82 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 77.1094 | 77.1094 | -0.18 | 0.82 | -0.72 | 0.28 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 77.2109 | 77.2109 | -0.04 | 0.96 | -0.83 | 0.17 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:33 | 77.3086 | 77.3086 | -0.02 | 0.98 | -0.85 | 0.15 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 9:33 | 77.4102 | 77.4102 | -0.02 | 0.98 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 77.5078 | 77.5078 | -0.02 | 0.98 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 77.6211 | 77.6211 | -0.01 | 0.99 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 9:33 | 77.7188 | 77.7188 | -0.01 | 0.99 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 77.8203 | 77.8203 | 0.01 | 1.01 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 77.9297 | 77.9297 | 0 | 1 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 78.0312 | 78.0312 | 0 | 1 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 78.1289 | 78.1289 | 0.01 | 1.01 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 78.2305 | 78.2305 | -0.01 | 0.99 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 78.3398 | 78.3398 | -0.1 | 0.9 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 78.4375 | 78.4375 | -0.17 | 0.83 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 78.5391 | 78.5391 | -0.19 | 0.81 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 9:33 | 78.6406 | 78.6406 | -0.18 | 0.82 | -0.8 | 0.2 | -0.65 | 0.35 | 71.29 | 24.41
2019-10-01 | 9:33 | 78.75 | 78.75 | -0.03 | 0.97 | -0.89 | 0.11 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 78.8477 | 78.8477 | -0.01 | 0.99 | -0.88 | 0.12 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 9:33 | 78.9492 | 78.9492 | -0.02 | 0.98 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 79.0586 | 79.0586 | -0.01 | 0.99 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 79.1602 | 79.1602 | -0.01 | 0.99 | -0.85 | 0.15 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:33 | 79.2578 | 79.2578 | -0.01 | 0.99 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:33 | 79.3594 | 79.3594 | 0 | 1 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 79.4688 | 79.4688 | 0 | 1 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 79.5703 | 79.5703 | 0.01 | 1.01 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 79.6797 | 79.6797 | 0 | 1 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 79.7695 | 79.7695 | -0.01 | 0.99 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 79.8789 | 79.8789 | -0.13 | 0.87 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 79.9805 | 79.9805 | -0.17 | 0.83 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 80.0781 | 80.0781 | -0.17 | 0.83 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 80.1875 | 80.1875 | -0.04 | 0.96 | -0.9 | 0.1 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 9:33 | 80.2891 | 80.2891 | -0.02 | 0.98 | -0.88 | 0.12 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:33 | 80.3906 | 80.3906 | -0.02 | 0.98 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 80.5 | 80.5 | 0 | 1 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 80.5977 | 80.5977 | -0.01 | 0.99 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 80.6992 | 80.6992 | -0.01 | 0.99 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 80.8008 | 80.8008 | 0 | 1 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 80.8984 | 80.8984 | -0.02 | 0.98 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 81.0078 | 81.0078 | 0 | 1 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 81.1094 | 81.1094 | 0 | 1 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 81.2109 | 81.2109 | 0 | 1 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 9:33 | 81.3203 | 81.3203 | -0.05 | 0.95 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 81.418 | 81.418 | -0.16 | 0.84 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:33 | 81.5195 | 81.5195 | -0.18 | 0.82 | -0.8 | 0.2 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 9:33 | 81.6289 | 81.6289 | -0.18 | 0.82 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 81.7305 | 81.7305 | -0.04 | 0.96 | -0.89 | 0.11 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 81.8281 | 81.8281 | -0.03 | 0.97 | -0.87 | 0.13 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 81.9297 | 81.9297 | -0.01 | 0.99 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:33 | 82.0391 | 82.0391 | 0 | 1 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 82.1406 | 82.1406 | 0 | 1 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 82.2383 | 82.2383 | -0.02 | 0.98 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 82.3398 | 82.3398 | 0 | 1 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 82.4492 | 82.4492 | -0.01 | 0.99 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 82.5508 | 82.5508 | -0.01 | 0.99 | -0.84 | 0.16 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 9:33 | 82.6484 | 82.6484 | 0 | 1 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 82.7578 | 82.7578 | -0.02 | 0.98 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 82.8594 | 82.8594 | -0.14 | 0.86 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 82.9609 | 82.9609 | -0.19 | 0.81 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 83.0586 | 83.0586 | -0.18 | 0.82 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 83.168 | 83.168 | -0.1 | 0.9 | -0.88 | 0.12 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 83.2695 | 83.2695 | -0.04 | 0.96 | -0.89 | 0.11 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:33 | 83.3711 | 83.3711 | -0.03 | 0.97 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 83.4688 | 83.4688 | -0.01 | 0.99 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 83.5781 | 83.5781 | -0.01 | 0.99 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:33 | 83.6797 | 83.6797 | -0.02 | 0.98 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 83.7812 | 83.7812 | -0.02 | 0.98 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 83.8906 | 83.8906 | -0.01 | 0.99 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 83.9883 | 83.9883 | 0 | 1 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 84.0898 | 84.0898 | 0 | 1 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 84.1875 | 84.1875 | 0 | 1 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 84.3008 | 84.3008 | -0.05 | 0.95 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:33 | 84.3984 | 84.3984 | -0.17 | 0.83 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 84.5 | 84.5 | -0.18 | 0.82 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 23.44
2019-10-01 | 9:33 | 84.5977 | 84.5977 | -0.2 | 0.8 | -0.8 | 0.2 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 84.7109 | 84.7109 | -0.04 | 0.96 | -0.92 | 0.08 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:33 | 84.8086 | 84.8086 | -0.03 | 0.97 | -0.89 | 0.11 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:33 | 84.9102 | 84.9102 | -0.03 | 0.97 | -0.88 | 0.12 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 85.0195 | 85.0195 | -0.01 | 0.99 | -0.86 | 0.14 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:33 | 85.1211 | 85.1211 | -0.02 | 0.98 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 85.2188 | 85.2188 | -0.01 | 0.99 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 85.3203 | 85.3203 | -0.02 | 0.98 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 85.4297 | 85.4297 | -0.01 | 0.99 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 85.5312 | 85.5312 | -0.01 | 0.99 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 85.6289 | 85.6289 | -0.02 | 0.98 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:33 | 85.7305 | 85.7305 | -0.01 | 0.99 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 85.8398 | 85.8398 | -0.12 | 0.88 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 85.9375 | 85.9375 | -0.18 | 0.82 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 86.0508 | 86.0508 | -0.18 | 0.82 | -0.83 | 0.17 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:33 | 86.1484 | 86.1484 | -0.2 | 0.8 | -0.82 | 0.18 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:33 | 86.25 | 86.25 | -0.03 | 0.97 | -0.93 | 0.07 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:33 | 86.3477 | 86.3477 | -0.02 | 0.98 | -0.89 | 0.11 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 86.4492 | 86.4492 | -0.02 | 0.98 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 86.5586 | 86.5586 | -0.01 | 0.99 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:33 | 86.6602 | 86.6602 | -0.01 | 0.99 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 86.7578 | 86.7578 | -0.01 | 0.99 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 86.8594 | 86.8594 | -0.02 | 0.98 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 86.9688 | 86.9688 | -0.02 | 0.98 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:33 | 87.0703 | 87.0703 | -0.02 | 0.98 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 87.1797 | 87.1797 | 0 | 1 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:33 | 87.2812 | 87.2812 | -0.01 | 0.99 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 87.3789 | 87.3789 | -0.16 | 0.84 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 87.4805 | 87.4805 | -0.18 | 0.82 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 87.5898 | 87.5898 | -0.19 | 0.81 | -0.81 | 0.19 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 87.6875 | 87.6875 | -0.05 | 0.95 | -0.92 | 0.08 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 87.7891 | 87.7891 | -0.04 | 0.96 | -0.91 | 0.09 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 87.8906 | 87.8906 | -0.02 | 0.98 | -0.88 | 0.12 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 9:33 | 88 | 88 | -0.02 | 0.98 | -0.87 | 0.13 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 88.0977 | 88.0977 | -0.02 | 0.98 | -0.87 | 0.13 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:33 | 88.1992 | 88.1992 | -0.01 | 0.99 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 88.3086 | 88.3086 | -0.01 | 0.99 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 88.4102 | 88.4102 | -0.02 | 0.98 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 88.5078 | 88.5078 | -0.01 | 0.99 | -0.86 | 0.14 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 9:33 | 88.6094 | 88.6094 | -0.02 | 0.98 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 88.7188 | 88.7188 | -0.03 | 0.97 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 88.8203 | 88.8203 | -0.05 | 0.95 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:33 | 88.918 | 88.918 | -0.15 | 0.85 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 89.0195 | 89.0195 | -0.19 | 0.81 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 89.1289 | 89.1289 | -0.18 | 0.82 | -0.81 | 0.19 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 9:33 | 89.2305 | 89.2305 | -0.03 | 0.97 | -0.9 | 0.1 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 89.3281 | 89.3281 | -0.04 | 0.96 | -0.89 | 0.11 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 89.4297 | 89.4297 | -0.03 | 0.97 | -0.87 | 0.13 | -0.66 | 0.34 | 74.22 | 27.34
2019-10-01 | 9:33 | 89.5391 | 89.5391 | -0.03 | 0.97 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 89.6406 | 89.6406 | -0.03 | 0.97 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 89.7383 | 89.7383 | -0.01 | 0.99 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 89.8477 | 89.8477 | -0.02 | 0.98 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-10-01 | 9:33 | 89.9492 | 89.9492 | -0.03 | 0.97 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 90.0508 | 90.0508 | -0.01 | 0.99 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 90.1484 | 90.1484 | 0 | 1 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 90.2578 | 90.2578 | -0.01 | 0.99 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 90.3594 | 90.3594 | -0.12 | 0.88 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 90.4609 | 90.4609 | -0.19 | 0.81 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 90.5586 | 90.5586 | -0.21 | 0.79 | -0.83 | 0.17 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:33 | 90.668 | 90.668 | -0.13 | 0.87 | -0.89 | 0.11 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:33 | 90.7695 | 90.7695 | -0.03 | 0.97 | -0.91 | 0.09 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:33 | 90.8711 | 90.8711 | -0.02 | 0.98 | -0.89 | 0.11 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:33 | 90.9805 | 90.9805 | -0.04 | 0.96 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 91.0781 | 91.0781 | -0.03 | 0.97 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 91.1797 | 91.1797 | -0.03 | 0.97 | -0.87 | 0.13 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 91.2812 | 91.2812 | -0.03 | 0.97 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 91.3906 | 91.3906 | -0.01 | 0.99 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 91.4883 | 91.4883 | -0.01 | 0.99 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 91.5898 | 91.5898 | -0.01 | 0.99 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 91.6875 | 91.6875 | -0.02 | 0.98 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 91.8008 | 91.8008 | -0.04 | 0.96 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 27.34
2019-10-01 | 9:33 | 91.8984 | 91.8984 | -0.15 | 0.85 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 92.0078 | 92.0078 | -0.2 | 0.8 | -0.84 | 0.16 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:33 | 92.1094 | 92.1094 | -0.2 | 0.8 | -0.83 | 0.17 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 92.2109 | 92.2109 | -0.06 | 0.94 | -0.92 | 0.08 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 92.3086 | 92.3086 | -0.04 | 0.96 | -0.89 | 0.11 | -0.65 | 0.35 | 74.22 | 23.44
2019-10-01 | 9:33 | 92.4102 | 92.4102 | -0.03 | 0.97 | -0.89 | 0.11 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 92.5195 | 92.5195 | -0.04 | 0.96 | -0.89 | 0.11 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 92.6211 | 92.6211 | -0.03 | 0.97 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 92.7188 | 92.7188 | -0.01 | 0.99 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 92.8281 | 92.8281 | -0.02 | 0.98 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 92.9297 | 92.9297 | -0.02 | 0.98 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:33 | 93.0312 | 93.0312 | -0.02 | 0.98 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 93.1406 | 93.1406 | -0.03 | 0.97 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 93.2383 | 93.2383 | -0.03 | 0.97 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 93.3398 | 93.3398 | -0.06 | 0.94 | -0.83 | 0.17 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:33 | 93.4375 | 93.4375 | -0.18 | 0.82 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 93.5508 | 93.5508 | -0.2 | 0.8 | -0.81 | 0.19 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:33 | 93.6484 | 93.6484 | -0.19 | 0.81 | -0.82 | 0.18 | -0.64 | 0.36 | 74.22 | 27.34
2019-10-01 | 9:33 | 93.75 | 93.75 | -0.05 | 0.95 | -0.91 | 0.09 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 93.8477 | 93.8477 | -0.03 | 0.97 | -0.9 | 0.1 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 93.9609 | 93.9609 | -0.03 | 0.97 | -0.89 | 0.11 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 94.0586 | 94.0586 | -0.03 | 0.97 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 94.1602 | 94.1602 | -0.02 | 0.98 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 94.2695 | 94.2695 | -0.04 | 0.96 | -0.86 | 0.14 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 94.3711 | 94.3711 | -0.03 | 0.97 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 94.4688 | 94.4688 | -0.03 | 0.97 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 94.5703 | 94.5703 | -0.04 | 0.96 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 94.6797 | 94.6797 | -0.04 | 0.96 | -0.87 | 0.13 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 9:33 | 94.7812 | 94.7812 | -0.03 | 0.97 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:33 | 94.8789 | 94.8789 | -0.15 | 0.85 | -0.83 | 0.17 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:33 | 94.9805 | 94.9805 | -0.19 | 0.81 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 95.0898 | 95.0898 | -0.19 | 0.81 | -0.85 | 0.15 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:33 | 95.1875 | 95.1875 | -0.08 | 0.92 | -0.93 | 0.07 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 95.2891 | 95.2891 | -0.06 | 0.94 | -0.89 | 0.11 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 95.3984 | 95.3984 | -0.05 | 0.95 | -0.89 | 0.11 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 95.5 | 95.5 | -0.04 | 0.96 | -0.89 | 0.11 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:33 | 95.5977 | 95.5977 | -0.04 | 0.96 | -0.88 | 0.12 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 95.7109 | 95.7109 | -0.04 | 0.96 | -0.88 | 0.12 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 95.8086 | 95.8086 | -0.02 | 0.98 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:33 | 95.9102 | 95.9102 | -0.03 | 0.97 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 96.0078 | 96.0078 | -0.03 | 0.97 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 96.1094 | 96.1094 | -0.03 | 0.97 | -0.85 | 0.15 | -0.68 | 0.32 | 75.2 | 26.37
2019-10-01 | 9:33 | 96.2188 | 96.2188 | -0.03 | 0.97 | -0.88 | 0.12 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 96.3203 | 96.3203 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 96.418 | 96.418 | -0.18 | 0.82 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 96.5312 | 96.5312 | -0.2 | 0.8 | -0.82 | 0.18 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:33 | 96.6289 | 96.6289 | -0.22 | 0.78 | -0.81 | 0.19 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 9:33 | 96.7305 | 96.7305 | -0.07 | 0.93 | -0.92 | 0.08 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 96.8281 | 96.8281 | -0.06 | 0.94 | -0.89 | 0.11 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 96.9375 | 96.9375 | -0.04 | 0.96 | -0.89 | 0.11 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 97.0391 | 97.0391 | -0.04 | 0.96 | -0.89 | 0.11 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 97.1406 | 97.1406 | -0.04 | 0.96 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 97.2383 | 97.2383 | -0.03 | 0.97 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 97.3477 | 97.3477 | -0.03 | 0.97 | -0.88 | 0.12 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 97.4492 | 97.4492 | -0.03 | 0.97 | -0.87 | 0.13 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:33 | 97.5508 | 97.5508 | -0.03 | 0.97 | -0.88 | 0.12 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 97.6602 | 97.6602 | -0.03 | 0.97 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 97.7578 | 97.7578 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 9:33 | 97.8594 | 97.8594 | -0.12 | 0.88 | -0.84 | 0.16 | -0.68 | 0.32 | 75.2 | 25.39
2019-10-01 | 9:33 | 97.9688 | 97.9688 | -0.19 | 0.81 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 98.0703 | 98.0703 | -0.21 | 0.79 | -0.81 | 0.19 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 9:33 | 98.168 | 98.168 | -0.17 | 0.83 | -0.85 | 0.15 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 98.2695 | 98.2695 | -0.06 | 0.94 | -0.9 | 0.1 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 98.3711 | 98.3711 | -0.05 | 0.95 | -0.9 | 0.1 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 98.4805 | 98.4805 | -0.04 | 0.96 | -0.88 | 0.12 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 98.5781 | 98.5781 | -0.04 | 0.96 | -0.87 | 0.13 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:33 | 98.6797 | 98.6797 | -0.04 | 0.96 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:33 | 98.7812 | 98.7812 | -0.04 | 0.96 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 98.8906 | 98.8906 | -0.05 | 0.95 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 98.9883 | 98.9883 | -0.04 | 0.96 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 99.0977 | 99.0977 | -0.05 | 0.95 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 9:33 | 99.1992 | 99.1992 | -0.05 | 0.95 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 99.3008 | 99.3008 | -0.08 | 0.92 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 99.3984 | 99.3984 | -0.2 | 0.8 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 99.5 | 99.5 | -0.2 | 0.8 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:33 | 99.6094 | 99.6094 | -0.21 | 0.79 | -0.81 | 0.19 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:33 | 99.7109 | 99.7109 | -0.08 | 0.92 | -0.91 | 0.09 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 99.8086 | 99.8086 | -0.07 | 0.93 | -0.9 | 0.1 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 99.9102 | 99.9102 | -0.04 | 0.96 | -0.88 | 0.12 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 100.0195 | 100.0195 | -0.06 | 0.94 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 100.1211 | 100.1211 | -0.06 | 0.94 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 23.44
2019-10-01 | 9:33 | 100.2305 | 100.2305 | -0.05 | 0.95 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:33 | 100.3281 | 100.3281 | -0.06 | 0.94 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 100.4297 | 100.4297 | -0.06 | 0.94 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 100.5313 | 100.5313 | -0.05 | 0.95 | -0.87 | 0.13 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:33 | 100.6406 | 100.6406 | -0.05 | 0.95 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 100.7383 | 100.7383 | -0.04 | 0.96 | -0.87 | 0.13 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:33 | 100.8398 | 100.8398 | -0.12 | 0.88 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 100.9375 | 100.9375 | -0.19 | 0.81 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 101.0508 | 101.0508 | -0.23 | 0.77 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 101.1484 | 101.1484 | -0.22 | 0.78 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:33 | 101.25 | 101.25 | -0.07 | 0.93 | -0.89 | 0.11 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:33 | 101.3594 | 101.3594 | -0.06 | 0.94 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 101.4609 | 101.4609 | -0.05 | 0.95 | -0.88 | 0.12 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 101.5586 | 101.5586 | -0.06 | 0.94 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 101.6602 | 101.6602 | -0.06 | 0.94 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 101.7695 | 101.7695 | -0.05 | 0.95 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 101.8711 | 101.8711 | -0.04 | 0.96 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 101.9688 | 101.9688 | -0.05 | 0.95 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 23.44
2019-10-01 | 9:33 | 102.0703 | 102.0703 | -0.05 | 0.95 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 102.1797 | 102.1797 | -0.06 | 0.94 | -0.86 | 0.14 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:33 | 102.2813 | 102.2813 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 102.3789 | 102.3789 | -0.18 | 0.82 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 102.4883 | 102.4883 | -0.22 | 0.78 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:33 | 102.5898 | 102.5898 | -0.22 | 0.78 | -0.78 | 0.22 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:33 | 102.6992 | 102.6992 | -0.1 | 0.9 | -0.88 | 0.12 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:33 | 102.7891 | 102.7891 | -0.07 | 0.93 | -0.89 | 0.11 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 102.8984 | 102.8984 | -0.07 | 0.93 | -0.87 | 0.13 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 103 | 103 | -0.07 | 0.93 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 103.0977 | 103.0977 | -0.06 | 0.94 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 103.1992 | 103.1992 | -0.06 | 0.94 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 103.3086 | 103.3086 | -0.05 | 0.95 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 103.4102 | 103.4102 | -0.04 | 0.96 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 103.5195 | 103.5195 | -0.04 | 0.96 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 103.6211 | 103.6211 | -0.06 | 0.94 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 103.7188 | 103.7188 | -0.04 | 0.96 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 103.8203 | 103.8203 | -0.09 | 0.91 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 103.9297 | 103.9297 | -0.21 | 0.79 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 104.0313 | 104.0313 | -0.21 | 0.79 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 104.1289 | 104.1289 | -0.23 | 0.77 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 27.34
2019-10-01 | 9:33 | 104.2305 | 104.2305 | -0.09 | 0.91 | -0.88 | 0.12 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 9:33 | 104.3281 | 104.3281 | -0.07 | 0.93 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 104.4375 | 104.4375 | -0.07 | 0.93 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 104.5391 | 104.5391 | -0.05 | 0.95 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 104.6406 | 104.6406 | -0.05 | 0.95 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 104.75 | 104.75 | -0.05 | 0.95 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 104.8477 | 104.8477 | -0.07 | 0.93 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 104.9492 | 104.9492 | -0.05 | 0.95 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:33 | 105.0586 | 105.0586 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:33 | 105.1602 | 105.1602 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 105.2578 | 105.2578 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 105.3594 | 105.3594 | -0.15 | 0.85 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 105.4609 | 105.4609 | -0.21 | 0.79 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 105.5703 | 105.5703 | -0.23 | 0.77 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:33 | 105.668 | 105.668 | -0.24 | 0.76 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 105.7695 | 105.7695 | -0.11 | 0.89 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 105.8789 | 105.8789 | -0.11 | 0.89 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 105.9805 | 105.9805 | -0.1 | 0.9 | -0.85 | 0.15 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 106.0781 | 106.0781 | -0.1 | 0.9 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 106.1875 | 106.1875 | -0.11 | 0.89 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 106.2891 | 106.2891 | -0.11 | 0.89 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 106.3906 | 106.3906 | -0.11 | 0.89 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 106.4883 | 106.4883 | -0.09 | 0.91 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 106.5977 | 106.5977 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 106.6992 | 106.6992 | -0.08 | 0.92 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:33 | 106.8008 | 106.8008 | -0.12 | 0.88 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:33 | 106.8984 | 106.8984 | -0.23 | 0.77 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 107.0078 | 107.0078 | -0.26 | 0.74 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:33 | 107.1094 | 107.1094 | -0.26 | 0.74 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 27.34
2019-10-01 | 9:33 | 107.2109 | 107.2109 | -0.12 | 0.88 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:33 | 107.3203 | 107.3203 | -0.1 | 0.9 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 107.418 | 107.418 | -0.09 | 0.91 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 107.5195 | 107.5195 | -0.07 | 0.93 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:33 | 107.6211 | 107.6211 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 107.7305 | 107.7305 | -0.08 | 0.92 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 107.8281 | 107.8281 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 9:33 | 107.9297 | 107.9297 | -0.08 | 0.92 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 108.0313 | 108.0313 | -0.09 | 0.91 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 108.1406 | 108.1406 | -0.07 | 0.93 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 108.2383 | 108.2383 | -0.09 | 0.91 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 108.3477 | 108.3477 | -0.13 | 0.87 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 108.4492 | 108.4492 | -0.23 | 0.77 | -0.73 | 0.27 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 108.5508 | 108.5508 | -0.23 | 0.77 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 108.6484 | 108.6484 | -0.25 | 0.75 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 108.75 | 108.75 | -0.1 | 0.9 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 108.8594 | 108.8594 | -0.09 | 0.91 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 108.9609 | 108.9609 | -0.11 | 0.89 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 109.0586 | 109.0586 | -0.1 | 0.9 | -0.84 | 0.16 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:33 | 109.1602 | 109.1602 | -0.11 | 0.89 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 109.2695 | 109.2695 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 109.3711 | 109.3711 | -0.1 | 0.9 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 109.4688 | 109.4688 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 109.5781 | 109.5781 | -0.1 | 0.9 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 109.6875 | 109.6875 | -0.12 | 0.88 | -0.82 | 0.18 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:33 | 109.7813 | 109.7813 | -0.1 | 0.9 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:33 | 109.8906 | 109.8906 | -0.2 | 0.8 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 109.9883 | 109.9883 | -0.28 | 0.72 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:33 | 110.0898 | 110.0898 | -0.28 | 0.72 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 110.1875 | 110.1875 | -0.16 | 0.84 | -0.82 | 0.18 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:33 | 110.2891 | 110.2891 | -0.12 | 0.88 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 110.3984 | 110.3984 | -0.11 | 0.89 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 110.5 | 110.5 | -0.1 | 0.9 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 23.44
2019-10-01 | 9:33 | 110.6094 | 110.6094 | -0.12 | 0.88 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:33 | 110.7109 | 110.7109 | -0.11 | 0.89 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:33 | 110.8086 | 110.8086 | -0.09 | 0.91 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 110.9102 | 110.9102 | -0.1 | 0.9 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 111.0195 | 111.0195 | -0.1 | 0.9 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 111.1211 | 111.1211 | -0.11 | 0.89 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 111.2188 | 111.2188 | -0.12 | 0.88 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:33 | 111.3203 | 111.3203 | -0.13 | 0.87 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:33 | 111.4297 | 111.4297 | -0.25 | 0.75 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:33 | 111.5313 | 111.5313 | -0.27 | 0.73 | -0.72 | 0.28 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 111.6289 | 111.6289 | -0.27 | 0.73 | -0.72 | 0.28 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:33 | 111.7383 | 111.7383 | -0.14 | 0.86 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:33 | 111.8398 | 111.8398 | -0.12 | 0.88 | -0.83 | 0.17 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:33 | 111.9375 | 111.9375 | -0.11 | 0.89 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 112.0391 | 112.0391 | -0.12 | 0.88 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:33 | 112.1484 | 112.1484 | -0.12 | 0.88 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 112.25 | 112.25 | -0.11 | 0.89 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:33 | 112.3477 | 112.3477 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:33 | 112.4492 | 112.4492 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 23.44
2019-10-01 | 9:33 | 112.5586 | 112.5586 | -0.09 | 0.91 | -0.82 | 0.18 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:33 | 112.6602 | 112.6602 | -0.11 | 0.89 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 112.7578 | 112.7578 | -0.11 | 0.89 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:33 | 112.8711 | 112.8711 | -0.18 | 0.82 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 23.44
2019-10-01 | 9:33 | 112.9688 | 112.9688 | -0.28 | 0.72 | -0.71 | 0.29 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:33 | 113.0703 | 113.0703 | -0.3 | 0.7 | -0.69 | 0.31 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:33 | 113.168 | 113.168 | -0.31 | 0.69 | -0.7 | 0.3 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:33 | 113.2813 | 113.2813 | -0.15 | 0.85 | -0.83 | 0.17 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 9:33 | 113.3789 | 113.3789 | -0.14 | 0.86 | -0.83 | 0.17 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:34 | 113.4805 | 113.4805 | -0.14 | 0.86 | -0.82 | 0.18 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 113.5781 | 113.5781 | -0.12 | 0.88 | -0.82 | 0.18 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:34 | 113.6875 | 113.6875 | -0.13 | 0.87 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 113.7891 | 113.7891 | -0.11 | 0.89 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:34 | 113.8906 | 113.8906 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 114 | 114 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 114.0977 | 114.0977 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 114.1992 | 114.1992 | -0.1 | 0.9 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:34 | 114.3008 | 114.3008 | -0.12 | 0.88 | -0.81 | 0.19 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 9:34 | 114.4102 | 114.4102 | -0.23 | 0.77 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 114.5078 | 114.5078 | -0.29 | 0.71 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 114.6094 | 114.6094 | -0.29 | 0.71 | -0.68 | 0.32 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 114.7188 | 114.7188 | -0.17 | 0.83 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 114.8203 | 114.8203 | -0.12 | 0.88 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 114.918 | 114.918 | -0.12 | 0.88 | -0.82 | 0.18 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:34 | 115.0195 | 115.0195 | -0.12 | 0.88 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 115.1289 | 115.1289 | -0.12 | 0.88 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 115.2305 | 115.2305 | -0.11 | 0.89 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 115.3281 | 115.3281 | -0.12 | 0.88 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 115.4375 | 115.4375 | -0.09 | 0.91 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 115.5391 | 115.5391 | -0.11 | 0.89 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:34 | 115.6406 | 115.6406 | -0.12 | 0.88 | -0.82 | 0.18 | -0.69 | 0.31 | 74.22 | 25.39
2019-10-01 | 9:34 | 115.7383 | 115.7383 | -0.12 | 0.88 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:34 | 115.8398 | 115.8398 | -0.17 | 0.83 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 115.9492 | 115.9492 | -0.27 | 0.73 | -0.7 | 0.3 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 116.0508 | 116.0508 | -0.28 | 0.72 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:34 | 116.1484 | 116.1484 | -0.28 | 0.72 | -0.69 | 0.31 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:34 | 116.2578 | 116.2578 | -0.14 | 0.86 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 116.3594 | 116.3594 | -0.12 | 0.88 | -0.82 | 0.18 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:34 | 116.4609 | 116.4609 | -0.12 | 0.88 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 116.5703 | 116.5703 | -0.12 | 0.88 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 116.668 | 116.668 | -0.11 | 0.89 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 116.7695 | 116.7695 | -0.09 | 0.91 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 116.8711 | 116.8711 | -0.09 | 0.91 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 116.9805 | 116.9805 | -0.1 | 0.9 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 117.0781 | 117.0781 | -0.1 | 0.9 | -0.82 | 0.18 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:34 | 117.1797 | 117.1797 | -0.11 | 0.89 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 117.2813 | 117.2813 | -0.12 | 0.88 | -0.81 | 0.19 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 117.3906 | 117.3906 | -0.24 | 0.76 | -0.72 | 0.28 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 117.4883 | 117.4883 | -0.27 | 0.73 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 117.5898 | 117.5898 | -0.28 | 0.72 | -0.69 | 0.31 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 117.6992 | 117.6992 | -0.18 | 0.82 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 117.8008 | 117.8008 | -0.14 | 0.86 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 117.8984 | 117.8984 | -0.11 | 0.89 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 118 | 118 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:34 | 118.1094 | 118.1094 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 118.2109 | 118.2109 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 118.3086 | 118.3086 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 118.4102 | 118.4102 | -0.11 | 0.89 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 118.5195 | 118.5195 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 118.6211 | 118.6211 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:34 | 118.7305 | 118.7305 | -0.1 | 0.9 | -0.81 | 0.19 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 9:34 | 118.8281 | 118.8281 | -0.15 | 0.85 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:34 | 118.9297 | 118.9297 | -0.28 | 0.72 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 119.0313 | 119.0313 | -0.25 | 0.75 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:34 | 119.1289 | 119.1289 | -0.28 | 0.72 | -0.69 | 0.31 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 119.2383 | 119.2383 | -0.14 | 0.86 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:34 | 119.3398 | 119.3398 | -0.11 | 0.89 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 119.4375 | 119.4375 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 119.5391 | 119.5391 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 119.6484 | 119.6484 | -0.09 | 0.91 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 119.75 | 119.75 | -0.08 | 0.92 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 119.8594 | 119.8594 | -0.09 | 0.91 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:34 | 119.9609 | 119.9609 | -0.09 | 0.91 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:34 | 120.0586 | 120.0586 | -0.09 | 0.91 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 120.1602 | 120.1602 | -0.09 | 0.91 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 120.2578 | 120.2578 | -0.09 | 0.91 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 120.3711 | 120.3711 | -0.18 | 0.82 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 120.4688 | 120.4688 | -0.26 | 0.74 | -0.68 | 0.32 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 120.5703 | 120.5703 | -0.28 | 0.72 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:34 | 120.668 | 120.668 | -0.29 | 0.71 | -0.67 | 0.33 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 9:34 | 120.7813 | 120.7813 | -0.13 | 0.87 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 120.8789 | 120.8789 | -0.13 | 0.87 | -0.82 | 0.18 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 120.9883 | 120.9883 | -0.11 | 0.89 | -0.81 | 0.19 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 121.0898 | 121.0898 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 121.1875 | 121.1875 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:34 | 121.2891 | 121.2891 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:34 | 121.3984 | 121.3984 | -0.09 | 0.91 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 121.5 | 121.5 | -0.09 | 0.91 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 121.5977 | 121.5977 | -0.1 | 0.9 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 121.7109 | 121.7109 | -0.09 | 0.91 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 121.8086 | 121.8086 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 121.9102 | 121.9102 | -0.23 | 0.77 | -0.7 | 0.3 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 122.0078 | 122.0078 | -0.28 | 0.72 | -0.66 | 0.34 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:34 | 122.1211 | 122.1211 | -0.29 | 0.71 | -0.66 | 0.34 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:34 | 122.2188 | 122.2188 | -0.18 | 0.82 | -0.79 | 0.21 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 122.3203 | 122.3203 | -0.13 | 0.87 | -0.8 | 0.2 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 122.418 | 122.418 | -0.13 | 0.87 | -0.8 | 0.2 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 122.5313 | 122.5313 | -0.13 | 0.87 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 122.6289 | 122.6289 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 122.7305 | 122.7305 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 122.8281 | 122.8281 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 122.9375 | 122.9375 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 123.0391 | 123.0391 | -0.12 | 0.88 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 123.1406 | 123.1406 | -0.13 | 0.87 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-10-01 | 9:34 | 123.25 | 123.25 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 123.3477 | 123.3477 | -0.19 | 0.81 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 123.4492 | 123.4492 | -0.28 | 0.72 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:34 | 123.5586 | 123.5586 | -0.29 | 0.71 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:34 | 123.6602 | 123.6602 | -0.3 | 0.7 | -0.68 | 0.32 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:34 | 123.7578 | 123.7578 | -0.14 | 0.86 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 123.8594 | 123.8594 | -0.13 | 0.87 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 123.9609 | 123.9609 | -0.12 | 0.88 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 124.0703 | 124.0703 | -0.12 | 0.88 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:34 | 124.168 | 124.168 | -0.12 | 0.88 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 124.2695 | 124.2695 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 124.3711 | 124.3711 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 124.4805 | 124.4805 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 124.5781 | 124.5781 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 124.6797 | 124.6797 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 124.7891 | 124.7891 | -0.09 | 0.91 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 124.8906 | 124.8906 | -0.22 | 0.78 | -0.71 | 0.29 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:34 | 124.9883 | 124.9883 | -0.27 | 0.73 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 125.0898 | 125.0898 | -0.27 | 0.73 | -0.68 | 0.32 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:34 | 125.1992 | 125.1992 | -0.2 | 0.8 | -0.73 | 0.27 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:34 | 125.3008 | 125.3008 | -0.13 | 0.87 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 125.3984 | 125.3984 | -0.12 | 0.88 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:34 | 125.5 | 125.5 | -0.12 | 0.88 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:34 | 125.6094 | 125.6094 | -0.12 | 0.88 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 125.7188 | 125.7188 | -0.1 | 0.9 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 125.8086 | 125.8086 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 125.918 | 125.918 | -0.1 | 0.9 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:34 | 126.0195 | 126.0195 | -0.09 | 0.91 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 9:34 | 126.1211 | 126.1211 | -0.09 | 0.91 | -0.8 | 0.2 | -0.68 | 0.32 | 75.2 | 26.37
2019-10-01 | 9:34 | 126.2305 | 126.2305 | -0.1 | 0.9 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:34 | 126.3281 | 126.3281 | -0.13 | 0.87 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 126.4297 | 126.4297 | -0.25 | 0.75 | -0.69 | 0.31 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 126.5313 | 126.5313 | -0.28 | 0.72 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 126.6289 | 126.6289 | -0.28 | 0.72 | -0.65 | 0.35 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:34 | 126.7383 | 126.7383 | -0.15 | 0.85 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 126.8398 | 126.8398 | -0.11 | 0.89 | -0.8 | 0.2 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:34 | 126.9492 | 126.9492 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:34 | 127.0508 | 127.0508 | -0.1 | 0.9 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 127.1484 | 127.1484 | -0.11 | 0.89 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 127.25 | 127.25 | -0.11 | 0.89 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 127.3594 | 127.3594 | -0.11 | 0.89 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 127.4609 | 127.4609 | -0.11 | 0.89 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 127.5586 | 127.5586 | -0.12 | 0.88 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 127.6602 | 127.6602 | -0.12 | 0.88 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:34 | 127.7578 | 127.7578 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 127.8711 | 127.8711 | -0.19 | 0.81 | -0.74 | 0.26 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 127.9688 | 127.9688 | -0.28 | 0.72 | -0.68 | 0.32 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 128.0781 | 128.0781 | -0.28 | 0.72 | -0.66 | 0.34 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:34 | 128.1797 | 128.1797 | -0.31 | 0.69 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:34 | 128.2813 | 128.2813 | -0.15 | 0.85 | -0.79 | 0.21 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:34 | 128.3789 | 128.3789 | -0.14 | 0.86 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 128.4883 | 128.4883 | -0.13 | 0.87 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 128.5898 | 128.5898 | -0.12 | 0.88 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 128.6875 | 128.6875 | -0.12 | 0.88 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:34 | 128.7891 | 128.7891 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 128.8984 | 128.8984 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 129 | 129 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 129.0977 | 129.0977 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 129.2109 | 129.2109 | -0.13 | 0.87 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 129.3086 | 129.3086 | -0.13 | 0.87 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 9:34 | 129.4102 | 129.4102 | -0.23 | 0.77 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 129.5078 | 129.5078 | -0.28 | 0.72 | -0.65 | 0.35 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:34 | 129.6211 | 129.6211 | -0.28 | 0.72 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 129.7188 | 129.7188 | -0.15 | 0.85 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 129.8203 | 129.8203 | -0.13 | 0.87 | -0.79 | 0.21 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 129.918 | 129.918 | -0.12 | 0.88 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 130.0313 | 130.0313 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 130.1289 | 130.1289 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 130.2305 | 130.2305 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 130.3398 | 130.3398 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 130.4375 | 130.4375 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 130.5391 | 130.5391 | -0.12 | 0.88 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 130.6406 | 130.6406 | -0.09 | 0.91 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:34 | 130.75 | 130.75 | -0.09 | 0.91 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 130.8477 | 130.8477 | -0.16 | 0.84 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 130.9492 | 130.9492 | -0.26 | 0.74 | -0.68 | 0.32 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 131.0508 | 131.0508 | -0.28 | 0.72 | -0.66 | 0.34 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 131.1602 | 131.1602 | -0.29 | 0.71 | -0.65 | 0.35 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 131.2578 | 131.2578 | -0.13 | 0.87 | -0.79 | 0.21 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:34 | 131.3594 | 131.3594 | -0.14 | 0.86 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 131.4688 | 131.4688 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 131.5703 | 131.5703 | -0.11 | 0.89 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 131.668 | 131.668 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 131.7695 | 131.7695 | -0.1 | 0.9 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 9:34 | 131.8789 | 131.8789 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 131.9805 | 131.9805 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:34 | 132.0781 | 132.0781 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 132.1797 | 132.1797 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 132.2891 | 132.2891 | -0.1 | 0.9 | -0.8 | 0.2 | -0.69 | 0.31 | 72.27 | 24.41
2019-10-01 | 9:34 | 132.3906 | 132.3906 | -0.18 | 0.82 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 132.4883 | 132.4883 | -0.26 | 0.74 | -0.66 | 0.34 | -0.66 | 0.34 | 74.22 | 27.34
2019-10-01 | 9:34 | 132.5977 | 132.5977 | -0.29 | 0.71 | -0.66 | 0.34 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:34 | 132.6992 | 132.6992 | -0.22 | 0.78 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 132.8008 | 132.8008 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 132.9102 | 132.9102 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:34 | 133.0078 | 133.0078 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:34 | 133.1094 | 133.1094 | -0.09 | 0.91 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:34 | 133.2109 | 133.2109 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 133.3203 | 133.3203 | -0.1 | 0.9 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 133.418 | 133.418 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 133.5195 | 133.5195 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 133.6211 | 133.6211 | -0.1 | 0.9 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 133.7305 | 133.7305 | -0.09 | 0.91 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 133.8281 | 133.8281 | -0.12 | 0.88 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 133.9297 | 133.9297 | -0.23 | 0.77 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 134.0391 | 134.0391 | -0.25 | 0.75 | -0.65 | 0.35 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 134.1406 | 134.1406 | -0.27 | 0.73 | -0.65 | 0.35 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:34 | 134.2383 | 134.2383 | -0.12 | 0.88 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 134.3398 | 134.3398 | -0.1 | 0.9 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:34 | 134.4492 | 134.4492 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 134.5508 | 134.5508 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 134.6484 | 134.6484 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 134.75 | 134.75 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 134.8477 | 134.8477 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 134.9609 | 134.9609 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 135.0586 | 135.0586 | -0.08 | 0.92 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 135.168 | 135.168 | -0.1 | 0.9 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:34 | 135.2695 | 135.2695 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:34 | 135.3711 | 135.3711 | -0.17 | 0.83 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 135.4688 | 135.4688 | -0.27 | 0.73 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:34 | 135.5781 | 135.5781 | -0.28 | 0.72 | -0.65 | 0.35 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 135.6797 | 135.6797 | -0.29 | 0.71 | -0.64 | 0.36 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 9:34 | 135.7813 | 135.7813 | -0.12 | 0.88 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 135.8789 | 135.8789 | -0.13 | 0.87 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 135.9883 | 135.9883 | -0.12 | 0.88 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 136.0898 | 136.0898 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 136.1875 | 136.1875 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:34 | 136.3008 | 136.3008 | -0.09 | 0.91 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 136.3984 | 136.3984 | -0.09 | 0.91 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 136.5 | 136.5 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 136.5977 | 136.5977 | -0.1 | 0.9 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 136.7109 | 136.7109 | -0.08 | 0.92 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 136.8086 | 136.8086 | -0.1 | 0.9 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:34 | 136.9102 | 136.9102 | -0.23 | 0.77 | -0.68 | 0.32 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 137.0078 | 137.0078 | -0.25 | 0.75 | -0.65 | 0.35 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 137.1211 | 137.1211 | -0.26 | 0.74 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 137.2188 | 137.2188 | -0.14 | 0.86 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:34 | 137.3281 | 137.3281 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 137.4297 | 137.4297 | -0.11 | 0.89 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 137.5313 | 137.5313 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 137.6289 | 137.6289 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 9:34 | 137.7305 | 137.7305 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 137.8398 | 137.8398 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 137.9375 | 137.9375 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 138.0391 | 138.0391 | -0.11 | 0.89 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 138.1406 | 138.1406 | -0.1 | 0.9 | -0.79 | 0.21 | -0.68 | 0.32 | 75.2 | 25.39
2019-10-01 | 9:34 | 138.25 | 138.25 | -0.1 | 0.9 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 138.3477 | 138.3477 | -0.15 | 0.85 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 138.4609 | 138.4609 | -0.25 | 0.75 | -0.68 | 0.32 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 138.5586 | 138.5586 | -0.26 | 0.74 | -0.64 | 0.36 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:34 | 138.6602 | 138.6602 | -0.28 | 0.72 | -0.65 | 0.35 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 138.7578 | 138.7578 | -0.13 | 0.87 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 138.8711 | 138.8711 | -0.12 | 0.88 | -0.78 | 0.22 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:34 | 138.9688 | 138.9688 | -0.12 | 0.88 | -0.79 | 0.21 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 139.0703 | 139.0703 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 139.168 | 139.168 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 139.2813 | 139.2813 | -0.12 | 0.88 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 139.3789 | 139.3789 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 139.4805 | 139.4805 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 139.5898 | 139.5898 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 139.6992 | 139.6992 | -0.12 | 0.88 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 139.7891 | 139.7891 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 139.8906 | 139.8906 | -0.2 | 0.8 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 140 | 140 | -0.27 | 0.73 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 140.0977 | 140.0977 | -0.29 | 0.71 | -0.65 | 0.35 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 140.1992 | 140.1992 | -0.28 | 0.72 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 140.3008 | 140.3008 | -0.12 | 0.88 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 140.4102 | 140.4102 | -0.12 | 0.88 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 140.5078 | 140.5078 | -0.12 | 0.88 | -0.79 | 0.21 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:34 | 140.6094 | 140.6094 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:34 | 140.7188 | 140.7188 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 140.8203 | 140.8203 | -0.12 | 0.88 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:34 | 140.918 | 140.918 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 141.0195 | 141.0195 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 141.1289 | 141.1289 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 141.2305 | 141.2305 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 75.2 | 27.34
2019-10-01 | 9:34 | 141.3281 | 141.3281 | -0.15 | 0.85 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:34 | 141.4297 | 141.4297 | -0.24 | 0.76 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 141.5391 | 141.5391 | -0.29 | 0.71 | -0.64 | 0.36 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 141.6406 | 141.6406 | -0.28 | 0.72 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:34 | 141.7383 | 141.7383 | -0.14 | 0.86 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:34 | 141.8477 | 141.8477 | -0.11 | 0.89 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 141.9492 | 141.9492 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 142.0508 | 142.0508 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 142.1484 | 142.1484 | -0.08 | 0.92 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 9:34 | 142.2578 | 142.2578 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 142.3594 | 142.3594 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:34 | 142.4609 | 142.4609 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:34 | 142.5586 | 142.5586 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 142.668 | 142.668 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 142.7695 | 142.7695 | -0.1 | 0.9 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 9:34 | 142.8711 | 142.8711 | -0.18 | 0.82 | -0.72 | 0.28 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 142.9688 | 142.9688 | -0.24 | 0.76 | -0.66 | 0.34 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:34 | 143.0781 | 143.0781 | -0.25 | 0.75 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:34 | 143.1797 | 143.1797 | -0.28 | 0.72 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:34 | 143.2891 | 143.2891 | -0.12 | 0.88 | -0.77 | 0.23 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:34 | 143.3906 | 143.3906 | -0.1 | 0.9 | -0.78 | 0.22 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:34 | 143.4883 | 143.4883 | -0.1 | 0.9 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 143.5898 | 143.5898 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:34 | 143.6992 | 143.6992 | -0.09 | 0.91 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 143.8008 | 143.8008 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 143.8984 | 143.8984 | -0.07 | 0.93 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 144 | 144 | -0.09 | 0.91 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 9:34 | 144.1094 | 144.1094 | -0.1 | 0.9 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 144.2109 | 144.2109 | -0.09 | 0.91 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 144.3086 | 144.3086 | -0.1 | 0.9 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 144.418 | 144.418 | -0.23 | 0.77 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 144.5195 | 144.5195 | -0.29 | 0.71 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 144.6211 | 144.6211 | -0.29 | 0.71 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 144.7188 | 144.7188 | -0.17 | 0.83 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 144.8281 | 144.8281 | -0.14 | 0.86 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 144.9297 | 144.9297 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:34 | 145.0313 | 145.0313 | -0.11 | 0.89 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 145.1289 | 145.1289 | -0.1 | 0.9 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 145.2383 | 145.2383 | -0.1 | 0.9 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 145.3398 | 145.3398 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:34 | 145.4375 | 145.4375 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 145.5508 | 145.5508 | -0.08 | 0.92 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:34 | 145.6484 | 145.6484 | -0.08 | 0.92 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 145.75 | 145.75 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:34 | 145.8477 | 145.8477 | -0.11 | 0.89 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 145.9609 | 145.9609 | -0.24 | 0.76 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 146.0586 | 146.0586 | -0.27 | 0.73 | -0.63 | 0.37 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 146.1602 | 146.1602 | -0.28 | 0.72 | -0.63 | 0.37 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:34 | 146.2578 | 146.2578 | -0.14 | 0.86 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 146.3711 | 146.3711 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 146.4688 | 146.4688 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 146.5703 | 146.5703 | -0.09 | 0.91 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 146.6797 | 146.6797 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 146.7813 | 146.7813 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 146.8789 | 146.8789 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:34 | 146.9805 | 146.9805 | -0.1 | 0.9 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 9:34 | 147.0898 | 147.0898 | -0.11 | 0.89 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 147.1875 | 147.1875 | -0.1 | 0.9 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:34 | 147.2891 | 147.2891 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 27.34
2019-10-01 | 9:34 | 147.3906 | 147.3906 | -0.2 | 0.8 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 147.5 | 147.5 | -0.25 | 0.75 | -0.65 | 0.35 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 147.5977 | 147.5977 | -0.27 | 0.73 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 147.7109 | 147.7109 | -0.28 | 0.72 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:34 | 147.8086 | 147.8086 | -0.14 | 0.86 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 147.9102 | 147.9102 | -0.12 | 0.88 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 148.0078 | 148.0078 | -0.11 | 0.89 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 148.1094 | 148.1094 | -0.11 | 0.89 | -0.78 | 0.22 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:34 | 148.2188 | 148.2188 | -0.11 | 0.89 | -0.79 | 0.21 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:34 | 148.3203 | 148.3203 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 148.418 | 148.418 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 148.5195 | 148.5195 | -0.11 | 0.89 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 148.6289 | 148.6289 | -0.11 | 0.89 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:34 | 148.7305 | 148.7305 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 148.8398 | 148.8398 | -0.12 | 0.88 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 148.9375 | 148.9375 | -0.23 | 0.77 | -0.69 | 0.31 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 149.0391 | 149.0391 | -0.26 | 0.74 | -0.65 | 0.35 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:34 | 149.1406 | 149.1406 | -0.28 | 0.72 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:34 | 149.25 | 149.25 | -0.13 | 0.87 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 149.3477 | 149.3477 | -0.11 | 0.89 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:34 | 149.4492 | 149.4492 | -0.09 | 0.91 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 149.5586 | 149.5586 | -0.1 | 0.9 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 149.6484 | 149.6484 | -0.1 | 0.9 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 149.7578 | 149.7578 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 24.41
2019-10-01 | 9:34 | 149.8594 | 149.8594 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 149.9688 | 149.9688 | -0.08 | 0.92 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:34 | 150.0703 | 150.0703 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:34 | 150.168 | 150.168 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 150.2695 | 150.2695 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 150.3789 | 150.3789 | -0.17 | 0.83 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 150.4805 | 150.4805 | -0.25 | 0.75 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 150.5781 | 150.5781 | -0.27 | 0.73 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 9:34 | 150.6797 | 150.6797 | -0.28 | 0.72 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:34 | 150.7813 | 150.7813 | -0.12 | 0.88 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 150.8906 | 150.8906 | -0.11 | 0.89 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 150.9883 | 150.9883 | -0.11 | 0.89 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 151.0898 | 151.0898 | -0.1 | 0.9 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 151.1992 | 151.1992 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 23.44
2019-10-01 | 9:34 | 151.3008 | 151.3008 | -0.08 | 0.92 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 151.3984 | 151.3984 | -0.1 | 0.9 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:34 | 151.5078 | 151.5078 | -0.08 | 0.92 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:34 | 151.6094 | 151.6094 | -0.08 | 0.92 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 9:34 | 151.7109 | 151.7109 | -0.08 | 0.92 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 151.8086 | 151.8086 | -0.08 | 0.92 | -0.78 | 0.22 | -0.68 | 0.32 | 72.27 | 23.44
2019-10-01 | 9:34 | 151.918 | 151.918 | -0.2 | 0.8 | -0.69 | 0.31 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 152.0195 | 152.0195 | -0.24 | 0.76 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 152.1211 | 152.1211 | -0.25 | 0.75 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 152.2188 | 152.2188 | -0.14 | 0.86 | -0.7 | 0.3 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:34 | 152.3281 | 152.3281 | -0.1 | 0.9 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 152.4297 | 152.4297 | -0.09 | 0.91 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 152.5313 | 152.5313 | -0.09 | 0.91 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 152.6406 | 152.6406 | -0.08 | 0.92 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 152.7383 | 152.7383 | -0.08 | 0.92 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 152.8398 | 152.8398 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 152.9375 | 152.9375 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 153.0508 | 153.0508 | -0.08 | 0.92 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:34 | 153.1484 | 153.1484 | -0.07 | 0.93 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 153.25 | 153.25 | -0.09 | 0.91 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 153.3477 | 153.3477 | -0.1 | 0.9 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:34 | 153.4609 | 153.4609 | -0.21 | 0.79 | -0.67 | 0.33 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 153.5586 | 153.5586 | -0.26 | 0.74 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:34 | 153.6602 | 153.6602 | -0.29 | 0.71 | -0.63 | 0.37 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:34 | 153.7695 | 153.7695 | -0.16 | 0.84 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:34 | 153.8711 | 153.8711 | -0.13 | 0.87 | -0.77 | 0.23 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:34 | 153.9688 | 153.9688 | -0.13 | 0.87 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 154.0703 | 154.0703 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 154.1797 | 154.1797 | -0.11 | 0.89 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:34 | 154.2813 | 154.2813 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:34 | 154.3789 | 154.3789 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 154.4805 | 154.4805 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 154.5898 | 154.5898 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:34 | 154.6875 | 154.6875 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 154.7891 | 154.7891 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 154.8984 | 154.8984 | -0.15 | 0.85 | -0.74 | 0.26 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 155 | 155 | -0.22 | 0.78 | -0.68 | 0.32 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:34 | 155.0977 | 155.0977 | -0.26 | 0.74 | -0.63 | 0.37 | -0.66 | 0.34 | 73.24 | 25.39 | BREAK 1
2019-10-01 | 9:34 | 1.0586 | 156.1563 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 1.1602 | 156.2579 | -0.08 | 0.92 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 26.37
2019-10-01 | 9:34 | 1.2617 | 156.3594 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 1.3711 | 156.4688 | -0.18 | 0.82 | -0.7 | 0.3 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:34 | 1.4805 | 156.5782 | -0.24 | 0.76 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 1.5703 | 156.668 | -0.27 | 0.73 | -0.62 | 0.38 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:34 | 1.6719 | 156.7696 | -0.25 | 0.75 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:34 | 1.7812 | 156.879 | -0.1 | 0.9 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 1.8789 | 156.9766 | -0.1 | 0.9 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:34 | 1.9805 | 157.0782 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:34 | 2.082 | 157.1797 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 2.1914 | 157.2891 | -0.08 | 0.92 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:34 | 2.2891 | 157.3868 | -0.07 | 0.93 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:34 | 2.3906 | 157.4883 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 23.44
2019-10-01 | 9:34 | 2.5 | 157.5977 | -0.06 | 0.94 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 2.6016 | 157.6993 | -0.07 | 0.93 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:34 | 2.6992 | 157.7969 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:34 | 2.8008 | 157.8985 | -0.1 | 0.9 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 23.44
2019-10-01 | 9:34 | 2.9102 | 158.0079 | -0.21 | 0.79 | -0.66 | 0.34 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:34 | 3.0117 | 158.1094 | -0.26 | 0.74 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 23.44
2019-10-01 | 9:34 | 3.1094 | 158.2071 | -0.26 | 0.74 | -0.63 | 0.37 | -0.63 | 0.37 | 75.2 | 25.39
2019-10-01 | 9:34 | 3.2109 | 158.3086 | -0.12 | 0.88 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:34 | 3.3203 | 158.418 | -0.11 | 0.89 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 3.4219 | 158.5196 | -0.09 | 0.91 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:34 | 3.5195 | 158.6172 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:34 | 3.6289 | 158.7266 | -0.1 | 0.9 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 3.7305 | 158.8282 | -0.1 | 0.9 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 3.832 | 158.9297 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 3.9297 | 159.0274 | -0.1 | 0.9 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:34 | 4.0391 | 159.1368 | -0.09 | 0.91 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:34 | 4.1406 | 159.2383 | -0.09 | 0.91 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:34 | 4.2422 | 159.3399 | -0.1 | 0.9 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:34 | 4.3398 | 159.4375 | -0.14 | 0.86 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 4.4492 | 159.5469 | -0.24 | 0.76 | -0.64 | 0.36 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:35 | 4.5508 | 159.6485 | -0.27 | 0.73 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 4.6602 | 159.7579 | -0.27 | 0.73 | -0.6 | 0.4 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:35 | 4.7617 | 159.8594 | -0.11 | 0.89 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 4.8594 | 159.9571 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 4.9609 | 160.0586 | -0.09 | 0.91 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 5.0586 | 160.1563 | -0.09 | 0.91 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 5.1719 | 160.2696 | -0.08 | 0.92 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 5.2695 | 160.3672 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 5.3711 | 160.4688 | -0.07 | 0.93 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 5.4688 | 160.5665 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:35 | 5.582 | 160.6797 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 5.6797 | 160.7774 | -0.07 | 0.93 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 23.44
2019-10-01 | 9:35 | 5.7891 | 160.8868 | -0.07 | 0.93 | -0.78 | 0.22 | -0.69 | 0.31 | 75.2 | 26.37
2019-10-01 | 9:35 | 5.8906 | 160.9883 | -0.19 | 0.81 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 5.9922 | 161.0899 | -0.22 | 0.78 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 6.0898 | 161.1875 | -0.23 | 0.77 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 6.1992 | 161.2969 | -0.11 | 0.89 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 6.3008 | 161.3985 | -0.09 | 0.91 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 6.4023 | 161.5 | -0.08 | 0.92 | -0.77 | 0.23 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:35 | 6.5 | 161.5977 | -0.08 | 0.92 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 6.6094 | 161.7071 | -0.08 | 0.92 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 6.7109 | 161.8086 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:35 | 6.8086 | 161.9063 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 25.39
2019-10-01 | 9:35 | 6.9219 | 162.0196 | -0.08 | 0.92 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 7.0195 | 162.1172 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 7.1211 | 162.2188 | -0.08 | 0.92 | -0.79 | 0.21 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 9:35 | 7.2188 | 162.3165 | -0.08 | 0.92 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:35 | 7.332 | 162.4297 | -0.12 | 0.88 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 7.4297 | 162.5274 | -0.24 | 0.76 | -0.66 | 0.34 | -0.67 | 0.33 | 73.24 | 23.44
2019-10-01 | 9:35 | 7.5312 | 162.629 | -0.26 | 0.74 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:35 | 7.6289 | 162.7266 | -0.27 | 0.73 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 23.44
2019-10-01 | 9:35 | 7.7422 | 162.8399 | -0.11 | 0.89 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 7.8398 | 162.9375 | -0.09 | 0.91 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:35 | 7.9414 | 163.0391 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 8.0508 | 163.1485 | -0.08 | 0.92 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:35 | 8.1523 | 163.25 | -0.07 | 0.93 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 8.25 | 163.3477 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 8.3516 | 163.4493 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 8.4609 | 163.5586 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 8.5586 | 163.6563 | -0.07 | 0.93 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:35 | 8.6602 | 163.7579 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 8.7617 | 163.8594 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 8.8711 | 163.9688 | -0.15 | 0.85 | -0.72 | 0.28 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 8.9688 | 164.0665 | -0.23 | 0.77 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 9.0703 | 164.168 | -0.24 | 0.76 | -0.62 | 0.38 | -0.65 | 0.35 | 76.17 | 25.39
2019-10-01 | 9:35 | 9.1719 | 164.2696 | -0.24 | 0.76 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 9.2812 | 164.379 | -0.11 | 0.89 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 9.3789 | 164.4766 | -0.1 | 0.9 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:35 | 9.4805 | 164.5782 | -0.1 | 0.9 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 9.5898 | 164.6875 | -0.09 | 0.91 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 9.6914 | 164.7891 | -0.08 | 0.92 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 9.7891 | 164.8868 | -0.09 | 0.91 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 9.8906 | 164.9883 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 23.44
2019-10-01 | 9:35 | 10 | 165.0977 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 10.1016 | 165.1993 | -0.08 | 0.92 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 23.44
2019-10-01 | 9:35 | 10.1992 | 165.2969 | -0.07 | 0.93 | -0.79 | 0.21 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:35 | 10.3008 | 165.3985 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 10.4102 | 165.5079 | -0.21 | 0.79 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 10.5117 | 165.6094 | -0.24 | 0.76 | -0.63 | 0.37 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 10.6211 | 165.7188 | -0.25 | 0.75 | -0.62 | 0.38 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 10.7188 | 165.8165 | -0.11 | 0.89 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:35 | 10.8203 | 165.918 | -0.09 | 0.91 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:35 | 10.9219 | 166.0196 | -0.09 | 0.91 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 11.0195 | 166.1172 | -0.08 | 0.92 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 11.1289 | 166.2266 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 11.2305 | 166.3282 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 76.17 | 26.37
2019-10-01 | 9:35 | 11.332 | 166.4297 | -0.06 | 0.94 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:35 | 11.4297 | 166.5274 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 11.5391 | 166.6368 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 24.41
2019-10-01 | 9:35 | 11.6406 | 166.7383 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 75.2 | 26.37
2019-10-01 | 9:35 | 11.75 | 166.8477 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 11.8516 | 166.9493 | -0.14 | 0.86 | -0.71 | 0.29 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 11.9492 | 167.0469 | -0.23 | 0.77 | -0.63 | 0.37 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:35 | 12.0508 | 167.1485 | -0.24 | 0.76 | -0.62 | 0.38 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:35 | 12.1602 | 167.2579 | -0.26 | 0.74 | -0.62 | 0.38 | -0.64 | 0.36 | 75.2 | 26.37
2019-10-01 | 9:35 | 12.2617 | 167.3594 | -0.1 | 0.9 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 12.3594 | 167.4571 | -0.09 | 0.91 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 12.4609 | 167.5586 | -0.1 | 0.9 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 12.5586 | 167.6563 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 12.6719 | 167.7696 | -0.1 | 0.9 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 12.7695 | 167.8672 | -0.09 | 0.91 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 12.8789 | 167.9766 | -0.09 | 0.91 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 12.9805 | 168.0782 | -0.08 | 0.92 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 13.082 | 168.1797 | -0.09 | 0.91 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 13.1797 | 168.2774 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 13.2891 | 168.3868 | -0.1 | 0.9 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:35 | 13.3906 | 168.4883 | -0.22 | 0.78 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 13.4922 | 168.5899 | -0.26 | 0.74 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 13.5898 | 168.6875 | -0.27 | 0.73 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 13.6992 | 168.7969 | -0.16 | 0.84 | -0.72 | 0.28 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:35 | 13.8008 | 168.8985 | -0.11 | 0.89 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 13.9023 | 169 | -0.09 | 0.91 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 14.0117 | 169.1094 | -0.09 | 0.91 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 14.1094 | 169.2071 | -0.09 | 0.91 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 14.2109 | 169.3086 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:35 | 14.3086 | 169.4063 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 14.4219 | 169.5196 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 14.5195 | 169.6172 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 14.6211 | 169.7188 | -0.06 | 0.94 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 14.7188 | 169.8165 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:35 | 14.832 | 169.9297 | -0.08 | 0.92 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:35 | 14.9297 | 170.0274 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 15.0312 | 170.129 | -0.22 | 0.78 | -0.62 | 0.38 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 15.1406 | 170.2383 | -0.22 | 0.78 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 15.2422 | 170.3399 | -0.1 | 0.9 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 15.3398 | 170.4375 | -0.09 | 0.91 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 15.4414 | 170.5391 | -0.08 | 0.92 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 15.5508 | 170.6485 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 15.6523 | 170.75 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 15.75 | 170.8477 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 15.8516 | 170.9493 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 15.9609 | 171.0586 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 16.0586 | 171.1563 | -0.07 | 0.93 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 16.1602 | 171.2579 | -0.07 | 0.93 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 16.2695 | 171.3672 | -0.06 | 0.94 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 16.3711 | 171.4688 | -0.15 | 0.85 | -0.7 | 0.3 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:35 | 16.4688 | 171.5665 | -0.23 | 0.77 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 16.5703 | 171.668 | -0.26 | 0.74 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 16.6797 | 171.7774 | -0.27 | 0.73 | -0.66 | 0.34 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:35 | 16.7812 | 171.879 | -0.12 | 0.88 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 16.8789 | 171.9766 | -0.1 | 0.9 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 16.9805 | 172.0782 | -0.1 | 0.9 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 17.0898 | 172.1875 | -0.09 | 0.91 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 17.1914 | 172.2891 | -0.09 | 0.91 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 17.2891 | 172.3868 | -0.08 | 0.92 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 17.4023 | 172.5 | -0.09 | 0.91 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 17.5 | 172.5977 | -0.06 | 0.94 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:35 | 17.6016 | 172.6993 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 23.44
2019-10-01 | 9:35 | 17.7109 | 172.8086 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 17.8086 | 172.9063 | -0.09 | 0.91 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 17.9102 | 173.0079 | -0.21 | 0.79 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 18.0117 | 173.1094 | -0.25 | 0.75 | -0.61 | 0.39 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 18.1133 | 173.211 | -0.26 | 0.74 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 18.2227 | 173.3204 | -0.11 | 0.89 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 18.3203 | 173.418 | -0.1 | 0.9 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 18.4219 | 173.5196 | -0.09 | 0.91 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 18.5312 | 173.629 | -0.08 | 0.92 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 18.6328 | 173.7305 | -0.08 | 0.92 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 18.7305 | 173.8282 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 23.44
2019-10-01 | 9:35 | 18.8398 | 173.9375 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 18.9414 | 174.0391 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:35 | 19.043 | 174.1407 | -0.08 | 0.92 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:35 | 19.1406 | 174.2383 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 19.25 | 174.3477 | -0.07 | 0.93 | -0.78 | 0.22 | -0.69 | 0.31 | 74.22 | 25.39
2019-10-01 | 9:35 | 19.3516 | 174.4493 | -0.15 | 0.85 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 19.4531 | 174.5508 | -0.2 | 0.8 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 19.5508 | 174.6485 | -0.23 | 0.77 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 19.6602 | 174.7579 | -0.24 | 0.76 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 19.7617 | 174.8594 | -0.1 | 0.9 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 19.8633 | 174.961 | -0.09 | 0.91 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 19.9727 | 175.0704 | -0.08 | 0.92 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 20.0703 | 175.168 | -0.08 | 0.92 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 20.1719 | 175.2696 | -0.08 | 0.92 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 20.2695 | 175.3672 | -0.08 | 0.92 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 20.3828 | 175.4805 | -0.08 | 0.92 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 20.4805 | 175.5782 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 20.582 | 175.6797 | -0.06 | 0.94 | -0.78 | 0.22 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:35 | 20.6797 | 175.7774 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 20.793 | 175.8907 | -0.08 | 0.92 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 23.44
2019-10-01 | 9:35 | 20.8906 | 175.9883 | -0.17 | 0.83 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 20.9922 | 176.0899 | -0.23 | 0.77 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 21.1016 | 176.1993 | -0.24 | 0.76 | -0.62 | 0.38 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 21.2031 | 176.3008 | -0.16 | 0.84 | -0.67 | 0.33 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:35 | 21.3008 | 176.3985 | -0.08 | 0.92 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 21.4023 | 176.5 | -0.07 | 0.93 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 21.5117 | 176.6094 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 21.6133 | 176.711 | -0.07 | 0.93 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 23.44
2019-10-01 | 9:35 | 21.7109 | 176.8086 | -0.07 | 0.93 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 21.8125 | 176.9102 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 21.9219 | 177.0196 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 22.0195 | 177.1172 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 22.1328 | 177.2305 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 22.2305 | 177.3282 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 22.332 | 177.4297 | -0.08 | 0.92 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 22.4297 | 177.5274 | -0.21 | 0.79 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 22.5312 | 177.629 | -0.24 | 0.76 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 22.6406 | 177.7383 | -0.23 | 0.77 | -0.63 | 0.37 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 22.7422 | 177.8399 | -0.09 | 0.91 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 22.8398 | 177.9375 | -0.08 | 0.92 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 22.9414 | 178.0391 | -0.08 | 0.92 | -0.75 | 0.25 | -0.65 | 0.35 | 72.27 | 23.44
2019-10-01 | 9:35 | 23.0508 | 178.1485 | -0.07 | 0.93 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 23.1523 | 178.25 | -0.06 | 0.94 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 23.2617 | 178.3594 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 23.3633 | 178.461 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:35 | 23.4609 | 178.5586 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 23.5625 | 178.6602 | -0.07 | 0.93 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:35 | 23.6719 | 178.7696 | -0.05 | 0.95 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 9:35 | 23.7695 | 178.8672 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 23.8711 | 178.9688 | -0.11 | 0.89 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 23.9727 | 179.0704 | -0.21 | 0.79 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 24.0703 | 179.168 | -0.23 | 0.77 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 23.44
2019-10-01 | 9:35 | 24.1797 | 179.2774 | -0.24 | 0.76 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 24.2812 | 179.379 | -0.08 | 0.92 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 24.3906 | 179.4883 | -0.08 | 0.92 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 24.4922 | 179.5899 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 24.5898 | 179.6875 | -0.06 | 0.94 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 24.6914 | 179.7891 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 24.8008 | 179.8985 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 24.9023 | 180 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 25 | 180.0977 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 25.1016 | 180.1993 | -0.08 | 0.92 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:35 | 25.2109 | 180.3086 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 25.3125 | 180.4102 | -0.08 | 0.92 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:35 | 25.4102 | 180.5079 | -0.19 | 0.81 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 25.5117 | 180.6094 | -0.22 | 0.78 | -0.63 | 0.37 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 25.6211 | 180.7188 | -0.22 | 0.78 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 25.7227 | 180.8204 | -0.11 | 0.89 | -0.72 | 0.28 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 25.8203 | 180.918 | -0.07 | 0.93 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 25.9297 | 181.0274 | -0.08 | 0.92 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 26.0312 | 181.129 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 26.1328 | 181.2305 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 26.2305 | 181.3282 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 26.3398 | 181.4375 | -0.06 | 0.94 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 23.44
2019-10-01 | 9:35 | 26.4414 | 181.5391 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 26.543 | 181.6407 | -0.06 | 0.94 | -0.78 | 0.22 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:35 | 26.6406 | 181.7383 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 9:35 | 26.75 | 181.8477 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 26.8516 | 181.9493 | -0.11 | 0.89 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 26.9531 | 182.0508 | -0.2 | 0.8 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 27.0625 | 182.1602 | -0.24 | 0.76 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 27.1602 | 182.2579 | -0.24 | 0.76 | -0.6 | 0.4 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 27.2617 | 182.3594 | -0.09 | 0.91 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 27.3633 | 182.461 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 27.4727 | 182.5704 | -0.07 | 0.93 | -0.76 | 0.24 | -0.64 | 0.36 | 73.24 | 23.44
2019-10-01 | 9:35 | 27.5703 | 182.668 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 27.6719 | 182.7696 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 27.7695 | 182.8672 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 27.8828 | 182.9805 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:35 | 27.9805 | 183.0782 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:35 | 28.0898 | 183.1875 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 28.1914 | 183.2891 | -0.05 | 0.95 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:35 | 28.293 | 183.3907 | -0.06 | 0.94 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 28.3906 | 183.4883 | -0.16 | 0.84 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 28.4922 | 183.5899 | -0.22 | 0.78 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 28.6016 | 183.6993 | -0.22 | 0.78 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 28.7031 | 183.8008 | -0.17 | 0.83 | -0.66 | 0.34 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:35 | 28.8008 | 183.8985 | -0.09 | 0.91 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 23.44
2019-10-01 | 9:35 | 28.9023 | 184 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 29.0117 | 184.1094 | -0.07 | 0.93 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 29.1133 | 184.211 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 29.2227 | 184.3204 | -0.06 | 0.94 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:35 | 29.3203 | 184.418 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 29.4219 | 184.5196 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 29.5195 | 184.6172 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 29.6328 | 184.7305 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 29.7305 | 184.8282 | -0.05 | 0.95 | -0.78 | 0.22 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 9:35 | 29.832 | 184.9297 | -0.11 | 0.89 | -0.74 | 0.26 | -0.67 | 0.33 | 72.27 | 23.44
2019-10-01 | 9:35 | 29.9297 | 185.0274 | -0.22 | 0.78 | -0.64 | 0.36 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:35 | 30.0312 | 185.129 | -0.23 | 0.77 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:35 | 30.1406 | 185.2383 | -0.23 | 0.77 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 23.44
2019-10-01 | 9:35 | 30.2422 | 185.3399 | -0.11 | 0.89 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:35 | 30.3516 | 185.4493 | -0.08 | 0.92 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 30.4531 | 185.5508 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 30.5508 | 185.6485 | -0.08 | 0.92 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 30.6523 | 185.75 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 30.7617 | 185.8594 | -0.08 | 0.92 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 30.8633 | 185.961 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 30.9609 | 186.0586 | -0.07 | 0.93 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 31.0625 | 186.1602 | -0.07 | 0.93 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 31.1719 | 186.2696 | -0.08 | 0.92 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 31.2695 | 186.3672 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 31.3711 | 186.4688 | -0.13 | 0.87 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 31.4805 | 186.5782 | -0.21 | 0.79 | -0.63 | 0.37 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 31.582 | 186.6797 | -0.25 | 0.75 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 31.6797 | 186.7774 | -0.24 | 0.76 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 31.7812 | 186.879 | -0.08 | 0.92 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:35 | 31.8906 | 186.9883 | -0.07 | 0.93 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 31.9922 | 187.0899 | -0.06 | 0.94 | -0.75 | 0.25 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:35 | 32.0898 | 187.1875 | -0.07 | 0.93 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 32.1914 | 187.2891 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 32.3008 | 187.3985 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 32.4023 | 187.5 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 32.5 | 187.5977 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 32.6133 | 187.711 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 32.7109 | 187.8086 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 32.8125 | 187.9102 | -0.05 | 0.95 | -0.77 | 0.23 | -0.68 | 0.32 | 76.17 | 26.37
2019-10-01 | 9:35 | 32.9102 | 188.0079 | -0.17 | 0.83 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 33.0195 | 188.1172 | -0.24 | 0.76 | -0.62 | 0.38 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 33.1211 | 188.2188 | -0.24 | 0.76 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 33.2227 | 188.3204 | -0.1 | 0.9 | -0.73 | 0.27 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:35 | 33.3203 | 188.418 | -0.09 | 0.91 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 33.4297 | 188.5274 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 33.5312 | 188.629 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 33.6328 | 188.7305 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 33.7422 | 188.8399 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 33.8398 | 188.9375 | -0.07 | 0.93 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 33.9414 | 189.0391 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 34.0508 | 189.1485 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:35 | 34.1523 | 189.25 | -0.06 | 0.94 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:35 | 34.25 | 189.3477 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 34.3516 | 189.4493 | -0.13 | 0.87 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 34.4531 | 189.5508 | -0.21 | 0.79 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:35 | 34.5625 | 189.6602 | -0.24 | 0.76 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 34.6602 | 189.7579 | -0.24 | 0.76 | -0.6 | 0.4 | -0.65 | 0.35 | 74.22 | 27.34
2019-10-01 | 9:35 | 34.7617 | 189.8594 | -0.1 | 0.9 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 34.8711 | 189.9688 | -0.08 | 0.92 | -0.73 | 0.27 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:35 | 34.9727 | 190.0704 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:35 | 35.0703 | 190.168 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 35.1797 | 190.2774 | -0.08 | 0.92 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 35.2812 | 190.379 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:35 | 35.3828 | 190.4805 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 35.4805 | 190.5782 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 35.5898 | 190.6875 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 9:35 | 35.6914 | 190.7891 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 35.793 | 190.8907 | -0.07 | 0.93 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 35.8906 | 190.9883 | -0.13 | 0.87 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 36 | 191.0977 | -0.23 | 0.77 | -0.63 | 0.37 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 36.1016 | 191.1993 | -0.24 | 0.76 | -0.6 | 0.4 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 36.2031 | 191.3008 | -0.24 | 0.76 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 36.3125 | 191.4102 | -0.09 | 0.91 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 36.4102 | 191.5079 | -0.09 | 0.91 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 36.5117 | 191.6094 | -0.08 | 0.92 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 36.6133 | 191.711 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 36.7227 | 191.8204 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 36.8203 | 191.918 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 36.9219 | 192.0196 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 37.0312 | 192.129 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 37.1328 | 192.2305 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:35 | 37.2305 | 192.3282 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 37.332 | 192.4297 | -0.08 | 0.92 | -0.73 | 0.27 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 37.4414 | 192.5391 | -0.19 | 0.81 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 37.543 | 192.6407 | -0.22 | 0.78 | -0.62 | 0.38 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 37.6406 | 192.7383 | -0.24 | 0.76 | -0.59 | 0.41 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 37.7422 | 192.8399 | -0.08 | 0.92 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 37.8516 | 192.9493 | -0.07 | 0.93 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 37.9531 | 193.0508 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:35 | 38.0508 | 193.1485 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 38.1523 | 193.25 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 38.2617 | 193.3594 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 38.3633 | 193.461 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 38.4609 | 193.5586 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 38.5703 | 193.668 | -0.07 | 0.93 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 26.37
2019-10-01 | 9:35 | 38.6719 | 193.7696 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 38.7695 | 193.8672 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 38.8711 | 193.9688 | -0.15 | 0.85 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 38.9805 | 194.0782 | -0.23 | 0.77 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 39.082 | 194.1797 | -0.26 | 0.74 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:35 | 39.1797 | 194.2774 | -0.24 | 0.76 | -0.6 | 0.4 | -0.63 | 0.37 | 74.22 | 25.39
2019-10-01 | 9:35 | 39.2812 | 194.379 | -0.09 | 0.91 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 39.3906 | 194.4883 | -0.08 | 0.92 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 39.4922 | 194.5899 | -0.07 | 0.93 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 39.6016 | 194.6993 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 39.7031 | 194.8008 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 39.8008 | 194.8985 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 39.9023 | 195 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 40.0117 | 195.1094 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 40.1133 | 195.211 | -0.05 | 0.95 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:35 | 40.2109 | 195.3086 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 40.3125 | 195.4102 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 40.4219 | 195.5196 | -0.18 | 0.82 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 40.5195 | 195.6172 | -0.2 | 0.8 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 40.6211 | 195.7188 | -0.22 | 0.78 | -0.61 | 0.39 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:35 | 40.7305 | 195.8282 | -0.1 | 0.9 | -0.7 | 0.3 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:35 | 40.832 | 195.9297 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 40.9297 | 196.0274 | -0.07 | 0.93 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 23.44
2019-10-01 | 9:35 | 41.0312 | 196.129 | -0.07 | 0.93 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 41.1406 | 196.2383 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 41.2422 | 196.3399 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:35 | 41.3398 | 196.4375 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 41.4414 | 196.5391 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 41.543 | 196.6407 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 41.6523 | 196.75 | -0.05 | 0.95 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 25.39
2019-10-01 | 9:35 | 41.75 | 196.8477 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 41.8633 | 196.961 | -0.09 | 0.91 | -0.72 | 0.28 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 41.9609 | 197.0586 | -0.19 | 0.81 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 42.0625 | 197.1602 | -0.2 | 0.8 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 42.1602 | 197.2579 | -0.22 | 0.78 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 42.2695 | 197.3672 | -0.09 | 0.91 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 42.3711 | 197.4688 | -0.08 | 0.92 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 42.4727 | 197.5704 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 42.5703 | 197.668 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 42.6797 | 197.7774 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 42.7812 | 197.879 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 42.8828 | 197.9805 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 42.9805 | 198.0782 | -0.05 | 0.95 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 43.0898 | 198.1875 | -0.05 | 0.95 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:35 | 43.1914 | 198.2891 | -0.06 | 0.94 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 43.293 | 198.3907 | -0.06 | 0.94 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:35 | 43.4023 | 198.5 | -0.15 | 0.85 | -0.68 | 0.32 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 43.5 | 198.5977 | -0.22 | 0.78 | -0.63 | 0.37 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:35 | 43.6016 | 198.6993 | -0.24 | 0.76 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 43.7031 | 198.8008 | -0.24 | 0.76 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 43.8125 | 198.9102 | -0.07 | 0.93 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 43.9102 | 199.0079 | -0.07 | 0.93 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 44.0117 | 199.1094 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 44.1133 | 199.211 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 44.2227 | 199.3204 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 44.3203 | 199.418 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 44.4219 | 199.5196 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 44.5312 | 199.629 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 44.6328 | 199.7305 | -0.04 | 0.96 | -0.78 | 0.22 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 44.7305 | 199.8282 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 44.832 | 199.9297 | -0.07 | 0.93 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 44.9414 | 200.0391 | -0.18 | 0.82 | -0.65 | 0.35 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 45.043 | 200.1407 | -0.2 | 0.8 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 45.1406 | 200.2383 | -0.21 | 0.79 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 45.2422 | 200.3399 | -0.08 | 0.92 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 45.3516 | 200.4493 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 45.4531 | 200.5508 | -0.06 | 0.94 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 45.5625 | 200.6602 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 45.6602 | 200.7579 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 45.7617 | 200.8594 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 45.8633 | 200.961 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 45.9727 | 201.0704 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 27.34
2019-10-01 | 9:35 | 46.0703 | 201.168 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 46.1719 | 201.2696 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:35 | 46.2695 | 201.3672 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 46.3711 | 201.4688 | -0.14 | 0.86 | -0.7 | 0.3 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 46.4805 | 201.5782 | -0.21 | 0.79 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 46.582 | 201.6797 | -0.24 | 0.76 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 46.6914 | 201.7891 | -0.23 | 0.77 | -0.6 | 0.4 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:35 | 46.793 | 201.8907 | -0.08 | 0.92 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:35 | 46.8906 | 201.9883 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 27.34
2019-10-01 | 9:35 | 46.9922 | 202.0899 | -0.07 | 0.93 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 27.34
2019-10-01 | 9:35 | 47.1016 | 202.1993 | -0.08 | 0.92 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 47.2031 | 202.3008 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 47.3008 | 202.3985 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 47.4023 | 202.5 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 47.5117 | 202.6094 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 47.6133 | 202.711 | -0.05 | 0.95 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:35 | 47.7109 | 202.8086 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:35 | 47.8203 | 202.918 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 24.41
2019-10-01 | 9:35 | 47.9219 | 203.0196 | -0.18 | 0.82 | -0.67 | 0.33 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 48.0195 | 203.1172 | -0.23 | 0.77 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 48.1211 | 203.2188 | -0.23 | 0.77 | -0.61 | 0.39 | -0.64 | 0.36 | 75.2 | 26.37
2019-10-01 | 9:35 | 48.2305 | 203.3282 | -0.12 | 0.88 | -0.69 | 0.31 | -0.64 | 0.36 | 75.2 | 23.44
2019-10-01 | 9:35 | 48.332 | 203.4297 | -0.08 | 0.92 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 48.4297 | 203.5274 | -0.05 | 0.95 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 48.5312 | 203.629 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 48.6406 | 203.7383 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:35 | 48.7422 | 203.8399 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 48.8398 | 203.9375 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 48.9531 | 204.0508 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 49.0508 | 204.1485 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:35 | 49.1523 | 204.25 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 49.25 | 204.3477 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 49.3633 | 204.461 | -0.07 | 0.93 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 49.4609 | 204.5586 | -0.18 | 0.82 | -0.64 | 0.36 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 49.5625 | 204.6602 | -0.21 | 0.79 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:35 | 49.6602 | 204.7579 | -0.23 | 0.77 | -0.6 | 0.4 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 49.7695 | 204.8672 | -0.09 | 0.91 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 49.8711 | 204.9688 | -0.06 | 0.94 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 49.9727 | 205.0704 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 50.082 | 205.1797 | -0.07 | 0.93 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 50.1797 | 205.2774 | -0.07 | 0.93 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 50.2812 | 205.379 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 50.3828 | 205.4805 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 50.4922 | 205.5899 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 50.5898 | 205.6875 | -0.07 | 0.93 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 50.6914 | 205.7891 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 9:35 | 50.793 | 205.8907 | -0.06 | 0.94 | -0.78 | 0.22 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:35 | 50.9023 | 206 | -0.16 | 0.84 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 51 | 206.0977 | -0.23 | 0.77 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 51.1016 | 206.1993 | -0.23 | 0.77 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 51.2109 | 206.3086 | -0.21 | 0.79 | -0.62 | 0.38 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 9:35 | 51.3125 | 206.4102 | -0.09 | 0.91 | -0.73 | 0.27 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 51.4102 | 206.5079 | -0.08 | 0.92 | -0.75 | 0.25 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:35 | 51.5195 | 206.6172 | -0.07 | 0.93 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 51.6211 | 206.7188 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:35 | 51.7227 | 206.8204 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 51.8203 | 206.918 | -0.05 | 0.95 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 27.34
2019-10-01 | 9:35 | 51.9297 | 207.0274 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 52.0312 | 207.129 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 52.1328 | 207.2305 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 52.2305 | 207.3282 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 52.332 | 207.4297 | -0.07 | 0.93 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 52.4414 | 207.5391 | -0.18 | 0.82 | -0.65 | 0.35 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 52.543 | 207.6407 | -0.21 | 0.79 | -0.6 | 0.4 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 52.6523 | 207.75 | -0.21 | 0.79 | -0.6 | 0.4 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 52.75 | 207.8477 | -0.08 | 0.92 | -0.71 | 0.29 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 52.8516 | 207.9493 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 52.9531 | 208.0508 | -0.05 | 0.95 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:35 | 53.0625 | 208.1602 | -0.06 | 0.94 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 53.1602 | 208.2579 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 53.2617 | 208.3594 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 53.3633 | 208.461 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 53.4727 | 208.5704 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:35 | 53.5703 | 208.668 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 53.6719 | 208.7696 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 53.7812 | 208.879 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:35 | 53.8828 | 208.9805 | -0.11 | 0.89 | -0.71 | 0.29 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 53.9805 | 209.0782 | -0.21 | 0.79 | -0.63 | 0.37 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 54.082 | 209.1797 | -0.22 | 0.78 | -0.6 | 0.4 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:35 | 54.1914 | 209.2891 | -0.24 | 0.76 | -0.58 | 0.42 | -0.63 | 0.37 | 74.22 | 26.37
2019-10-01 | 9:35 | 54.293 | 209.3907 | -0.08 | 0.92 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 54.3906 | 209.4883 | -0.07 | 0.93 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:35 | 54.4922 | 209.5899 | -0.07 | 0.93 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 54.6016 | 209.6993 | -0.06 | 0.94 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 24.41
2019-10-01 | 9:35 | 54.7031 | 209.8008 | -0.05 | 0.95 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 54.8008 | 209.8985 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 54.9102 | 210.0079 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 55.0117 | 210.1094 | -0.04 | 0.96 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 55.1133 | 210.211 | -0.05 | 0.95 | -0.76 | 0.24 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 9:35 | 55.2109 | 210.3086 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 55.3203 | 210.418 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 55.4219 | 210.5196 | -0.19 | 0.81 | -0.65 | 0.35 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 55.5195 | 210.6172 | -0.23 | 0.77 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 55.6211 | 210.7188 | -0.22 | 0.78 | -0.6 | 0.4 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 55.7305 | 210.8282 | -0.15 | 0.85 | -0.67 | 0.33 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:35 | 55.832 | 210.9297 | -0.07 | 0.93 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:35 | 55.9414 | 211.0391 | -0.07 | 0.93 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 56.043 | 211.1407 | -0.07 | 0.93 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:35 | 56.1406 | 211.2383 | -0.06 | 0.94 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:35 | 56.2422 | 211.3399 | -0.06 | 0.94 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 56.3516 | 211.4493 | -0.06 | 0.94 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 56.4531 | 211.5508 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 56.5508 | 211.6485 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 56.6523 | 211.75 | -0.04 | 0.96 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 56.75 | 211.8477 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 56.8633 | 211.961 | -0.08 | 0.92 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 56.9609 | 212.0586 | -0.18 | 0.82 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:35 | 57.0703 | 212.168 | -0.21 | 0.79 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 57.1719 | 212.2696 | -0.21 | 0.79 | -0.59 | 0.41 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 57.2695 | 212.3672 | -0.07 | 0.93 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 57.3711 | 212.4688 | -0.07 | 0.93 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 57.4727 | 212.5704 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 57.582 | 212.6797 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 57.6797 | 212.7774 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:35 | 57.7812 | 212.879 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 57.8828 | 212.9805 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 57.9922 | 213.0899 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 58.0898 | 213.1875 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 58.1914 | 213.2891 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:35 | 58.3008 | 213.3985 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 58.4023 | 213.5 | -0.15 | 0.85 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 58.5 | 213.5977 | -0.23 | 0.77 | -0.62 | 0.38 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 58.6133 | 213.711 | -0.23 | 0.77 | -0.61 | 0.39 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 9:35 | 58.7109 | 213.8086 | -0.22 | 0.78 | -0.58 | 0.42 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:35 | 58.8125 | 213.9102 | -0.08 | 0.92 | -0.73 | 0.27 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:35 | 58.9102 | 214.0079 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 59.0195 | 214.1172 | -0.07 | 0.93 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 59.1211 | 214.2188 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 59.2227 | 214.3204 | -0.06 | 0.94 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 59.3203 | 214.418 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 59.4297 | 214.5274 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:35 | 59.5312 | 214.629 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 59.6328 | 214.7305 | -0.04 | 0.96 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:35 | 59.7422 | 214.8399 | -0.03 | 0.97 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:35 | 59.8398 | 214.9375 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 59.9414 | 215.0391 | -0.16 | 0.84 | -0.64 | 0.36 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 60.043 | 215.1407 | -0.22 | 0.78 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:35 | 60.1523 | 215.25 | -0.21 | 0.79 | -0.61 | 0.39 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 60.25 | 215.3477 | -0.07 | 0.93 | -0.71 | 0.29 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:35 | 60.3516 | 215.4493 | -0.07 | 0.93 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:35 | 60.4531 | 215.5508 | -0.06 | 0.94 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 60.5625 | 215.6602 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 60.6602 | 215.7579 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:35 | 60.7617 | 215.8594 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:35 | 60.8711 | 215.9688 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 60.9727 | 216.0704 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:35 | 61.0703 | 216.168 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:35 | 61.1719 | 216.2696 | -0.05 | 0.95 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:35 | 61.2812 | 216.379 | -0.03 | 0.97 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:35 | 61.3828 | 216.4805 | -0.11 | 0.89 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:35 | 61.4805 | 216.5782 | -0.21 | 0.79 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 61.582 | 216.6797 | -0.22 | 0.78 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 61.6914 | 216.7891 | -0.24 | 0.76 | -0.6 | 0.4 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 61.793 | 216.8907 | -0.08 | 0.92 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:35 | 61.8906 | 216.9883 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 24.41
2019-10-01 | 9:35 | 62 | 217.0977 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:35 | 62.1016 | 217.1993 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:35 | 62.2031 | 217.3008 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:35 | 62.3008 | 217.3985 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:35 | 62.4102 | 217.5079 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 62.5117 | 217.6094 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:35 | 62.6133 | 217.711 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:35 | 62.7109 | 217.8086 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:35 | 62.8203 | 217.918 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:35 | 62.9219 | 218.0196 | -0.15 | 0.85 | -0.67 | 0.33 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:35 | 63.0312 | 218.129 | -0.22 | 0.78 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:35 | 63.1328 | 218.2305 | -0.22 | 0.78 | -0.61 | 0.39 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 63.2305 | 218.3282 | -0.15 | 0.85 | -0.66 | 0.34 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:35 | 63.332 | 218.4297 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 63.4414 | 218.5391 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 63.543 | 218.6407 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 63.6406 | 218.7383 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:36 | 63.7422 | 218.8399 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 63.8398 | 218.9375 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 63.9531 | 219.0508 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:36 | 64.0508 | 219.1485 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 64.1602 | 219.2579 | -0.04 | 0.96 | -0.74 | 0.26 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:36 | 64.2617 | 219.3594 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 64.3633 | 219.461 | -0.06 | 0.94 | -0.75 | 0.25 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:36 | 64.4609 | 219.5586 | -0.18 | 0.82 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 64.5703 | 219.668 | -0.21 | 0.79 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 27.34
2019-10-01 | 9:36 | 64.6719 | 219.7696 | -0.22 | 0.78 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 64.7695 | 219.8672 | -0.08 | 0.92 | -0.73 | 0.27 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 64.8711 | 219.9688 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 64.9805 | 220.0782 | -0.05 | 0.95 | -0.74 | 0.26 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:36 | 65.082 | 220.1797 | -0.06 | 0.94 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 65.1797 | 220.2774 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 65.293 | 220.3907 | -0.06 | 0.94 | -0.76 | 0.24 | -0.68 | 0.32 | 75.2 | 26.37
2019-10-01 | 9:36 | 65.3906 | 220.4883 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 65.4922 | 220.5899 | -0.07 | 0.93 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 65.5898 | 220.6875 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:36 | 65.7031 | 220.8008 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 65.8008 | 220.8985 | -0.06 | 0.94 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:36 | 65.9023 | 221 | -0.16 | 0.84 | -0.69 | 0.31 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:36 | 66 | 221.0977 | -0.21 | 0.79 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 66.1133 | 221.211 | -0.23 | 0.77 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 66.2109 | 221.3086 | -0.24 | 0.76 | -0.6 | 0.4 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 66.3125 | 221.4102 | -0.08 | 0.92 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 66.4219 | 221.5196 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 66.5195 | 221.6172 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:36 | 66.6211 | 221.7188 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 66.7227 | 221.8204 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 66.832 | 221.9297 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:36 | 66.9297 | 222.0274 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 67.0312 | 222.129 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 67.1328 | 222.2305 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 67.2422 | 222.3399 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 67.3398 | 222.4375 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 67.4414 | 222.5391 | -0.17 | 0.83 | -0.66 | 0.34 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 67.5508 | 222.6485 | -0.22 | 0.78 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 67.6523 | 222.75 | -0.22 | 0.78 | -0.6 | 0.4 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 67.75 | 222.8477 | -0.1 | 0.9 | -0.71 | 0.29 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 9:36 | 67.8633 | 222.961 | -0.06 | 0.94 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 67.9609 | 223.0586 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 68.0625 | 223.1602 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 68.1602 | 223.2579 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 25.39
2019-10-01 | 9:36 | 68.2617 | 223.3594 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 68.3711 | 223.4688 | -0.02 | 0.98 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 68.4727 | 223.5704 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 68.5703 | 223.668 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 68.6797 | 223.7774 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 68.7812 | 223.879 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 68.8828 | 223.9805 | -0.08 | 0.92 | -0.72 | 0.28 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 68.9922 | 224.0899 | -0.18 | 0.82 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 69.0898 | 224.1875 | -0.21 | 0.79 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 69.1914 | 224.2891 | -0.22 | 0.78 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 69.3008 | 224.3985 | -0.05 | 0.95 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 69.4023 | 224.5 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:36 | 69.5 | 224.5977 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 69.6016 | 224.6993 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 69.7031 | 224.8008 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 69.8125 | 224.9102 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 24.41
2019-10-01 | 9:36 | 69.9102 | 225.0079 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 76.17 | 25.39
2019-10-01 | 9:36 | 70.0117 | 225.1094 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 70.1211 | 225.2188 | -0.04 | 0.96 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:36 | 70.2227 | 225.3204 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 70.3203 | 225.418 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 70.4219 | 225.5196 | -0.15 | 0.85 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 70.5312 | 225.629 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 70.6328 | 225.7305 | -0.2 | 0.8 | -0.63 | 0.37 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 70.7305 | 225.8282 | -0.15 | 0.85 | -0.65 | 0.35 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 70.832 | 225.9297 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 70.9414 | 226.0391 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 71.043 | 226.1407 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 71.1406 | 226.2383 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:36 | 71.25 | 226.3477 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 24.41
2019-10-01 | 9:36 | 71.3516 | 226.4493 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 71.4531 | 226.5508 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 71.5508 | 226.6485 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:36 | 71.6602 | 226.7579 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 71.7617 | 226.8594 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 71.8633 | 226.961 | -0.08 | 0.92 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 71.9609 | 227.0586 | -0.19 | 0.81 | -0.64 | 0.36 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 9:36 | 72.0703 | 227.168 | -0.21 | 0.79 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:36 | 72.1719 | 227.2696 | -0.23 | 0.77 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 72.2695 | 227.3672 | -0.08 | 0.92 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 72.3828 | 227.4805 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 72.4805 | 227.5782 | -0.06 | 0.94 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 72.582 | 227.6797 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 72.6797 | 227.7774 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 72.793 | 227.8907 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 72.8906 | 227.9883 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 72.9922 | 228.0899 | -0.06 | 0.94 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 73.0898 | 228.1875 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:36 | 73.2031 | 228.3008 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 73.3008 | 228.3985 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 73.4023 | 228.5 | -0.15 | 0.85 | -0.68 | 0.32 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 73.5117 | 228.6094 | -0.21 | 0.79 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 73.6133 | 228.711 | -0.23 | 0.77 | -0.63 | 0.37 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 73.7109 | 228.8086 | -0.23 | 0.77 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:36 | 73.8125 | 228.9102 | -0.07 | 0.93 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 73.9219 | 229.0196 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 74.0195 | 229.1172 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 74.1211 | 229.2188 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 74.2227 | 229.3204 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 74.332 | 229.4297 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 74.4297 | 229.5274 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:36 | 74.5312 | 229.629 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 74.6406 | 229.7383 | -0.04 | 0.96 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:36 | 74.7422 | 229.8399 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 74.8398 | 229.9375 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 74.9531 | 230.0508 | -0.16 | 0.84 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 75.0508 | 230.1485 | -0.2 | 0.8 | -0.62 | 0.38 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:36 | 75.1523 | 230.25 | -0.23 | 0.77 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 75.25 | 230.3477 | -0.09 | 0.91 | -0.71 | 0.29 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 75.3633 | 230.461 | -0.07 | 0.93 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 75.4609 | 230.5586 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 75.5625 | 230.6602 | -0.07 | 0.93 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 75.6719 | 230.7696 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:36 | 75.7695 | 230.8672 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 76.17 | 24.41
2019-10-01 | 9:36 | 75.8711 | 230.9688 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:36 | 75.9727 | 231.0704 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 76.082 | 231.1797 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 76.1797 | 231.2774 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 76.2812 | 231.379 | -0.03 | 0.97 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:36 | 76.3828 | 231.4805 | -0.09 | 0.91 | -0.73 | 0.27 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 76.4922 | 231.5899 | -0.21 | 0.79 | -0.63 | 0.37 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 76.5898 | 231.6875 | -0.23 | 0.77 | -0.63 | 0.37 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 9:36 | 76.6914 | 231.7891 | -0.23 | 0.77 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 76.8008 | 231.8985 | -0.08 | 0.92 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 76.9023 | 232 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 77 | 232.0977 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 77.1016 | 232.1993 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 77.2109 | 232.3086 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 76.17 | 26.37
2019-10-01 | 9:36 | 77.3125 | 232.4102 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 77.4102 | 232.5079 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 77.5117 | 232.6094 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 77.6211 | 232.7188 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 77.7227 | 232.8204 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 77.8203 | 232.918 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 75.2 | 24.41
2019-10-01 | 9:36 | 77.9219 | 233.0196 | -0.14 | 0.86 | -0.68 | 0.32 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 78.0312 | 233.129 | -0.2 | 0.8 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:36 | 78.1328 | 233.2305 | -0.22 | 0.78 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 78.2305 | 233.3282 | -0.22 | 0.78 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 78.3398 | 233.4375 | -0.07 | 0.93 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 78.4414 | 233.5391 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 78.543 | 233.6407 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 78.6406 | 233.7383 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 78.75 | 233.8477 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 78.8516 | 233.9493 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 9:36 | 78.9531 | 234.0508 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:36 | 79.0508 | 234.1485 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 79.1602 | 234.2579 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 23.44
2019-10-01 | 9:36 | 79.2617 | 234.3594 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:36 | 79.3711 | 234.4688 | -0.07 | 0.93 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 79.4727 | 234.5704 | -0.17 | 0.83 | -0.65 | 0.35 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 79.5703 | 234.668 | -0.21 | 0.79 | -0.63 | 0.37 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 79.6797 | 234.7774 | -0.2 | 0.8 | -0.63 | 0.37 | -0.64 | 0.36 | 75.2 | 26.37
2019-10-01 | 9:36 | 79.7695 | 234.8672 | -0.08 | 0.92 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 79.8828 | 234.9805 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 79.9805 | 235.0782 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 80.082 | 235.1797 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 80.1797 | 235.2774 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:36 | 80.293 | 235.3907 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 80.3906 | 235.4883 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:36 | 80.5 | 235.5977 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 80.6016 | 235.6993 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 23.44
2019-10-01 | 9:36 | 80.7031 | 235.8008 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:36 | 80.8008 | 235.8985 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 80.9102 | 236.0079 | -0.1 | 0.9 | -0.7 | 0.3 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 81.0117 | 236.1094 | -0.18 | 0.82 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 81.1133 | 236.211 | -0.2 | 0.8 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 81.2109 | 236.3086 | -0.2 | 0.8 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 81.3125 | 236.4102 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 81.4219 | 236.5196 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 81.5195 | 236.6172 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 81.6328 | 236.7305 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 81.7305 | 236.8282 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:36 | 81.832 | 236.9297 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 81.9297 | 237.0274 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:36 | 82.043 | 237.1407 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:36 | 82.1406 | 237.2383 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 82.2422 | 237.3399 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 82.3398 | 237.4375 | -0.05 | 0.95 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:36 | 82.4531 | 237.5508 | -0.16 | 0.84 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 82.5508 | 237.6485 | -0.2 | 0.8 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 82.6523 | 237.75 | -0.21 | 0.79 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 23.44
2019-10-01 | 9:36 | 82.7617 | 237.8594 | -0.1 | 0.9 | -0.71 | 0.29 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 82.8633 | 237.961 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 82.9609 | 238.0586 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 83.0625 | 238.1602 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:36 | 83.1719 | 238.2696 | -0.04 | 0.96 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 83.2695 | 238.3672 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 83.3711 | 238.4688 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 83.4727 | 238.5704 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 83.582 | 238.6797 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 83.6797 | 238.7774 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 23.44
2019-10-01 | 9:36 | 83.7812 | 238.879 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 83.8906 | 238.9883 | -0.1 | 0.9 | -0.71 | 0.29 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 83.9922 | 239.0899 | -0.2 | 0.8 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 84.0898 | 239.1875 | -0.23 | 0.77 | -0.63 | 0.37 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 84.1914 | 239.2891 | -0.23 | 0.77 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 84.3008 | 239.3985 | -0.1 | 0.9 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 84.4023 | 239.5 | -0.07 | 0.93 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 84.5 | 239.5977 | -0.07 | 0.93 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 84.6016 | 239.6993 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 84.7109 | 239.8086 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:36 | 84.8125 | 239.9102 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:36 | 84.9102 | 240.0079 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 85.0117 | 240.1094 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 85.1211 | 240.2188 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:36 | 85.2227 | 240.3204 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 85.3203 | 240.418 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 85.4297 | 240.5274 | -0.14 | 0.86 | -0.67 | 0.33 | -0.66 | 0.34 | 76.17 | 25.39
2019-10-01 | 9:36 | 85.5312 | 240.629 | -0.22 | 0.78 | -0.62 | 0.38 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 85.6328 | 240.7305 | -0.22 | 0.78 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 85.7305 | 240.8282 | -0.22 | 0.78 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 85.8398 | 240.9375 | -0.07 | 0.93 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 23.44
2019-10-01 | 9:36 | 85.9414 | 241.0391 | -0.06 | 0.94 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 86.043 | 241.1407 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 86.1406 | 241.2383 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 86.25 | 241.3477 | -0.06 | 0.94 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 86.3516 | 241.4493 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 86.4609 | 241.5586 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 86.5625 | 241.6602 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 86.6602 | 241.7579 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 86.7617 | 241.8594 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 86.8711 | 241.9688 | -0.07 | 0.93 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 86.9727 | 242.0704 | -0.18 | 0.82 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 87.0703 | 242.168 | -0.22 | 0.78 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 87.1719 | 242.2696 | -0.22 | 0.78 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 87.2812 | 242.379 | -0.09 | 0.91 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:36 | 87.3828 | 242.4805 | -0.06 | 0.94 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 87.4805 | 242.5782 | -0.06 | 0.94 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 87.5898 | 242.6875 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 72.27 | 23.44
2019-10-01 | 9:36 | 87.6914 | 242.7891 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 87.793 | 242.8907 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:36 | 87.8906 | 242.9883 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 88 | 243.0977 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 88.1016 | 243.1993 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:36 | 88.2031 | 243.3008 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 88.3008 | 243.3985 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 88.4102 | 243.5079 | -0.11 | 0.89 | -0.7 | 0.3 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 88.5117 | 243.6094 | -0.18 | 0.82 | -0.64 | 0.36 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 88.6133 | 243.711 | -0.22 | 0.78 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 88.7227 | 243.8204 | -0.19 | 0.81 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 88.8203 | 243.918 | -0.07 | 0.93 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 88.9219 | 244.0196 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:36 | 89.0195 | 244.1172 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:36 | 89.1328 | 244.2305 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 89.2305 | 244.3282 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 89.332 | 244.4297 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 89.4297 | 244.5274 | -0.03 | 0.97 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:36 | 89.543 | 244.6407 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 89.6406 | 244.7383 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 89.7422 | 244.8399 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 89.8516 | 244.9493 | -0.03 | 0.97 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:36 | 89.9531 | 245.0508 | -0.12 | 0.88 | -0.67 | 0.33 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 90.0508 | 245.1485 | -0.19 | 0.81 | -0.63 | 0.37 | -0.64 | 0.36 | 74.22 | 27.34
2019-10-01 | 9:36 | 90.1523 | 245.25 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 90.2617 | 245.3594 | -0.1 | 0.9 | -0.7 | 0.3 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 90.3633 | 245.461 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 90.4609 | 245.5586 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 90.5625 | 245.6602 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 90.6719 | 245.7696 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 90.7695 | 245.8672 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:36 | 90.8828 | 245.9805 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 90.9805 | 246.0782 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:36 | 91.082 | 246.1797 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 91.1797 | 246.2774 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 27.34
2019-10-01 | 9:36 | 91.2812 | 246.379 | -0.04 | 0.96 | -0.76 | 0.24 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:36 | 91.3906 | 246.4883 | -0.1 | 0.9 | -0.71 | 0.29 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 91.4922 | 246.5899 | -0.19 | 0.81 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 91.5898 | 246.6875 | -0.23 | 0.77 | -0.61 | 0.39 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 91.6914 | 246.7891 | -0.23 | 0.77 | -0.6 | 0.4 | -0.63 | 0.37 | 73.24 | 23.44
2019-10-01 | 9:36 | 91.8008 | 246.8985 | -0.08 | 0.92 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 91.9023 | 247 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 92 | 247.0977 | -0.06 | 0.94 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 92.1133 | 247.211 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 92.2109 | 247.3086 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 92.3125 | 247.4102 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 92.4219 | 247.5196 | -0.04 | 0.96 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 92.5195 | 247.6172 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 92.6211 | 247.7188 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 92.7227 | 247.8204 | -0.03 | 0.97 | -0.77 | 0.23 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 9:36 | 92.8203 | 247.918 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 92.9297 | 248.0274 | -0.12 | 0.88 | -0.69 | 0.31 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:36 | 93.0312 | 248.129 | -0.18 | 0.82 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 93.1328 | 248.2305 | -0.21 | 0.79 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 93.2305 | 248.3282 | -0.2 | 0.8 | -0.61 | 0.39 | 1.26 |  | 73.24 | 24.41 | Anomolous SC pressure not used in analysis
2019-10-01 | 9:36 | 93.3398 | 248.4375 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 93.4414 | 248.5391 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 93.5508 | 248.6485 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 93.6523 | 248.75 | -0.05 | 0.95 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 93.75 | 248.8477 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 93.8516 | 248.9493 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 93.9609 | 249.0586 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:36 | 94.0625 | 249.1602 | -0.02 | 0.98 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 94.1602 | 249.2579 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 94.2617 | 249.3594 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 94.3711 | 249.4688 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:36 | 94.4727 | 249.5704 | -0.14 | 0.86 | -0.67 | 0.33 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 94.5703 | 249.668 | -0.19 | 0.81 | -0.62 | 0.38 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 94.6797 | 249.7774 | -0.21 | 0.79 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 94.7812 | 249.879 | -0.08 | 0.92 | -0.73 | 0.27 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 94.8828 | 249.9805 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:36 | 94.9805 | 250.0782 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 95.0898 | 250.1875 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 23.44
2019-10-01 | 9:36 | 95.1914 | 250.2891 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:36 | 95.293 | 250.3907 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 95.4023 | 250.5 | -0.05 | 0.95 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:36 | 95.5 | 250.5977 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 95.6016 | 250.6993 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 95.7031 | 250.8008 | -0.04 | 0.96 | -0.78 | 0.22 | -0.67 | 0.33 | 75.2 | 24.41
2019-10-01 | 9:36 | 95.8125 | 250.9102 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 95.9102 | 251.0079 | -0.11 | 0.89 | -0.7 | 0.3 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:36 | 96.0117 | 251.1094 | -0.19 | 0.81 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 96.1133 | 251.211 | -0.21 | 0.79 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 96.2227 | 251.3204 | -0.21 | 0.79 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:36 | 96.3203 | 251.418 | -0.07 | 0.93 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 96.4219 | 251.5196 | -0.06 | 0.94 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 96.5195 | 251.6172 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 96.6328 | 251.7305 | -0.04 | 0.96 | -0.77 | 0.23 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 96.7305 | 251.8282 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 96.8398 | 251.9375 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 96.9414 | 252.0391 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:36 | 97.043 | 252.1407 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 97.1406 | 252.2383 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 97.25 | 252.3477 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 97.3516 | 252.4493 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 97.4531 | 252.5508 | -0.15 | 0.85 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 97.5508 | 252.6485 | -0.19 | 0.81 | -0.63 | 0.37 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:36 | 97.6523 | 252.75 | -0.2 | 0.8 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:36 | 97.7617 | 252.8594 | -0.12 | 0.88 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 97.8633 | 252.961 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 97.9727 | 253.0704 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 98.0703 | 253.168 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 98.1719 | 253.2696 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 98.2695 | 253.3672 | -0.03 | 0.97 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 98.3828 | 253.4805 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 98.4805 | 253.5782 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 98.582 | 253.6797 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 98.6797 | 253.7774 | -0.02 | 0.98 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 98.793 | 253.8907 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 98.8906 | 253.9883 | -0.03 | 0.97 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 98.9922 | 254.0899 | -0.14 | 0.86 | -0.67 | 0.33 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 99.1016 | 254.1993 | -0.18 | 0.82 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 99.2031 | 254.3008 | -0.19 | 0.81 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 99.3008 | 254.3985 | -0.06 | 0.94 | -0.75 | 0.25 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 99.4023 | 254.5 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 99.5117 | 254.6094 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 99.6133 | 254.711 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 99.7109 | 254.8086 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 99.8125 | 254.9102 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 99.9219 | 255.0196 | -0.03 | 0.97 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 100.0195 | 255.1172 | -0.02 | 0.98 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 100.1211 | 255.2188 | -0.02 | 0.98 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 100.2305 | 255.3282 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 100.332 | 255.4297 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 100.4297 | 255.5274 | -0.11 | 0.89 | -0.69 | 0.31 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 100.5313 | 255.629 | -0.18 | 0.82 | -0.64 | 0.36 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 100.6406 | 255.7383 | -0.19 | 0.81 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:36 | 100.7422 | 255.8399 | -0.21 | 0.79 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 100.8398 | 255.9375 | -0.06 | 0.94 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 100.9531 | 256.0508 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 101.0508 | 256.1485 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 101.1523 | 256.25 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 101.25 | 256.3477 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 76.17 | 25.39
2019-10-01 | 9:36 | 101.3633 | 256.461 | -0.02 | 0.98 | -0.76 | 0.24 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:36 | 101.4609 | 256.5586 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 101.5625 | 256.6602 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 101.6719 | 256.7696 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 101.7695 | 256.8672 | -0.04 | 0.96 | -0.77 | 0.23 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 101.8711 | 256.9688 | -0.04 | 0.96 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:36 | 101.9727 | 257.0704 | -0.17 | 0.83 | -0.65 | 0.35 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 102.0703 | 257.168 | -0.19 | 0.81 | -0.63 | 0.37 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 102.1797 | 257.2774 | -0.21 | 0.79 | -0.63 | 0.37 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 9:36 | 102.2813 | 257.379 | -0.1 | 0.9 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 102.3828 | 257.4805 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:36 | 102.4922 | 257.5899 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 102.5898 | 257.6875 | -0.05 | 0.95 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 102.6914 | 257.7891 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 102.8008 | 257.8985 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:36 | 102.9023 | 258 | -0.05 | 0.95 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 103 | 258.0977 | -0.05 | 0.95 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 103.1016 | 258.1993 | -0.04 | 0.96 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 23.44
2019-10-01 | 9:36 | 103.2031 | 258.3008 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 103.3125 | 258.4102 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 103.4102 | 258.5079 | -0.12 | 0.88 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 103.5117 | 258.6094 | -0.2 | 0.8 | -0.63 | 0.37 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 103.6133 | 258.711 | -0.2 | 0.8 | -0.64 | 0.36 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 103.7227 | 258.8204 | -0.21 | 0.79 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 103.8203 | 258.918 | -0.07 | 0.93 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 103.9297 | 259.0274 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 104.0313 | 259.129 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 104.1328 | 259.2305 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 104.2305 | 259.3282 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:36 | 104.3398 | 259.4375 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 104.4414 | 259.5391 | -0.06 | 0.94 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 104.543 | 259.6407 | -0.05 | 0.95 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:36 | 104.6406 | 259.7383 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 104.7422 | 259.8399 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 104.8516 | 259.9493 | -0.03 | 0.97 | -0.77 | 0.23 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 9:36 | 104.9531 | 260.0508 | -0.15 | 0.85 | -0.67 | 0.33 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 105.0625 | 260.1602 | -0.21 | 0.79 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:36 | 105.1602 | 260.2579 | -0.23 | 0.77 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 105.2617 | 260.3594 | -0.15 | 0.85 | -0.66 | 0.34 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 105.3633 | 260.461 | -0.06 | 0.94 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 105.4727 | 260.5704 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 105.5703 | 260.668 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 105.6719 | 260.7696 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 105.7695 | 260.8672 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 105.8828 | 260.9805 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 105.9805 | 261.0782 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 106.082 | 261.1797 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:36 | 106.1914 | 261.2891 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 106.293 | 261.3907 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 106.3906 | 261.4883 | -0.06 | 0.94 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 106.4922 | 261.5899 | -0.17 | 0.83 | -0.64 | 0.36 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 106.6016 | 261.6993 | -0.21 | 0.79 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 106.7031 | 261.8008 | -0.2 | 0.8 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 106.8008 | 261.8985 | -0.07 | 0.93 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 106.9023 | 262 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 107.0117 | 262.1094 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 107.1133 | 262.211 | -0.03 | 0.97 | -0.76 | 0.24 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 107.2227 | 262.3204 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 107.3203 | 262.418 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:36 | 107.4219 | 262.5196 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 107.5195 | 262.6172 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 107.6211 | 262.7188 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 107.7305 | 262.8282 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 107.832 | 262.9297 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:36 | 107.9297 | 263.0274 | -0.12 | 0.88 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 108.0313 | 263.129 | -0.18 | 0.82 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 108.1406 | 263.2383 | -0.19 | 0.81 | -0.62 | 0.38 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:36 | 108.2422 | 263.3399 | -0.19 | 0.81 | -0.63 | 0.37 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:36 | 108.3516 | 263.4493 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 108.4531 | 263.5508 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 108.5508 | 263.6485 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:36 | 108.6523 | 263.75 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 108.7617 | 263.8594 | -0.03 | 0.97 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 108.8633 | 263.961 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 108.9609 | 264.0586 | -0.02 | 0.98 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 109.0625 | 264.1602 | -0.02 | 0.98 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 109.1602 | 264.2579 | -0.03 | 0.97 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 109.2695 | 264.3672 | -0.03 | 0.97 | -0.76 | 0.24 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 9:36 | 109.3711 | 264.4688 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 109.4805 | 264.5782 | -0.14 | 0.86 | -0.67 | 0.33 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 109.582 | 264.6797 | -0.2 | 0.8 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 109.6914 | 264.7891 | -0.21 | 0.79 | -0.62 | 0.38 | -0.64 | 0.36 | 75.2 | 24.41
2019-10-01 | 9:36 | 109.7813 | 264.879 | -0.07 | 0.93 | -0.73 | 0.27 | -0.63 | 0.37 | 74.22 | 25.39
2019-10-01 | 9:36 | 109.8906 | 264.9883 | -0.06 | 0.94 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 109.9922 | 265.0899 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 110.0898 | 265.1875 | -0.04 | 0.96 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 110.1914 | 265.2891 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 110.3008 | 265.3985 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 110.4023 | 265.5 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 110.5 | 265.5977 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 110.6133 | 265.711 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 110.7109 | 265.8086 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 110.8125 | 265.9102 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 110.9102 | 266.0079 | -0.07 | 0.93 | -0.71 | 0.29 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 111.0195 | 266.1172 | -0.16 | 0.84 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:36 | 111.1211 | 266.2188 | -0.18 | 0.82 | -0.62 | 0.38 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 111.2227 | 266.3204 | -0.19 | 0.81 | -0.61 | 0.39 | -0.65 | 0.35 | 75.2 | 24.41
2019-10-01 | 9:36 | 111.3203 | 266.418 | -0.05 | 0.95 | -0.75 | 0.25 | -0.64 | 0.36 | 75.2 | 23.44
2019-10-01 | 9:36 | 111.4297 | 266.5274 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 111.5313 | 266.629 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 111.6328 | 266.7305 | -0.03 | 0.97 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 111.7305 | 266.8282 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 111.8398 | 266.9375 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 111.9414 | 267.0391 | -0.03 | 0.97 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 112.043 | 267.1407 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 112.1523 | 267.25 | -0.04 | 0.96 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:36 | 112.25 | 267.3477 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 112.3516 | 267.4493 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:36 | 112.4531 | 267.5508 | -0.12 | 0.88 | -0.69 | 0.31 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 112.5625 | 267.6602 | -0.2 | 0.8 | -0.63 | 0.37 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:36 | 112.6602 | 267.7579 | -0.23 | 0.77 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 112.7617 | 267.8594 | -0.22 | 0.78 | -0.62 | 0.38 | -0.63 | 0.37 | 73.24 | 23.44
2019-10-01 | 9:36 | 112.8633 | 267.961 | -0.06 | 0.94 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 112.9727 | 268.0704 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 113.0703 | 268.168 | -0.05 | 0.95 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:36 | 113.1719 | 268.2696 | -0.05 | 0.95 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 113.2813 | 268.379 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 113.3828 | 268.4805 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 113.4805 | 268.5782 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 76.17 | 25.39
2019-10-01 | 9:36 | 113.582 | 268.6797 | -0.03 | 0.97 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 113.6914 | 268.7891 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 113.793 | 268.8907 | -0.02 | 0.98 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 9:36 | 113.8906 | 268.9883 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 113.9922 | 269.0899 | -0.18 | 0.82 | -0.65 | 0.35 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 114.1133 | 269.211 | -0.2 | 0.8 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 114.2109 | 269.3086 | -0.21 | 0.79 | -0.6 | 0.4 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 114.3125 | 269.4102 | -0.06 | 0.94 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 114.4102 | 269.5079 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 114.5117 | 269.6094 | -0.04 | 0.96 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 114.6133 | 269.711 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 114.7109 | 269.8086 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:36 | 114.8203 | 269.918 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 114.9219 | 270.0196 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 115.0195 | 270.1172 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 24.41
2019-10-01 | 9:36 | 115.1211 | 270.2188 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 115.2305 | 270.3282 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 115.332 | 270.4297 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 115.4414 | 270.5391 | -0.11 | 0.89 | -0.68 | 0.32 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 115.543 | 270.6407 | -0.18 | 0.82 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 115.6406 | 270.7383 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:36 | 115.7422 | 270.8399 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 115.8516 | 270.9493 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 115.9531 | 271.0508 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 116.0508 | 271.1485 | -0.05 | 0.95 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 23.44
2019-10-01 | 9:36 | 116.1523 | 271.25 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:36 | 116.2617 | 271.3594 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:36 | 116.3633 | 271.461 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 116.4609 | 271.5586 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 116.5703 | 271.668 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 116.6719 | 271.7696 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 116.7695 | 271.8672 | -0.04 | 0.96 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 116.8711 | 271.9688 | -0.04 | 0.96 | -0.74 | 0.26 | -0.69 | 0.31 | 74.22 | 24.41
2019-10-01 | 9:36 | 116.9805 | 272.0782 | -0.16 | 0.84 | -0.65 | 0.35 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 117.082 | 272.1797 | -0.21 | 0.79 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:36 | 117.1797 | 272.2774 | -0.22 | 0.78 | -0.62 | 0.38 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:36 | 117.2813 | 272.379 | -0.09 | 0.91 | -0.71 | 0.29 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 117.3906 | 272.4883 | -0.06 | 0.94 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 117.4922 | 272.5899 | -0.05 | 0.95 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:36 | 117.6016 | 272.6993 | -0.05 | 0.95 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 117.7031 | 272.8008 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:36 | 117.8008 | 272.8985 | -0.04 | 0.96 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 117.9023 | 273 | -0.05 | 0.95 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 118 | 273.0977 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 118.1133 | 273.211 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 118.2109 | 273.3086 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 118.3125 | 273.4102 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 23.44
2019-10-01 | 9:36 | 118.4102 | 273.5079 | -0.06 | 0.94 | -0.72 | 0.28 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 118.5195 | 273.6172 | -0.18 | 0.82 | -0.63 | 0.37 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:36 | 118.6211 | 273.7188 | -0.2 | 0.8 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 118.7227 | 273.8204 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 118.832 | 273.9297 | -0.05 | 0.95 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 118.9297 | 274.0274 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 119.0313 | 274.129 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 119.1328 | 274.2305 | -0.03 | 0.97 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 119.2422 | 274.3399 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:36 | 119.3398 | 274.4375 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 23.44
2019-10-01 | 9:36 | 119.4414 | 274.5391 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 119.543 | 274.6407 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 119.6602 | 274.7579 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 119.75 | 274.8477 | -0.04 | 0.96 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 119.8516 | 274.9493 | -0.01 | 0.99 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 119.9609 | 275.0586 | -0.14 | 0.86 | -0.67 | 0.33 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 120.0625 | 275.1602 | -0.19 | 0.81 | -0.63 | 0.37 | -0.64 | 0.36 | 75.2 | 24.41
2019-10-01 | 9:36 | 120.1602 | 275.2579 | -0.2 | 0.8 | -0.62 | 0.38 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 9:36 | 120.2695 | 275.3672 | -0.21 | 0.79 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 120.3711 | 275.4688 | -0.05 | 0.95 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 120.4727 | 275.5704 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 120.5703 | 275.668 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:36 | 120.6797 | 275.7774 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 72.27 | 23.44
2019-10-01 | 9:36 | 120.7813 | 275.879 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:36 | 120.8828 | 275.9805 | -0.02 | 0.98 | -0.74 | 0.26 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:36 | 120.9805 | 276.0782 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 71.29 | 24.41
2019-10-01 | 9:36 | 121.0898 | 276.1875 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:36 | 121.1914 | 276.2891 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 23.44
2019-10-01 | 9:36 | 121.293 | 276.3907 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 121.4023 | 276.5 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 121.5 | 276.5977 | -0.15 | 0.85 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 121.6016 | 276.6993 | -0.17 | 0.83 | -0.61 | 0.39 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 121.7031 | 276.8008 | -0.19 | 0.81 | -0.62 | 0.38 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:36 | 121.8125 | 276.9102 | -0.07 | 0.93 | -0.73 | 0.27 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:36 | 121.9102 | 277.0079 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:36 | 122.0117 | 277.1094 | -0.04 | 0.96 | -0.74 | 0.26 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:36 | 122.1211 | 277.2188 | -0.02 | 0.98 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:36 | 122.2227 | 277.3204 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 70.31 | 21.48
2019-10-01 | 9:36 | 122.3203 | 277.418 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 122.4219 | 277.5196 | -0.01 | 0.99 | -0.76 | 0.24 | -0.66 | 0.34 | 70.31 | 23.44
2019-10-01 | 9:36 | 122.5313 | 277.629 | -0.01 | 0.99 | -0.76 | 0.24 | -0.67 | 0.33 | 70.31 | 23.44
2019-10-01 | 9:36 | 122.6328 | 277.7305 | 0 | 1 | -0.76 | 0.24 | -0.66 | 0.34 | 70.31 | 23.44
2019-10-01 | 9:36 | 122.7305 | 277.8282 | -0.01 | 0.99 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:36 | 122.832 | 277.9297 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:36 | 122.9414 | 278.0391 | -0.07 | 0.93 | -0.71 | 0.29 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:36 | 123.043 | 278.1407 | -0.17 | 0.83 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:36 | 123.1406 | 278.2383 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 71.29 | 25.39
2019-10-01 | 9:36 | 123.2422 | 278.3399 | -0.2 | 0.8 | -0.62 | 0.38 | -0.64 | 0.36 | 72.27 | 23.44
2019-10-01 | 9:36 | 123.3516 | 278.4493 | -0.05 | 0.95 | -0.75 | 0.25 | -0.64 | 0.36 | 70.31 | 25.39
2019-10-01 | 9:36 | 123.4531 | 278.5508 | -0.04 | 0.96 | -0.73 | 0.27 | -0.67 | 0.33 | 71.29 | 23.44
2019-10-01 | 9:36 | 123.5508 | 278.6485 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 27.34
2019-10-01 | 9:36 | 123.6602 | 278.7579 | -0.03 | 0.97 | -0.76 | 0.24 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:36 | 123.7617 | 278.8594 | -0.02 | 0.98 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:36 | 123.8633 | 278.961 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:36 | 123.9609 | 279.0586 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 124.0703 | 279.168 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:36 | 124.1719 | 279.2696 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:36 | 124.2695 | 279.3672 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:37 | 124.3711 | 279.4688 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:37 | 124.4805 | 279.5782 | -0.14 | 0.86 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 124.582 | 279.6797 | -0.19 | 0.81 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 124.6914 | 279.7891 | -0.17 | 0.83 | -0.62 | 0.38 | -0.64 | 0.36 | 70.31 | 24.41
2019-10-01 | 9:37 | 124.793 | 279.8907 | -0.09 | 0.91 | -0.7 | 0.3 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 124.8906 | 279.9883 | -0.04 | 0.96 | -0.74 | 0.26 | -0.64 | 0.36 | 71.29 | 23.44
2019-10-01 | 9:37 | 124.9922 | 280.0899 | -0.04 | 0.96 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 125.0898 | 280.1875 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 69.34 | 23.44
2019-10-01 | 9:37 | 125.2031 | 280.3008 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 125.3008 | 280.3985 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 70.31 | 24.41
2019-10-01 | 9:37 | 125.4023 | 280.5 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 9:37 | 125.5 | 280.5977 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 68.36 | 23.44
2019-10-01 | 9:37 | 125.6133 | 280.711 | -0.01 | 0.99 | -0.76 | 0.24 | -0.66 | 0.34 | 69.34 | 23.44
2019-10-01 | 9:37 | 125.7109 | 280.8086 | -0.03 | 0.97 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:37 | 125.8203 | 280.918 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 68.36 | 26.37
2019-10-01 | 9:37 | 125.9219 | 281.0196 | -0.05 | 0.95 | -0.72 | 0.28 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 126.0195 | 281.1172 | -0.17 | 0.83 | -0.63 | 0.37 | -0.67 | 0.33 | 68.36 | 23.44
2019-10-01 | 9:37 | 126.1211 | 281.2188 | -0.19 | 0.81 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:37 | 126.2305 | 281.3282 | -0.18 | 0.82 | -0.62 | 0.38 | -0.64 | 0.36 | 71.29 | 24.41
2019-10-01 | 9:37 | 126.332 | 281.4297 | -0.06 | 0.94 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:37 | 126.4297 | 281.5274 | -0.04 | 0.96 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 126.5313 | 281.629 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:37 | 126.6328 | 281.7305 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:37 | 126.7422 | 281.8399 | -0.03 | 0.97 | -0.74 | 0.26 | -0.65 | 0.35 | 71.29 | 23.44
2019-10-01 | 9:37 | 126.8398 | 281.9375 | -0.01 | 0.99 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 126.9531 | 282.0508 | -0.01 | 0.99 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 127.0508 | 282.1485 | -0.03 | 0.97 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:37 | 127.1523 | 282.25 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 127.25 | 282.3477 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 9:37 | 127.3633 | 282.461 | -0.01 | 0.99 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:37 | 127.4609 | 282.5586 | -0.1 | 0.9 | -0.69 | 0.31 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:37 | 127.5625 | 282.6602 | -0.17 | 0.83 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 127.6719 | 282.7696 | -0.19 | 0.81 | -0.61 | 0.39 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 127.7695 | 282.8672 | -0.2 | 0.8 | -0.6 | 0.4 | -0.63 | 0.37 | 71.29 | 24.41
2019-10-01 | 9:37 | 127.8711 | 282.9688 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 71.29 | 24.41
2019-10-01 | 9:37 | 127.9727 | 283.0704 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 128.082 | 283.1797 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 128.1797 | 283.2774 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 23.44
2019-10-01 | 9:37 | 128.2813 | 283.379 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 128.3828 | 283.4805 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:37 | 128.4922 | 283.5899 | -0.01 | 0.99 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 128.5898 | 283.6875 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 9:37 | 128.6914 | 283.7891 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:37 | 128.793 | 283.8907 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 128.9023 | 284 | -0.03 | 0.97 | -0.74 | 0.26 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:37 | 129 | 284.0977 | -0.16 | 0.84 | -0.64 | 0.36 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 129.1016 | 284.1993 | -0.19 | 0.81 | -0.62 | 0.38 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 129.2109 | 284.3086 | -0.2 | 0.8 | -0.61 | 0.39 | -0.63 | 0.37 | 72.27 | 25.39
2019-10-01 | 9:37 | 129.3125 | 284.4102 | -0.07 | 0.93 | -0.73 | 0.27 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 129.4102 | 284.5079 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 129.5195 | 284.6172 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 129.6211 | 284.7188 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:37 | 129.7227 | 284.8204 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 129.8203 | 284.918 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:37 | 129.9219 | 285.0196 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:37 | 130.0313 | 285.129 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 9:37 | 130.1328 | 285.2305 | -0.02 | 0.98 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 130.2305 | 285.3282 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 130.332 | 285.4297 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:37 | 130.4414 | 285.5391 | -0.1 | 0.9 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 130.543 | 285.6407 | -0.17 | 0.83 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:37 | 130.6523 | 285.75 | -0.2 | 0.8 | -0.61 | 0.39 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:37 | 130.75 | 285.8477 | -0.2 | 0.8 | -0.59 | 0.41 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 130.8516 | 285.9493 | -0.05 | 0.95 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:37 | 130.9531 | 286.0508 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:37 | 131.0625 | 286.1602 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 131.1602 | 286.2579 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 131.2617 | 286.3594 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:37 | 131.3633 | 286.461 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:37 | 131.4727 | 286.5704 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 23.44
2019-10-01 | 9:37 | 131.5703 | 286.668 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 131.6719 | 286.7696 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:37 | 131.7813 | 286.879 | -0.01 | 0.99 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:37 | 131.8828 | 286.9805 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:37 | 131.9805 | 287.0782 | -0.13 | 0.87 | -0.65 | 0.35 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 132.082 | 287.1797 | -0.19 | 0.81 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 132.1914 | 287.2891 | -0.2 | 0.8 | -0.6 | 0.4 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 132.293 | 287.3907 | -0.11 | 0.89 | -0.67 | 0.33 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 132.3906 | 287.4883 | -0.04 | 0.96 | -0.74 | 0.26 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:37 | 132.4922 | 287.5899 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 132.6016 | 287.6993 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:37 | 132.7031 | 287.8008 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 132.8008 | 287.8985 | -0.03 | 0.97 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:37 | 132.9102 | 288.0079 | -0.01 | 0.99 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:37 | 133.0117 | 288.1094 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:37 | 133.1133 | 288.211 | -0.02 | 0.98 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 133.2227 | 288.3204 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 133.3203 | 288.418 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:37 | 133.4219 | 288.5196 | -0.07 | 0.93 | -0.71 | 0.29 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:37 | 133.5195 | 288.6172 | -0.18 | 0.82 | -0.63 | 0.37 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:37 | 133.6211 | 288.7188 | -0.19 | 0.81 | -0.61 | 0.39 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 133.7305 | 288.8282 | -0.18 | 0.82 | -0.62 | 0.38 | -0.63 | 0.37 | 73.24 | 24.41
2019-10-01 | 9:37 | 133.832 | 288.9297 | -0.06 | 0.94 | -0.72 | 0.28 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 9:37 | 133.9297 | 289.0274 | -0.04 | 0.96 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 23.44
2019-10-01 | 9:37 | 134.043 | 289.1407 | -0.03 | 0.97 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 134.1406 | 289.2383 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:37 | 134.2422 | 289.3399 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 9:37 | 134.3398 | 289.4375 | 0 | 1 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 134.4531 | 289.5508 | 0 | 1 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 23.44
2019-10-01 | 9:37 | 134.5508 | 289.6485 | -0.01 | 0.99 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 134.6523 | 289.75 | -0.01 | 0.99 | -0.76 | 0.24 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 9:37 | 134.75 | 289.8477 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 134.8633 | 289.961 | 0 | 1 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 23.44
2019-10-01 | 9:37 | 134.9609 | 290.0586 | -0.1 | 0.9 | -0.67 | 0.33 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 135.0625 | 290.1602 | -0.17 | 0.83 | -0.63 | 0.37 | -0.65 | 0.35 | 72.27 | 23.44
2019-10-01 | 9:37 | 135.1719 | 290.2696 | -0.2 | 0.8 | -0.58 | 0.42 | -0.63 | 0.37 | 72.27 | 24.41
2019-10-01 | 9:37 | 135.2695 | 290.3672 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:37 | 135.3711 | 290.4688 | -0.04 | 0.96 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:37 | 135.4727 | 290.5704 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:37 | 135.582 | 290.6797 | -0.01 | 0.99 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 135.6797 | 290.7774 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:37 | 135.7813 | 290.879 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:37 | 135.8828 | 290.9805 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 135.9922 | 291.0899 | -0.02 | 0.98 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:37 | 136.0898 | 291.1875 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:37 | 136.2031 | 291.3008 | -0.02 | 0.98 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:37 | 136.3008 | 291.3985 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 9:37 | 136.4023 | 291.5 | -0.04 | 0.96 | -0.72 | 0.28 | -0.68 | 0.32 | 74.22 | 24.41
2019-10-01 | 9:37 | 136.5 | 291.5977 | -0.15 | 0.85 | -0.64 | 0.36 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 9:37 | 136.6133 | 291.711 | -0.17 | 0.83 | -0.6 | 0.4 | -0.64 | 0.36 | 73.24 | 23.44
2019-10-01 | 9:37 | 136.7109 | 291.8086 | -0.18 | 0.82 | -0.61 | 0.39 | -0.62 | 0.38 | 75.2 | 24.41
2019-10-01 | 9:37 | 136.8125 | 291.9102 | -0.06 | 0.94 | -0.72 | 0.28 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 9:37 | 136.9102 | 292.0079 | -0.05 | 0.95 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 137.0195 | 292.1172 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:37 | 137.1211 | 292.2188 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 137.2227 | 292.3204 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 137.332 | 292.4297 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 137.4297 | 292.5274 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 9:37 | 137.5313 | 292.629 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 24.41
2019-10-01 | 9:37 | 137.6328 | 292.7305 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:37 | 137.7422 | 292.8399 | -0.03 | 0.97 | -0.76 | 0.24 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:37 | 137.8398 | 292.9375 | -0.02 | 0.98 | -0.75 | 0.25 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 9:37 | 137.9414 | 293.0391 | -0.09 | 0.91 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 138.043 | 293.1407 | -0.18 | 0.82 | -0.61 | 0.39 | -0.65 | 0.35 | 75.2 | 24.41
2019-10-01 | 9:37 | 138.1406 | 293.2383 | -0.2 | 0.8 | -0.6 | 0.4 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 9:37 | 138.25 | 293.3477 | -0.21 | 0.79 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:37 | 138.3516 | 293.4493 | -0.05 | 0.95 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 138.4531 | 293.5508 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 72.27 | 23.44
2019-10-01 | 9:37 | 138.5625 | 293.6602 | -0.04 | 0.96 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:37 | 138.6602 | 293.7579 | -0.03 | 0.97 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 138.7617 | 293.8594 | -0.03 | 0.97 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 138.8711 | 293.9688 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 138.9727 | 294.0704 | -0.02 | 0.98 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:37 | 139.0703 | 294.168 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 139.1719 | 294.2696 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:37 | 139.2813 | 294.379 | -0.01 | 0.99 | -0.76 | 0.24 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:37 | 139.3828 | 294.4805 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:37 | 139.4805 | 294.5782 | -0.13 | 0.87 | -0.66 | 0.34 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:37 | 139.582 | 294.6797 | -0.18 | 0.82 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:37 | 139.7031 | 294.8008 | -0.2 | 0.8 | -0.6 | 0.4 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 139.793 | 294.8907 | -0.13 | 0.87 | -0.66 | 0.34 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 9:37 | 139.8906 | 294.9883 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:37 | 140 | 295.0977 | -0.05 | 0.95 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 140.1016 | 295.1993 | -0.03 | 0.97 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 140.2031 | 295.3008 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:37 | 140.3008 | 295.3985 | -0.04 | 0.96 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:37 | 140.4102 | 295.5079 | -0.04 | 0.96 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:37 | 140.5117 | 295.6094 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:37 | 140.6133 | 295.711 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 9:37 | 140.7227 | 295.8204 | -0.03 | 0.97 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 140.8203 | 295.918 | -0.01 | 0.99 | -0.75 | 0.25 | -0.68 | 0.32 | 75.2 | 24.41
2019-10-01 | 9:37 | 140.9219 | 296.0196 | -0.04 | 0.96 | -0.73 | 0.27 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 141.0195 | 296.1172 | -0.16 | 0.84 | -0.64 | 0.36 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 141.1328 | 296.2305 | -0.17 | 0.83 | -0.61 | 0.39 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:37 | 141.2305 | 296.3282 | -0.19 | 0.81 | -0.61 | 0.39 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:37 | 141.332 | 296.4297 | -0.06 | 0.94 | -0.73 | 0.27 | -0.66 | 0.34 | 75.2 | 25.39
2019-10-01 | 9:37 | 141.4297 | 296.5274 | -0.04 | 0.96 | -0.74 | 0.26 | -0.63 | 0.37 | 74.22 | 24.41
2019-10-01 | 9:37 | 141.543 | 296.6407 | -0.02 | 0.98 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 141.6406 | 296.7383 | -0.02 | 0.98 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 141.7422 | 296.8399 | -0.02 | 0.98 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 141.8398 | 296.9375 | -0.02 | 0.98 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 141.9531 | 297.0508 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 142.0508 | 297.1485 | -0.02 | 0.98 | -0.73 | 0.27 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:37 | 142.1602 | 297.2579 | -0.03 | 0.97 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 24.41
2019-10-01 | 9:37 | 142.2617 | 297.3594 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 142.3633 | 297.461 | -0.03 | 0.97 | -0.74 | 0.26 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:37 | 142.4609 | 297.5586 | -0.11 | 0.89 | -0.68 | 0.32 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 9:37 | 142.5625 | 297.6602 | -0.18 | 0.82 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:37 | 142.6719 | 297.7696 | -0.19 | 0.81 | -0.61 | 0.39 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 142.7695 | 297.8672 | -0.21 | 0.79 | -0.59 | 0.41 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:37 | 142.8711 | 297.9688 | -0.06 | 0.94 | -0.73 | 0.27 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:37 | 142.9727 | 298.0704 | -0.04 | 0.96 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 143.082 | 298.1797 | -0.04 | 0.96 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 143.1797 | 298.2774 | -0.03 | 0.97 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 143.293 | 298.3907 | -0.02 | 0.98 | -0.73 | 0.27 | -0.64 | 0.36 | 75.2 | 25.39
2019-10-01 | 9:37 | 143.3906 | 298.4883 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 26.37
2019-10-01 | 9:37 | 143.4922 | 298.5899 | -0.02 | 0.98 | -0.74 | 0.26 | -0.65 | 0.35 | 74.22 | 25.39
2019-10-01 | 9:37 | 143.5898 | 298.6875 | -0.01 | 0.99 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 143.7031 | 298.8008 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:37 | 143.8008 | 298.8985 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 24.41
2019-10-01 | 9:37 | 143.9023 | 299 | -0.04 | 0.96 | -0.74 | 0.26 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:37 | 144 | 299.0977 | -0.17 | 0.83 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 144.1133 | 299.211 | -0.19 | 0.81 | -0.61 | 0.39 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 144.2109 | 299.3086 | -0.19 | 0.81 | -0.61 | 0.39 | -0.65 | 0.35 | 71.29 | 22.46
2019-10-01 | 9:37 | 144.3125 | 299.4102 | -0.07 | 0.93 | -0.71 | 0.29 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 144.4219 | 299.5196 | -0.05 | 0.95 | -0.73 | 0.27 | -0.65 | 0.35 | 71.29 | 22.46
2019-10-01 | 9:37 | 144.5195 | 299.6172 | -0.03 | 0.97 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 24.41
2019-10-01 | 9:37 | 144.6211 | 299.7188 | -0.03 | 0.97 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 144.7227 | 299.8204 | -0.04 | 0.96 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:37 | 144.832 | 299.9297 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 144.9297 | 300.0274 | -0.03 | 0.97 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 145.0313 | 300.129 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 145.1328 | 300.2305 | -0.01 | 0.99 | -0.74 | 0.26 | -0.66 | 0.34 | 71.29 | 23.44
2019-10-01 | 9:37 | 145.2422 | 300.3399 | -0.02 | 0.98 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 9:37 | 145.3398 | 300.4375 | -0.01 | 0.99 | -0.76 | 0.24 | -0.67 | 0.33 | 71.29 | 23.44
2019-10-01 | 9:37 | 145.4414 | 300.5391 | -0.08 | 0.92 | -0.69 | 0.31 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 9:37 | 145.5508 | 300.6485 | -0.17 | 0.83 | -0.61 | 0.39 | -0.64 | 0.36 | 71.29 | 23.44
2019-10-01 | 9:37 | 145.6523 | 300.75 | -0.2 | 0.8 | -0.61 | 0.39 | -0.64 | 0.36 | 72.27 | 23.44
2019-10-01 | 9:37 | 145.75 | 300.8477 | -0.19 | 0.81 | -0.6 | 0.4 | -0.64 | 0.36 | 73.24 | 24.41
2019-10-01 | 9:37 | 145.8516 | 300.9493 | -0.05 | 0.95 | -0.74 | 0.26 | -0.64 | 0.36 | 71.29 | 23.44
2019-10-01 | 9:37 | 145.9609 | 301.0586 | -0.05 | 0.95 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 24.41
2019-10-01 | 9:37 | 146.0625 | 301.1602 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 146.1602 | 301.2579 | -0.03 | 0.97 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 146.2617 | 301.3594 | -0.01 | 0.99 | -0.75 | 0.25 | -0.65 | 0.35 | 74.22 | 24.41
2019-10-01 | 9:37 | 146.3711 | 301.4688 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:37 | 146.4727 | 301.5704 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 22.46
2019-10-01 | 9:37 | 146.5703 | 301.668 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 146.6797 | 301.7774 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 25.39
2019-10-01 | 9:37 | 146.7813 | 301.879 | -0.02 | 0.98 | -0.74 | 0.26 | -0.66 | 0.34 | 74.22 | 24.41
2019-10-01 | 9:37 | 146.8828 | 301.9805 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 146.9805 | 302.0782 | -0.14 | 0.86 | -0.65 | 0.35 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 9:37 | 147.0898 | 302.1875 | -0.2 | 0.8 | -0.62 | 0.38 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 147.1914 | 302.2891 | -0.19 | 0.81 | -0.62 | 0.38 | -0.64 | 0.36 | 74.22 | 23.44
2019-10-01 | 9:37 | 147.293 | 302.3907 | -0.15 | 0.85 | -0.64 | 0.36 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 9:37 | 147.3906 | 302.4883 | -0.03 | 0.97 | -0.74 | 0.26 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 147.5 | 302.5977 | -0.03 | 0.97 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 23.44
2019-10-01 | 9:37 | 147.6016 | 302.6993 | -0.03 | 0.97 | -0.74 | 0.26 | -0.65 | 0.35 | 75.2 | 25.39
2019-10-01 | 9:37 | 147.7031 | 302.8008 | -0.02 | 0.98 | -0.74 | 0.26 | -0.64 | 0.36 | 70.31 | 23.44
2019-10-01 | 9:37 | 147.8125 | 302.9102 | -0.03 | 0.97 | -0.73 | 0.27 | -0.65 | 0.35 | 70.31 | 23.44
2019-10-01 | 9:37 | 147.9102 | 303.0079 | -0.01 | 0.99 | -0.73 | 0.27 | -0.65 | 0.35 | 70.31 | 23.44
2019-10-01 | 9:37 | 148.0117 | 303.1094 | -0.02 | 0.98 | -0.74 | 0.26 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 9:37 | 148.1211 | 303.2188 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 71.29 | 23.44
2019-10-01 | 9:37 | 148.2227 | 303.3204 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 9:37 | 148.3203 | 303.418 | -0.01 | 0.99 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 22.46
2019-10-01 | 9:37 | 148.4219 | 303.5196 | -0.02 | 0.98 | -0.73 | 0.27 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 148.5195 | 303.6172 | -0.14 | 0.86 | -0.63 | 0.37 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 9:37 | 148.6328 | 303.7305 | -0.17 | 0.83 | -0.6 | 0.4 | -0.65 | 0.35 | 71.29 | 23.44
2019-10-01 | 9:37 | 148.7305 | 303.8282 | -0.18 | 0.82 | -0.61 | 0.39 | -0.64 | 0.36 | 74.22 | 24.41
2019-10-01 | 9:37 | 148.832 | 303.9297 | -0.05 | 0.95 | -0.73 | 0.27 | -0.64 | 0.36 | 71.29 | 25.39
2019-10-01 | 9:37 | 148.9414 | 304.0391 | -0.02 | 0.98 | -0.73 | 0.27 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 9:37 | 149.043 | 304.1407 | -0.02 | 0.98 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 26.37
2019-10-01 | 9:37 | 149.1406 | 304.2383 | -0.02 | 0.98 | -0.73 | 0.27 | -0.64 | 0.36 | 70.31 | 22.46
2019-10-01 | 9:37 | 149.25 | 304.3477 | -0.02 | 0.98 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 149.3516 | 304.4493 | -0.02 | 0.98 | -0.74 | 0.26 | -0.65 | 0.35 | 71.29 | 25.39
2019-10-01 | 9:37 | 149.4531 | 304.5508 | -0.01 | 0.99 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:37 | 149.5508 | 304.6485 | -0.02 | 0.98 | -0.74 | 0.26 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 9:37 | 149.6602 | 304.7579 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 9:37 | 149.7617 | 304.8594 | -0.01 | 0.99 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 9:37 | 149.8633 | 304.961 | -0.01 | 0.99 | -0.75 | 0.25 | -0.67 | 0.33 | 71.29 | 22.46
2019-10-01 | 9:37 | 149.9609 | 305.0586 | -0.1 | 0.9 | -0.68 | 0.32 | -0.66 | 0.34 | 75.2 | 26.37
2019-10-01 | 9:37 | 150.0703 | 305.168 | -0.18 | 0.82 | -0.62 | 0.38 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 9:37 | 150.1719 | 305.2696 | -0.2 | 0.8 | -0.6 | 0.4 | -0.63 | 0.37 | 75.2 | 25.39
2019-10-01 | 9:37 | 150.2695 | 305.3672 | -0.2 | 0.8 | -0.6 | 0.4 | -0.64 | 0.36 | 71.29 | 22.46
2019-10-01 | 9:37 | 150.3828 | 305.4805 | -0.05 | 0.95 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 23.44
2019-10-01 | 9:37 | 150.4805 | 305.5782 | -0.04 | 0.96 | -0.74 | 0.26 | -0.64 | 0.36 | 75.2 | 27.34
2019-10-01 | 9:37 | 150.582 | 305.6797 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 75.2 | 22.46
2019-10-01 | 9:37 | 150.6797 | 305.7774 | -0.04 | 0.96 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 9:37 | 150.793 | 305.8907 | -0.03 | 0.97 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 9:37 | 150.8906 | 305.9883 | -0.02 | 0.98 | -0.75 | 0.25 | -0.67 | 0.33 | 75.2 | 26.37

## 13.3mL s
|  |  |  | BoilerPressure |  | HEPressure |  | SCPressure
Date | Clock | Timer |  | Gauge (raw) | Absolute (raw) | Gauge (raw) | Absolute (raw) | Gauge (raw) | Absolute (raw) | HETemperature | SCTemperature
2019-10-01 | 10:03 | 0.24219 | 0.24219 | 0.06 | 1.06 | -0.3 | 0.7 | -0.25 | 0.75 | 32.23 | 23.44
2019-10-01 | 10:03 | 0.35938 | 0.35938 | 0.05 | 1.05 | -0.28 | 0.72 | -0.26 | 0.74 | 33.2 | 23.44 |  | Volume | Seconds
2019-10-01 | 10:03 | 0.44141 | 0.44141 | 0 | 1 | -0.26 | 0.74 | -0.24 | 0.76 | 32.23 | 22.46 |  | 100 | 7 | start
2019-10-01 | 10:03 | 0.5625 | 0.5625 | -0.01 | 0.99 | -0.26 | 0.74 | -0.23 | 0.77 | 31.25 | 22.46 |  | 100 | 7
2019-10-01 | 10:03 | 0.65234 | 0.65234 | -0.02 | 0.98 | -0.25 | 0.75 | -0.23 | 0.77 | 31.25 | 22.46 |  | 100 | 7
2019-10-01 | 10:03 | 0.76172 | 0.76172 | 0 | 1 | -0.24 | 0.76 | -0.22 | 0.78 | 32.23 | 25.39
2019-10-01 | 10:03 | 0.85156 | 0.85156 | 0.04 | 1.04 | -0.27 | 0.73 | -0.22 | 0.78 | 34.18 | 23.44 |  | 100 | 8 | end
2019-10-01 | 10:03 | 0.99219 | 0.99219 | 0.04 | 1.04 | -0.28 | 0.72 | -0.23 | 0.77 | 32.23 | 23.44 |  | 100 | 8
2019-10-01 | 10:03 | 1.0625 | 1.0625 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 32.23 | 24.41 |  | 100 | 8
2019-10-01 | 10:03 | 1.1914 | 1.1914 | 0.05 | 1.05 | -0.29 | 0.71 | -0.23 | 0.77 | 32.23 | 23.44
2019-10-01 | 10:03 | 1.2617 | 1.2617 | 0.05 | 1.05 | -0.29 | 0.71 | -0.23 | 0.77 | 32.23 | 23.44
2019-10-01 | 10:03 | 1.3828 | 1.3828 | 0.06 | 1.06 | -0.29 | 0.71 | -0.25 | 0.75 | 32.23 | 24.41
2019-10-01 | 10:03 | 1.4727 | 1.4727 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 33.2 | 22.46
2019-10-01 | 10:03 | 1.582 | 1.582 | 0.06 | 1.06 | -0.3 | 0.7 | -0.26 | 0.74 | 32.23 | 23.44
2019-10-01 | 10:03 | 1.6719 | 1.6719 | 0.06 | 1.06 | -0.29 | 0.71 | -0.24 | 0.76 | 32.23 | 23.44
2019-10-01 | 10:03 | 1.7812 | 1.7812 | 0.06 | 1.06 | -0.31 | 0.69 | -0.26 | 0.74 | 31.25 | 23.44
2019-10-01 | 10:03 | 1.8828 | 1.8828 | 0 | 1 | -0.28 | 0.72 | -0.25 | 0.75 | 32.23 | 22.46
2019-10-01 | 10:03 | 1.9805 | 1.9805 | 0 | 1 | -0.26 | 0.74 | -0.23 | 0.77 | 33.2 | 24.41
2019-10-01 | 10:03 | 2.1094 | 2.1094 | -0.01 | 0.99 | -0.24 | 0.76 | -0.23 | 0.77 | 32.23 | 25.39
2019-10-01 | 10:03 | 2.1914 | 2.1914 | -0.02 | 0.98 | -0.24 | 0.76 | -0.22 | 0.78 | 31.25 | 24.41
2019-10-01 | 10:03 | 2.293 | 2.293 | -0.01 | 0.99 | -0.23 | 0.77 | -0.21 | 0.79 | 33.2 | 24.41
2019-10-01 | 10:03 | 2.3906 | 2.3906 | 0.05 | 1.05 | -0.28 | 0.72 | -0.23 | 0.77 | 32.23 | 23.44
2019-10-01 | 10:03 | 2.5195 | 2.5195 | 0.05 | 1.05 | -0.27 | 0.73 | -0.23 | 0.77 | 32.23 | 24.41
2019-10-01 | 10:03 | 2.6211 | 2.6211 | 0.04 | 1.04 | -0.27 | 0.73 | -0.24 | 0.76 | 32.23 | 23.44
2019-10-01 | 10:03 | 2.6992 | 2.6992 | 0.06 | 1.06 | -0.28 | 0.72 | -0.24 | 0.76 | 33.2 | 23.44 | [6 empty] | 70
2019-10-01 | 10:03 | 2.8125 | 2.8125 | 0.06 | 1.06 | -0.29 | 0.71 | -0.23 | 0.77 | 32.23 | 23.44 | [6 empty] | 130
2019-10-01 | 10:03 | 2.9102 | 2.9102 | 0.06 | 1.06 | -0.29 | 0.71 | -0.24 | 0.76 | 32.23 | 23.44
2019-10-01 | 10:03 | 3.0117 | 3.0117 | 0.05 | 1.05 | -0.3 | 0.7 | -0.24 | 0.76 | 31.25 | 25.39
2019-10-01 | 10:03 | 3.1094 | 3.1094 | 0.05 | 1.05 | -0.3 | 0.7 | -0.25 | 0.75 | 34.18 | 23.44 |  | There is no way to take equilibrium data from this
2019-10-01 | 10:03 | 3.2227 | 3.2227 | 0.06 | 1.06 | -0.29 | 0.71 | -0.25 | 0.75 | 33.2 | 23.44
2019-10-01 | 10:03 | 3.3203 | 3.3203 | 0.05 | 1.05 | -0.29 | 0.71 | -0.27 | 0.73 | 32.23 | 24.41
2019-10-01 | 10:03 | 3.4297 | 3.4297 | 0 | 1 | -0.25 | 0.75 | -0.24 | 0.76 | 33.2 | 24.41
2019-10-01 | 10:03 | 3.5312 | 3.5312 | -0.02 | 0.98 | -0.26 | 0.74 | -0.22 | 0.78 | 33.2 | 24.41
2019-10-01 | 10:03 | 3.6328 | 3.6328 | -0.02 | 0.98 | -0.24 | 0.76 | -0.23 | 0.77 | 32.23 | 23.44
2019-10-01 | 10:03 | 3.7422 | 3.7422 | -0.01 | 0.99 | -0.24 | 0.76 | -0.23 | 0.77 | 33.2 | 25.39
2019-10-01 | 10:03 | 3.8398 | 3.8398 | 0.04 | 1.04 | -0.27 | 0.73 | -0.21 | 0.79 | 33.2 | 24.41
2019-10-01 | 10:03 | 3.9414 | 3.9414 | 0.04 | 1.04 | -0.28 | 0.72 | -0.24 | 0.76 | 31.25 | 24.41
2019-10-01 | 10:03 | 4.043 | 4.043 | 0.06 | 1.06 | -0.28 | 0.72 | -0.23 | 0.77 | 32.23 | 24.41
2019-10-01 | 10:03 | 4.1406 | 4.1406 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 31.25 | 24.41
2019-10-01 | 10:03 | 4.2695 | 4.2695 | 0.04 | 1.04 | -0.3 | 0.7 | -0.24 | 0.76 | 33.2 | 24.41
2019-10-01 | 10:03 | 4.3594 | 4.3594 | 0.06 | 1.06 | -0.28 | 0.72 | -0.25 | 0.75 | 31.25 | 25.39
2019-10-01 | 10:03 | 4.4492 | 4.4492 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 31.25 | 24.41
2019-10-01 | 10:03 | 4.5703 | 4.5703 | 0.06 | 1.06 | -0.3 | 0.7 | -0.25 | 0.75 | 33.2 | 24.41
2019-10-01 | 10:03 | 4.6797 | 4.6797 | 0.06 | 1.06 | -0.29 | 0.71 | -0.26 | 0.74 | 32.23 | 24.41
2019-10-01 | 10:03 | 4.7695 | 4.7695 | 0.06 | 1.06 | -0.31 | 0.69 | -0.26 | 0.74 | 32.23 | 24.41
2019-10-01 | 10:03 | 4.8594 | 4.8594 | 0.04 | 1.04 | -0.28 | 0.72 | -0.25 | 0.75 | 32.23 | 24.41
2019-10-01 | 10:03 | 4.9727 | 4.9727 | -0.01 | 0.99 | -0.26 | 0.74 | -0.24 | 0.76 | 33.2 | 24.41
2019-10-01 | 10:03 | 5.082 | 5.082 | -0.02 | 0.98 | -0.24 | 0.76 | -0.23 | 0.77 | 32.23 | 24.41
2019-10-01 | 10:03 | 5.1719 | 5.1719 | -0.02 | 0.98 | -0.23 | 0.77 | -0.21 | 0.79 | 32.23 | 24.41
2019-10-01 | 10:03 | 5.2812 | 5.2812 | -0.01 | 0.99 | -0.23 | 0.77 | -0.23 | 0.77 | 32.23 | 25.39
2019-10-01 | 10:03 | 5.3828 | 5.3828 | 0.04 | 1.04 | -0.28 | 0.72 | -0.24 | 0.76 | 32.23 | 23.44
2019-10-01 | 10:03 | 5.4805 | 5.4805 | 0.04 | 1.04 | -0.29 | 0.71 | -0.24 | 0.76 | 31.25 | 23.44
2019-10-01 | 10:03 | 5.6016 | 5.6016 | 0.05 | 1.05 | -0.29 | 0.71 | -0.24 | 0.76 | 32.23 | 23.44
2019-10-01 | 10:03 | 5.6992 | 5.6992 | 0.04 | 1.04 | -0.31 | 0.69 | -0.25 | 0.75 | 34.18 | 24.41
2019-10-01 | 10:03 | 5.793 | 5.793 | 0.04 | 1.04 | -0.31 | 0.69 | -0.28 | 0.72 | 33.2 | 24.41
2019-10-01 | 10:03 | 5.8906 | 5.8906 | 0.04 | 1.04 | -0.33 | 0.67 | -0.27 | 0.73 | 34.18 | 24.41
2019-10-01 | 10:03 | 5.9922 | 5.9922 | 0.06 | 1.06 | -0.33 | 0.67 | -0.29 | 0.71 | 36.13 | 23.44
2019-10-01 | 10:03 | 6.1016 | 6.1016 | 0.06 | 1.06 | -0.34 | 0.66 | -0.29 | 0.71 | 38.09 | 24.41
2019-10-01 | 10:03 | 6.1992 | 6.1992 | 0.06 | 1.06 | -0.35 | 0.65 | -0.3 | 0.7 | 39.06 | 23.44 |  | noise in the sc water bath temperatures again
2019-10-01 | 10:03 | 6.3008 | 6.3008 | 0.06 | 1.06 | -0.36 | 0.64 | -0.32 | 0.68 | 41.02 | 23.44 |  | temperature equilibrium from 175 seconds
2019-10-01 | 10:03 | 6.4102 | 6.4102 | 0 | 1 | -0.33 | 0.67 | -0.31 | 0.69 | 43.95 | 25.39
2019-10-01 | 10:03 | 6.5117 | 6.5117 | -0.02 | 0.98 | -0.3 | 0.7 | -0.31 | 0.69 | 45.9 | 26.37 |  | minimum heat exchanger outlet temperature is: |  |  | 73.24 | average sc bath temp between 25 and 150 seconds |  | 25.8566
2019-10-01 | 10:03 | 6.6094 | 6.6094 | -0.02 | 0.98 | -0.31 | 0.69 | -0.31 | 0.69 | 47.85 | 24.41 |  | maximum heat exchanger outlet temperature is: |  |  | 80.08
2019-10-01 | 10:03 | 6.7109 | 6.7109 | -0.03 | 0.97 | -0.3 | 0.7 | -0.31 | 0.69 | 50.78 | 25.39
2019-10-01 | 10:03 | 6.8125 | 6.8125 | 0.03 | 1.03 | -0.36 | 0.64 | -0.31 | 0.69 | 50.78 | 23.44 |  | average HE outlet temperature is: |  |  | 75.984
2019-10-01 | 10:03 | 6.9297 | 6.9297 | 0.04 | 1.04 | -0.37 | 0.63 | -0.34 | 0.66 | 53.71 | 25.39
2019-10-01 | 10:03 | 7.0312 | 7.0312 | 0.04 | 1.04 | -0.4 | 0.6 | -0.35 | 0.65 | 57.62 | 24.41 |  | number of temperature points measured is: |  |  | 1257
2019-10-01 | 10:03 | 7.1211 | 7.1211 | 0.05 | 1.05 | -0.4 | 0.6 | -0.36 | 0.64 | 56.64 | 23.44
2019-10-01 | 10:03 | 7.2305 | 7.2305 | 0.05 | 1.05 | -0.41 | 0.59 | -0.37 | 0.63 | 59.57 | 24.41 |  | st dev he temp |  |  | 0.88257
2019-10-01 | 10:03 | 7.3398 | 7.3398 | 0.05 | 1.05 | -0.42 | 0.58 | -0.37 | 0.63 | 61.52 | 24.41
2019-10-01 | 10:03 | 7.4492 | 7.4492 | 0.05 | 1.05 | -0.44 | 0.56 | -0.37 | 0.63 | 62.5 | 25.39
2019-10-01 | 10:03 | 7.5625 | 7.5625 | 0.05 | 1.05 | -0.44 | 0.56 | -0.38 | 0.62 | 65.43 | 24.41
2019-10-01 | 10:03 | 7.6523 | 7.6523 | 0.05 | 1.05 | -0.44 | 0.56 | -0.4 | 0.6 | 65.43 | 23.44
2019-10-01 | 10:03 | 7.7617 | 7.7617 | 0.04 | 1.04 | -0.46 | 0.54 | -0.39 | 0.61 | 66.41 | 24.41
2019-10-01 | 10:03 | 7.8516 | 7.8516 | 0.05 | 1.05 | -0.45 | 0.55 | -0.41 | 0.59 | 67.38 | 25.39
2019-10-01 | 10:03 | 7.9609 | 7.9609 | -0.02 | 0.98 | -0.37 | 0.63 | -0.38 | 0.62 | 70.31 | 23.44
2019-10-01 | 10:03 | 8.0508 | 8.0508 | -0.04 | 0.96 | -0.37 | 0.63 | -0.38 | 0.62 | 69.34 | 24.41
2019-10-01 | 10:03 | 8.1602 | 8.1602 | -0.06 | 0.94 | -0.37 | 0.63 | -0.37 | 0.63 | 69.34 | 24.41
2019-10-01 | 10:03 | 8.2617 | 8.2617 | -0.05 | 0.95 | -0.36 | 0.64 | -0.38 | 0.62 | 70.31 | 24.41
2019-10-01 | 10:03 | 8.3516 | 8.3516 | 0.04 | 1.04 | -0.45 | 0.55 | -0.4 | 0.6 | 70.31 | 24.41
2019-10-01 | 10:03 | 8.4609 | 8.4609 | 0.04 | 1.04 | -0.46 | 0.54 | -0.4 | 0.6 | 70.31 | 24.41
2019-10-01 | 10:03 | 8.5625 | 8.5625 | 0.05 | 1.05 | -0.47 | 0.53 | -0.41 | 0.59 | 72.27 | 25.39
2019-10-01 | 10:03 | 8.6719 | 8.6719 | 0.04 | 1.04 | -0.48 | 0.52 | -0.43 | 0.57 | 72.27 | 25.39
2019-10-01 | 10:03 | 8.7695 | 8.7695 | 0.05 | 1.05 | -0.47 | 0.53 | -0.43 | 0.57 | 71.29 | 24.41
2019-10-01 | 10:03 | 8.8711 | 8.8711 | 0.06 | 1.06 | -0.48 | 0.52 | -0.43 | 0.57 | 71.29 | 24.41
2019-10-01 | 10:03 | 8.9727 | 8.9727 | 0.06 | 1.06 | -0.49 | 0.51 | -0.44 | 0.56 | 71.29 | 25.39
2019-10-01 | 10:03 | 9.0703 | 9.0703 | 0.07 | 1.07 | -0.48 | 0.52 | -0.44 | 0.56 | 72.27 | 25.39
2019-10-01 | 10:03 | 9.1797 | 9.1797 | 0.05 | 1.05 | -0.49 | 0.51 | -0.45 | 0.55 | 70.31 | 24.41
2019-10-01 | 10:03 | 9.2812 | 9.2812 | 0.06 | 1.06 | -0.5 | 0.5 | -0.46 | 0.54 | 70.31 | 24.41
2019-10-01 | 10:03 | 9.3906 | 9.3906 | 0.02 | 1.02 | -0.46 | 0.54 | -0.44 | 0.56 | 72.27 | 24.41
2019-10-01 | 10:03 | 9.4805 | 9.4805 | -0.03 | 0.97 | -0.41 | 0.59 | -0.43 | 0.57 | 71.29 | 24.41
2019-10-01 | 10:03 | 9.5898 | 9.5898 | -0.05 | 0.95 | -0.4 | 0.6 | -0.42 | 0.58 | 71.29 | 24.41
2019-10-01 | 10:03 | 9.6914 | 9.6914 | -0.05 | 0.95 | -0.39 | 0.61 | -0.42 | 0.58 | 70.31 | 24.41
2019-10-01 | 10:03 | 9.8008 | 9.8008 | -0.07 | 0.93 | -0.38 | 0.62 | -0.4 | 0.6 | 72.27 | 24.41
2019-10-01 | 10:03 | 9.9219 | 9.9219 | 0.04 | 1.04 | -0.49 | 0.51 | -0.43 | 0.57 | 70.31 | 24.41
2019-10-01 | 10:03 | 10.0195 | 10.0195 | 0.05 | 1.05 | -0.51 | 0.49 | -0.44 | 0.56 | 70.31 | 25.39
2019-10-01 | 10:03 | 10.1094 | 10.1094 | 0.05 | 1.05 | -0.5 | 0.5 | -0.44 | 0.56 | 70.31 | 24.41
2019-10-01 | 10:03 | 10.2227 | 10.2227 | 0.04 | 1.04 | -0.5 | 0.5 | -0.46 | 0.54 | 70.31 | 26.37
2019-10-01 | 10:03 | 10.3125 | 10.3125 | 0.06 | 1.06 | -0.53 | 0.47 | -0.47 | 0.53 | 71.29 | 24.41
2019-10-01 | 10:03 | 10.4102 | 10.4102 | 0.05 | 1.05 | -0.5 | 0.5 | -0.46 | 0.54 | 70.31 | 24.41
2019-10-01 | 10:03 | 10.5195 | 10.5195 | 0.05 | 1.05 | -0.52 | 0.48 | -0.47 | 0.53 | 69.34 | 26.37
2019-10-01 | 10:03 | 10.6094 | 10.6094 | 0.06 | 1.06 | -0.52 | 0.48 | -0.46 | 0.54 | 70.31 | 23.44
2019-10-01 | 10:03 | 10.7227 | 10.7227 | 0.05 | 1.05 | -0.53 | 0.47 | -0.48 | 0.52 | 69.34 | 24.41
2019-10-01 | 10:03 | 10.8203 | 10.8203 | 0.05 | 1.05 | -0.52 | 0.48 | -0.47 | 0.53 | 71.29 | 23.44
2019-10-01 | 10:03 | 10.9297 | 10.9297 | -0.02 | 0.98 | -0.46 | 0.54 | -0.46 | 0.54 | 69.34 | 24.41
2019-10-01 | 10:03 | 11.0312 | 11.0312 | -0.05 | 0.95 | -0.42 | 0.58 | -0.44 | 0.56 | 70.31 | 24.41
2019-10-01 | 10:03 | 11.1328 | 11.1328 | -0.07 | 0.93 | -0.42 | 0.58 | -0.45 | 0.55 | 70.31 | 25.39
2019-10-01 | 10:03 | 11.2305 | 11.2305 | -0.08 | 0.92 | -0.4 | 0.6 | -0.44 | 0.56 | 70.31 | 24.41
2019-10-01 | 10:03 | 11.332 | 11.332 | 0.03 | 1.03 | -0.5 | 0.5 | -0.47 | 0.53 | 70.31 | 24.41
2019-10-01 | 10:03 | 11.4414 | 11.4414 | 0.04 | 1.04 | -0.53 | 0.47 | -0.47 | 0.53 | 70.31 | 24.41
2019-10-01 | 10:03 | 11.543 | 11.543 | 0.05 | 1.05 | -0.53 | 0.47 | -0.5 | 0.5 | 69.34 | 24.41
2019-10-01 | 10:03 | 11.6406 | 11.6406 | 0.05 | 1.05 | -0.55 | 0.45 | -0.51 | 0.49 | 69.34 | 24.41
2019-10-01 | 10:03 | 11.75 | 11.75 | 0.05 | 1.05 | -0.54 | 0.46 | -0.5 | 0.5 | 69.34 | 25.39
2019-10-01 | 10:03 | 11.8398 | 11.8398 | 0.05 | 1.05 | -0.57 | 0.43 | -0.5 | 0.5 | 69.34 | 25.39
2019-10-01 | 10:03 | 11.9727 | 11.9727 | 0.06 | 1.06 | -0.56 | 0.44 | -0.52 | 0.48 | 69.34 | 25.39
2019-10-01 | 10:03 | 12.082 | 12.082 | 0.06 | 1.06 | -0.56 | 0.44 | -0.51 | 0.49 | 70.31 | 25.39
2019-10-01 | 10:03 | 12.1719 | 12.1719 | 0.06 | 1.06 | -0.57 | 0.43 | -0.51 | 0.49 | 69.34 | 24.41
2019-10-01 | 10:03 | 12.2695 | 12.2695 | 0.04 | 1.04 | -0.57 | 0.43 | -0.52 | 0.48 | 69.34 | 24.41
2019-10-01 | 10:03 | 12.3828 | 12.3828 | 0.05 | 1.05 | -0.57 | 0.43 | -0.53 | 0.47 | 70.31 | 24.41
2019-10-01 | 10:03 | 12.4805 | 12.4805 | 0 | 1 | -0.51 | 0.49 | -0.51 | 0.49 | 69.34 | 26.37
2019-10-01 | 10:03 | 12.582 | 12.582 | -0.07 | 0.93 | -0.44 | 0.56 | -0.49 | 0.51 | 71.29 | 25.39
2019-10-01 | 10:03 | 12.6719 | 12.6719 | -0.08 | 0.92 | -0.44 | 0.56 | -0.49 | 0.51 | 69.34 | 25.39
2019-10-01 | 10:03 | 12.7695 | 12.7695 | -0.09 | 0.91 | -0.42 | 0.58 | -0.49 | 0.51 | 69.34 | 25.39
2019-10-01 | 10:03 | 12.8828 | 12.8828 | 0.02 | 1.02 | -0.57 | 0.43 | -0.51 | 0.49 | 70.31 | 24.41
2019-10-01 | 10:03 | 12.9805 | 12.9805 | 0.04 | 1.04 | -0.57 | 0.43 | -0.53 | 0.47 | 69.34 | 24.41
2019-10-01 | 10:03 | 13.082 | 13.082 | 0.05 | 1.05 | -0.57 | 0.43 | -0.53 | 0.47 | 69.34 | 24.41
2019-10-01 | 10:03 | 13.1797 | 13.1797 | 0.05 | 1.05 | -0.58 | 0.42 | -0.53 | 0.47 | 70.31 | 24.41
2019-10-01 | 10:03 | 13.2812 | 13.2812 | 0.05 | 1.05 | -0.6 | 0.4 | -0.53 | 0.47 | 69.34 | 23.44
2019-10-01 | 10:03 | 13.4023 | 13.4023 | 0.06 | 1.06 | -0.6 | 0.4 | -0.54 | 0.46 | 70.31 | 25.39
2019-10-01 | 10:03 | 13.4922 | 13.4922 | 0.05 | 1.05 | -0.6 | 0.4 | -0.55 | 0.45 | 69.34 | 25.39
2019-10-01 | 10:03 | 13.6016 | 13.6016 | 0.04 | 1.04 | -0.61 | 0.39 | -0.55 | 0.45 | 69.34 | 25.39
2019-10-01 | 10:03 | 13.7109 | 13.7109 | 0.05 | 1.05 | -0.62 | 0.38 | -0.56 | 0.44 | 70.31 | 24.41
2019-10-01 | 10:03 | 13.8125 | 13.8125 | 0.06 | 1.06 | -0.61 | 0.39 | -0.57 | 0.43 | 70.31 | 26.37
2019-10-01 | 10:03 | 13.9102 | 13.9102 | 0.04 | 1.04 | -0.59 | 0.41 | -0.57 | 0.43 | 70.31 | 24.41
2019-10-01 | 10:03 | 14.0117 | 14.0117 | -0.02 | 0.98 | -0.52 | 0.48 | -0.53 | 0.47 | 69.34 | 24.41
2019-10-01 | 10:03 | 14.1328 | 14.1328 | -0.08 | 0.92 | -0.47 | 0.53 | -0.54 | 0.46 | 70.31 | 25.39
2019-10-01 | 10:03 | 14.2305 | 14.2305 | -0.09 | 0.91 | -0.47 | 0.53 | -0.53 | 0.47 | 69.34 | 25.39
2019-10-01 | 10:03 | 14.3203 | 14.3203 | -0.01 | 0.99 | -0.54 | 0.46 | -0.53 | 0.47 | 69.34 | 24.41
2019-10-01 | 10:03 | 14.4102 | 14.4102 | 0.04 | 1.04 | -0.6 | 0.4 | -0.55 | 0.45 | 69.34 | 24.41
2019-10-01 | 10:03 | 14.5312 | 14.5312 | 0.04 | 1.04 | -0.62 | 0.38 | -0.57 | 0.43 | 69.34 | 26.37
2019-10-01 | 10:03 | 14.6406 | 14.6406 | 0.05 | 1.05 | -0.62 | 0.38 | -0.56 | 0.44 | 70.31 | 25.39
2019-10-01 | 10:03 | 14.7422 | 14.7422 | 0.04 | 1.04 | -0.62 | 0.38 | -0.56 | 0.44 | 69.34 | 25.39
2019-10-01 | 10:03 | 14.8398 | 14.8398 | 0.05 | 1.05 | -0.63 | 0.37 | -0.58 | 0.42 | 69.34 | 25.39
2019-10-01 | 10:03 | 14.9297 | 14.9297 | 0.05 | 1.05 | -0.61 | 0.39 | -0.57 | 0.43 | 69.34 | 26.37
2019-10-01 | 10:03 | 15.043 | 15.043 | 0.06 | 1.06 | -0.63 | 0.37 | -0.58 | 0.42 | 69.34 | 25.39
2019-10-01 | 10:03 | 15.1406 | 15.1406 | 0.06 | 1.06 | -0.62 | 0.38 | -0.58 | 0.42 | 70.31 | 24.41
2019-10-01 | 10:03 | 15.2422 | 15.2422 | 0.05 | 1.05 | -0.65 | 0.35 | -0.59 | 0.41 | 69.34 | 24.41
2019-10-01 | 10:03 | 15.3398 | 15.3398 | 0.06 | 1.06 | -0.64 | 0.36 | -0.59 | 0.41 | 68.36 | 24.41
2019-10-01 | 10:03 | 15.4414 | 15.4414 | -0.01 | 0.99 | -0.54 | 0.46 | -0.59 | 0.41 | 69.34 | 25.39
2019-10-01 | 10:03 | 15.5508 | 15.5508 | -0.06 | 0.94 | -0.5 | 0.5 | -0.56 | 0.44 | 70.31 | 25.39
2019-10-01 | 10:03 | 15.6719 | 15.6719 | -0.09 | 0.91 | -0.49 | 0.51 | -0.54 | 0.46 | 70.31 | 25.39
2019-10-01 | 10:03 | 15.7695 | 15.7695 | -0.1 | 0.9 | -0.46 | 0.54 | -0.53 | 0.47 | 70.31 | 25.39
2019-10-01 | 10:03 | 15.8594 | 15.8594 | 0.04 | 1.04 | -0.61 | 0.39 | -0.56 | 0.44 | 69.34 | 24.41
2019-10-01 | 10:03 | 15.9727 | 15.9727 | 0.04 | 1.04 | -0.62 | 0.38 | -0.57 | 0.43 | 69.34 | 24.41
2019-10-01 | 10:03 | 16.0625 | 16.0625 | 0.05 | 1.05 | -0.63 | 0.37 | -0.57 | 0.43 | 70.31 | 27.34
2019-10-01 | 10:03 | 16.1719 | 16.1719 | 0.05 | 1.05 | -0.64 | 0.36 | -0.59 | 0.41 | 70.31 | 25.39
2019-10-01 | 10:03 | 16.2695 | 16.2695 | 0.04 | 1.04 | -0.63 | 0.37 | -0.6 | 0.4 | 69.34 | 25.39
2019-10-01 | 10:03 | 16.3828 | 16.3828 | 0.05 | 1.05 | -0.65 | 0.35 | -0.58 | 0.42 | 70.31 | 26.37
2019-10-01 | 10:03 | 16.4727 | 16.4727 | 0.05 | 1.05 | -0.65 | 0.35 | -0.6 | 0.4 | 68.36 | 25.39
2019-10-01 | 10:03 | 16.5703 | 16.5703 | 0.05 | 1.05 | -0.66 | 0.34 | -0.6 | 0.4 | 68.36 | 25.39
2019-10-01 | 10:03 | 16.6797 | 16.6797 | 0.06 | 1.06 | -0.65 | 0.35 | -0.59 | 0.41 | 69.34 | 24.41
2019-10-01 | 10:03 | 16.7812 | 16.7812 | 0.05 | 1.05 | -0.66 | 0.34 | -0.62 | 0.38 | 68.36 | 24.41
2019-10-01 | 10:03 | 16.8828 | 16.8828 | 0.07 | 1.07 | -0.66 | 0.34 | -0.6 | 0.4 | 69.34 | 27.34
2019-10-01 | 10:03 | 16.9805 | 16.9805 | -0.05 | 0.95 | -0.56 | 0.44 | -0.58 | 0.42 | 69.34 | 25.39
2019-10-01 | 10:03 | 17.0898 | 17.0898 | -0.08 | 0.92 | -0.51 | 0.49 | -0.58 | 0.42 | 68.36 | 24.41
2019-10-01 | 10:03 | 17.1992 | 17.1992 | -0.1 | 0.9 | -0.49 | 0.51 | -0.58 | 0.42 | 69.34 | 25.39
2019-10-01 | 10:03 | 17.3125 | 17.3125 | -0.11 | 0.89 | -0.47 | 0.53 | -0.57 | 0.43 | 68.36 | 25.39
2019-10-01 | 10:03 | 17.4023 | 17.4023 | 0.04 | 1.04 | -0.64 | 0.36 | -0.6 | 0.4 | 70.31 | 26.37
2019-10-01 | 10:03 | 17.5195 | 17.5195 | 0.04 | 1.04 | -0.64 | 0.36 | -0.59 | 0.41 | 68.36 | 25.39
2019-10-01 | 10:03 | 17.6211 | 17.6211 | 0.04 | 1.04 | -0.65 | 0.35 | -0.6 | 0.4 | 68.36 | 25.39
2019-10-01 | 10:03 | 17.7227 | 17.7227 | 0.04 | 1.04 | -0.65 | 0.35 | -0.61 | 0.39 | 68.36 | 24.41
2019-10-01 | 10:03 | 17.8125 | 17.8125 | 0.05 | 1.05 | -0.67 | 0.33 | -0.61 | 0.39 | 68.36 | 25.39
2019-10-01 | 10:03 | 17.9102 | 17.9102 | 0.05 | 1.05 | -0.66 | 0.34 | -0.63 | 0.37 | 68.36 | 25.39
2019-10-01 | 10:03 | 18.0117 | 18.0117 | 0.05 | 1.05 | -0.66 | 0.34 | -0.62 | 0.38 | 69.34 | 25.39
2019-10-01 | 10:03 | 18.1094 | 18.1094 | 0.07 | 1.07 | -0.67 | 0.33 | -0.62 | 0.38 | 71.29 | 26.37
2019-10-01 | 10:03 | 18.2227 | 18.2227 | 0.06 | 1.06 | -0.67 | 0.33 | -0.63 | 0.37 | 69.34 | 24.41
2019-10-01 | 10:03 | 18.3203 | 18.3203 | 0.05 | 1.05 | -0.68 | 0.32 | -0.62 | 0.38 | 68.36 | 25.39
2019-10-01 | 10:03 | 18.4297 | 18.4297 | 0.05 | 1.05 | -0.67 | 0.33 | -0.62 | 0.38 | 68.36 | 25.39
2019-10-01 | 10:03 | 18.5625 | 18.5625 | -0.08 | 0.92 | -0.54 | 0.46 | -0.61 | 0.39 | 67.38 | 25.39
2019-10-01 | 10:03 | 18.6406 | 18.6406 | -0.1 | 0.9 | -0.5 | 0.5 | -0.59 | 0.41 | 69.34 | 26.37
2019-10-01 | 10:03 | 18.7617 | 18.7617 | -0.09 | 0.91 | -0.5 | 0.5 | -0.59 | 0.41 | 70.31 | 24.41
2019-10-01 | 10:03 | 18.8594 | 18.8594 | 0.03 | 1.03 | -0.62 | 0.38 | -0.59 | 0.41 | 68.36 | 26.37
2019-10-01 | 10:03 | 18.9492 | 18.9492 | 0.04 | 1.04 | -0.66 | 0.34 | -0.62 | 0.38 | 68.36 | 25.39
2019-10-01 | 10:03 | 19.0508 | 19.0508 | 0.05 | 1.05 | -0.66 | 0.34 | -0.61 | 0.39 | 68.36 | 24.41
2019-10-01 | 10:03 | 19.1523 | 19.1523 | 0.04 | 1.04 | -0.67 | 0.33 | -0.61 | 0.39 | 68.36 | 25.39
2019-10-01 | 10:03 | 19.2695 | 19.2695 | 0.04 | 1.04 | -0.68 | 0.32 | -0.63 | 0.37 | 69.34 | 24.41
2019-10-01 | 10:03 | 19.3516 | 19.3516 | 0.05 | 1.05 | -0.69 | 0.31 | -0.65 | 0.35 | 69.34 | 25.39
2019-10-01 | 10:03 | 19.4492 | 19.4492 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 68.36 | 26.37
2019-10-01 | 10:03 | 19.5625 | 19.5625 | 0.04 | 1.04 | -0.69 | 0.31 | -0.64 | 0.36 | 68.36 | 25.39
2019-10-01 | 10:03 | 19.6602 | 19.6602 | 0.05 | 1.05 | -0.68 | 0.32 | -0.64 | 0.36 | 68.36 | 25.39
2019-10-01 | 10:03 | 19.7617 | 19.7617 | 0.05 | 1.05 | -0.7 | 0.3 | -0.64 | 0.36 | 68.36 | 25.39
2019-10-01 | 10:03 | 19.8906 | 19.8906 | 0.06 | 1.06 | -0.7 | 0.3 | -0.65 | 0.35 | 67.38 | 25.39
2019-10-01 | 10:03 | 19.9922 | 19.9922 | 0.01 | 1.01 | -0.64 | 0.36 | -0.64 | 0.36 | 68.36 | 25.39
2019-10-01 | 10:03 | 20.0898 | 20.0898 | -0.09 | 0.91 | -0.53 | 0.47 | -0.62 | 0.38 | 70.31 | 26.37
2019-10-01 | 10:03 | 20.1719 | 20.1719 | -0.11 | 0.89 | -0.52 | 0.48 | -0.6 | 0.4 | 67.38 | 25.39
2019-10-01 | 10:03 | 20.2812 | 20.2812 | -0.12 | 0.88 | -0.51 | 0.49 | -0.6 | 0.4 | 69.34 | 26.37
2019-10-01 | 10:03 | 20.3828 | 20.3828 | 0.03 | 1.03 | -0.67 | 0.33 | -0.61 | 0.39 | 69.34 | 26.37
2019-10-01 | 10:03 | 20.4805 | 20.4805 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 68.36 | 26.37
2019-10-01 | 10:03 | 20.582 | 20.582 | 0.04 | 1.04 | -0.69 | 0.31 | -0.63 | 0.37 | 69.34 | 26.37
2019-10-01 | 10:03 | 20.6797 | 20.6797 | 0.04 | 1.04 | -0.71 | 0.29 | -0.64 | 0.36 | 67.38 | 27.34
2019-10-01 | 10:03 | 20.8125 | 20.8125 | 0.06 | 1.06 | -0.71 | 0.29 | -0.63 | 0.37 | 68.36 | 28.32
2019-10-01 | 10:03 | 20.9102 | 20.9102 | 0.04 | 1.04 | -0.7 | 0.3 | -0.65 | 0.35 | 67.38 | 25.39
2019-10-01 | 10:03 | 21 | 21 | 0.06 | 1.06 | -0.7 | 0.3 | -0.64 | 0.36 | 69.34 | 26.37
2019-10-01 | 10:03 | 21.1016 | 21.1016 | 0.05 | 1.05 | -0.7 | 0.3 | -0.63 | 0.37 | 68.36 | 27.34
2019-10-01 | 10:03 | 21.1992 | 21.1992 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 67.38 | 25.39
2019-10-01 | 10:03 | 21.3008 | 21.3008 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 68.36 | 24.41
2019-10-01 | 10:03 | 21.4023 | 21.4023 | 0.06 | 1.06 | -0.71 | 0.29 | -0.66 | 0.34 | 67.38 | 24.41
2019-10-01 | 10:03 | 21.5 | 21.5 | -0.05 | 0.95 | -0.6 | 0.4 | -0.64 | 0.36 | 69.34 | 26.37
2019-10-01 | 10:03 | 21.6094 | 21.6094 | -0.1 | 0.9 | -0.55 | 0.45 | -0.63 | 0.37 | 69.34 | 27.34
2019-10-01 | 10:03 | 21.7109 | 21.7109 | -0.11 | 0.89 | -0.54 | 0.46 | -0.62 | 0.38 | 68.36 | 25.39
2019-10-01 | 10:03 | 21.8203 | 21.8203 | -0.05 | 0.95 | -0.57 | 0.43 | -0.63 | 0.37 | 67.38 | 24.41
2019-10-01 | 10:03 | 21.9219 | 21.9219 | 0.04 | 1.04 | -0.7 | 0.3 | -0.63 | 0.37 | 67.38 | 27.34
2019-10-01 | 10:03 | 22.0195 | 22.0195 | 0.04 | 1.04 | -0.72 | 0.28 | -0.64 | 0.36 | 67.38 | 25.39
2019-10-01 | 10:03 | 22.1211 | 22.1211 | 0.04 | 1.04 | -0.72 | 0.28 | -0.64 | 0.36 | 67.38 | 24.41
2019-10-01 | 10:03 | 22.2422 | 22.2422 | 0.04 | 1.04 | -0.74 | 0.26 | -0.66 | 0.34 | 67.38 | 24.41
2019-10-01 | 10:03 | 22.3398 | 22.3398 | 0.05 | 1.05 | -0.73 | 0.27 | -0.66 | 0.34 | 68.36 | 26.37
2019-10-01 | 10:03 | 22.4414 | 22.4414 | 0.06 | 1.06 | -0.74 | 0.26 | -0.66 | 0.34 | 66.41 | 25.39
2019-10-01 | 10:03 | 22.543 | 22.543 | 0.05 | 1.05 | -0.72 | 0.28 | -0.66 | 0.34 | 68.36 | 26.37
2019-10-01 | 10:03 | 22.6523 | 22.6523 | 0.06 | 1.06 | -0.74 | 0.26 | -0.65 | 0.35 | 69.34 | 27.34
2019-10-01 | 10:03 | 22.7422 | 22.7422 | 0.05 | 1.05 | -0.73 | 0.27 | -0.67 | 0.33 | 69.34 | 27.34
2019-10-01 | 10:03 | 22.8398 | 22.8398 | 0.05 | 1.05 | -0.75 | 0.25 | -0.65 | 0.35 | 69.34 | 25.39
2019-10-01 | 10:03 | 22.9414 | 22.9414 | 0.04 | 1.04 | -0.71 | 0.29 | -0.65 | 0.35 | 68.36 | 25.39
2019-10-01 | 10:03 | 23.0508 | 23.0508 | -0.07 | 0.93 | -0.6 | 0.4 | -0.65 | 0.35 | 68.36 | 26.37
2019-10-01 | 10:03 | 23.1719 | 23.1719 | -0.11 | 0.89 | -0.56 | 0.44 | -0.63 | 0.37 | 69.34 | 26.37
2019-10-01 | 10:03 | 23.2695 | 23.2695 | -0.1 | 0.9 | -0.55 | 0.45 | -0.62 | 0.38 | 68.36 | 26.37
2019-10-01 | 10:03 | 23.3711 | 23.3711 | 0.03 | 1.03 | -0.7 | 0.3 | -0.64 | 0.36 | 68.36 | 26.37
2019-10-01 | 10:03 | 23.4727 | 23.4727 | 0.04 | 1.04 | -0.73 | 0.27 | -0.64 | 0.36 | 67.38 | 26.37
2019-10-01 | 10:03 | 23.5625 | 23.5625 | 0.04 | 1.04 | -0.74 | 0.26 | -0.65 | 0.35 | 67.38 | 26.37
2019-10-01 | 10:03 | 23.6719 | 23.6719 | 0.04 | 1.04 | -0.74 | 0.26 | -0.66 | 0.34 | 67.38 | 26.37
2019-10-01 | 10:03 | 23.7695 | 23.7695 | 0.06 | 1.06 | -0.74 | 0.26 | -0.66 | 0.34 | 67.38 | 26.37
2019-10-01 | 10:03 | 23.9023 | 23.9023 | 0.04 | 1.04 | -0.74 | 0.26 | -0.65 | 0.35 | 67.38 | 25.39
2019-10-01 | 10:03 | 24 | 24 | 0.05 | 1.05 | -0.75 | 0.25 | -0.67 | 0.33 | 67.38 | 26.37
2019-10-01 | 10:03 | 24.1016 | 24.1016 | 0.05 | 1.05 | -0.76 | 0.24 | -0.66 | 0.34 | 68.36 | 27.34
2019-10-01 | 10:03 | 24.1992 | 24.1992 | 0.05 | 1.05 | -0.75 | 0.25 | -0.67 | 0.33 | 68.36 | 28.32
2019-10-01 | 10:03 | 24.3125 | 24.3125 | 0.06 | 1.06 | -0.75 | 0.25 | -0.67 | 0.33 | 67.38 | 25.39
2019-10-01 | 10:03 | 24.4102 | 24.4102 | 0.07 | 1.07 | -0.76 | 0.24 | -0.68 | 0.32 | 67.38 | 25.39
2019-10-01 | 10:03 | 24.4922 | 24.4922 | -0.03 | 0.97 | -0.64 | 0.36 | -0.65 | 0.35 | 69.34 | 26.37
2019-10-01 | 10:03 | 24.5898 | 24.5898 | -0.09 | 0.91 | -0.59 | 0.41 | -0.64 | 0.36 | 68.36 | 27.34
2019-10-01 | 10:03 | 24.6992 | 24.6992 | -0.11 | 0.89 | -0.56 | 0.44 | -0.64 | 0.36 | 67.38 | 26.37
2019-10-01 | 10:03 | 24.8203 | 24.8203 | -0.12 | 0.88 | -0.58 | 0.42 | -0.62 | 0.38 | 67.38 | 27.34
2019-10-01 | 10:03 | 24.9297 | 24.9297 | 0.04 | 1.04 | -0.73 | 0.27 | -0.64 | 0.36 | 68.36 | 26.37
2019-10-01 | 10:03 | 25.0117 | 25.0117 | 0.04 | 1.04 | -0.73 | 0.27 | -0.65 | 0.35 | 67.38 | 26.37
2019-10-01 | 10:03 | 25.1016 | 25.1016 | 0.04 | 1.04 | -0.75 | 0.25 | -0.65 | 0.35 | 66.41 | 25.39
2019-10-01 | 10:03 | 25.2109 | 25.2109 | 0.05 | 1.05 | -0.75 | 0.25 | -0.66 | 0.34 | 67.38 | 24.41
2019-10-01 | 10:03 | 25.3125 | 25.3125 | 0.06 | 1.06 | -0.76 | 0.24 | -0.67 | 0.33 | 66.41 | 26.37
2019-10-01 | 10:03 | 25.4297 | 25.4297 | 0.06 | 1.06 | -0.77 | 0.23 | -0.66 | 0.34 | 67.38 | 25.39
2019-10-01 | 10:03 | 25.5312 | 25.5312 | 0.07 | 1.07 | -0.78 | 0.22 | -0.68 | 0.32 | 66.41 | 26.37
2019-10-01 | 10:03 | 25.6406 | 25.6406 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 66.41 | 25.39
2019-10-01 | 10:03 | 25.7305 | 25.7305 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 66.41 | 26.37
2019-10-01 | 10:03 | 25.8203 | 25.8203 | 0.04 | 1.04 | -0.77 | 0.23 | -0.67 | 0.33 | 66.41 | 25.39
2019-10-01 | 10:03 | 25.9219 | 25.9219 | 0.05 | 1.05 | -0.77 | 0.23 | -0.68 | 0.32 | 67.38 | 25.39
2019-10-01 | 10:03 | 26.0312 | 26.0312 | -0.05 | 0.95 | -0.65 | 0.35 | -0.67 | 0.33 | 66.41 | 26.37
2019-10-01 | 10:03 | 26.1328 | 26.1328 | -0.09 | 0.91 | -0.6 | 0.4 | -0.65 | 0.35 | 67.38 | 26.37
2019-10-01 | 10:03 | 26.2305 | 26.2305 | -0.12 | 0.88 | -0.59 | 0.41 | -0.64 | 0.36 | 66.41 | 25.39
2019-10-01 | 10:03 | 26.3398 | 26.3398 | 0.01 | 1.01 | -0.7 | 0.3 | -0.64 | 0.36 | 66.41 | 24.41
2019-10-01 | 10:03 | 26.4414 | 26.4414 | 0.04 | 1.04 | -0.75 | 0.25 | -0.65 | 0.35 | 66.41 | 26.37
2019-10-01 | 10:03 | 26.5508 | 26.5508 | 0.04 | 1.04 | -0.76 | 0.24 | -0.66 | 0.34 | 66.41 | 25.39
2019-10-01 | 10:03 | 26.6406 | 26.6406 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 66.41 | 25.39
2019-10-01 | 10:03 | 26.75 | 26.75 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 66.41 | 25.39
2019-10-01 | 10:03 | 26.8516 | 26.8516 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 67.38 | 25.39
2019-10-01 | 10:03 | 26.9609 | 26.9609 | 0.04 | 1.04 | -0.77 | 0.23 | -0.68 | 0.32 | 66.41 | 25.39
2019-10-01 | 10:03 | 27.0625 | 27.0625 | 0.05 | 1.05 | -0.77 | 0.23 | -0.66 | 0.34 | 67.38 | 25.39
2019-10-01 | 10:03 | 27.1523 | 27.1523 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 66.41 | 25.39
2019-10-01 | 10:03 | 27.2812 | 27.2812 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 66.41 | 25.39
2019-10-01 | 10:03 | 27.3906 | 27.3906 | 0.07 | 1.07 | -0.78 | 0.22 | -0.67 | 0.33 | 67.38 | 25.39
2019-10-01 | 10:03 | 27.4805 | 27.4805 | 0.02 | 1.02 | -0.74 | 0.26 | -0.68 | 0.32 | 68.36 | 24.41
2019-10-01 | 10:03 | 27.6016 | 27.6016 | -0.08 | 0.92 | -0.63 | 0.37 | -0.65 | 0.35 | 67.38 | 26.37
2019-10-01 | 10:03 | 27.6719 | 27.6719 | -0.12 | 0.88 | -0.59 | 0.41 | -0.65 | 0.35 | 67.38 | 25.39
2019-10-01 | 10:03 | 27.7812 | 27.7812 | -0.12 | 0.88 | -0.57 | 0.43 | -0.63 | 0.37 | 68.36 | 26.37
2019-10-01 | 10:03 | 27.8828 | 27.8828 | 0.03 | 1.03 | -0.73 | 0.27 | -0.65 | 0.35 | 66.41 | 25.39
2019-10-01 | 10:03 | 27.9805 | 27.9805 | 0.04 | 1.04 | -0.75 | 0.25 | -0.66 | 0.34 | 68.36 | 27.34
2019-10-01 | 10:03 | 28.0898 | 28.0898 | 0.04 | 1.04 | -0.76 | 0.24 | -0.66 | 0.34 | 67.38 | 26.37
2019-10-01 | 10:03 | 28.1914 | 28.1914 | 0.04 | 1.04 | -0.77 | 0.23 | -0.66 | 0.34 | 67.38 | 27.34
2019-10-01 | 10:03 | 28.293 | 28.293 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 66.41 | 24.41
2019-10-01 | 10:03 | 28.3906 | 28.3906 | 0.06 | 1.06 | -0.77 | 0.23 | -0.67 | 0.33 | 67.38 | 27.34
2019-10-01 | 10:03 | 28.4922 | 28.4922 | 0.05 | 1.05 | -0.78 | 0.22 | -0.66 | 0.34 | 66.41 | 26.37
2019-10-01 | 10:03 | 28.6211 | 28.6211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 67.38 | 26.37
2019-10-01 | 10:03 | 28.7227 | 28.7227 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 67.38 | 27.34
2019-10-01 | 10:03 | 28.8125 | 28.8125 | 0.06 | 1.06 | -0.78 | 0.22 | -0.67 | 0.33 | 67.38 | 25.39
2019-10-01 | 10:03 | 28.9297 | 28.9297 | 0.05 | 1.05 | -0.77 | 0.23 | -0.69 | 0.31 | 66.41 | 25.39
2019-10-01 | 10:03 | 29.0195 | 29.0195 | -0.05 | 0.95 | -0.67 | 0.33 | -0.67 | 0.33 | 66.41 | 24.41
2019-10-01 | 10:03 | 29.1094 | 29.1094 | -0.12 | 0.88 | -0.62 | 0.38 | -0.64 | 0.36 | 68.36 | 26.37
2019-10-01 | 10:03 | 29.2227 | 29.2227 | -0.11 | 0.89 | -0.59 | 0.41 | -0.64 | 0.36 | 67.38 | 26.37
2019-10-01 | 10:03 | 29.3203 | 29.3203 | -0.09 | 0.91 | -0.62 | 0.38 | -0.63 | 0.37 | 68.36 | 26.37
2019-10-01 | 10:03 | 29.4219 | 29.4219 | 0.03 | 1.03 | -0.74 | 0.26 | -0.64 | 0.36 | 67.38 | 27.34
2019-10-01 | 10:03 | 29.543 | 29.543 | 0.04 | 1.04 | -0.76 | 0.24 | -0.65 | 0.35 | 68.36 | 26.37
2019-10-01 | 10:03 | 29.6406 | 29.6406 | 0.05 | 1.05 | -0.76 | 0.24 | -0.66 | 0.34 | 68.36 | 26.37
2019-10-01 | 10:03 | 29.75 | 29.75 | 0.04 | 1.04 | -0.76 | 0.24 | -0.65 | 0.35 | 66.41 | 26.37
2019-10-01 | 10:03 | 29.832 | 29.832 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 67.38 | 25.39
2019-10-01 | 10:03 | 29.9414 | 29.9414 | 0.04 | 1.04 | -0.78 | 0.22 | -0.66 | 0.34 | 67.38 | 27.34
2019-10-01 | 10:03 | 30.043 | 30.043 | 0.04 | 1.04 | -0.78 | 0.22 | -0.67 | 0.33 | 68.36 | 26.37
2019-10-01 | 10:03 | 30.1406 | 30.1406 | 0.05 | 1.05 | -0.78 | 0.22 | -0.67 | 0.33 | 68.36 | 25.39
2019-10-01 | 10:03 | 30.2422 | 30.2422 | 0.05 | 1.05 | -0.78 | 0.22 | -0.66 | 0.34 | 67.38 | 25.39
2019-10-01 | 10:03 | 30.3398 | 30.3398 | 0.06 | 1.06 | -0.78 | 0.22 | -0.68 | 0.32 | 67.38 | 27.34
2019-10-01 | 10:03 | 30.4492 | 30.4492 | 0.04 | 1.04 | -0.75 | 0.25 | -0.66 | 0.34 | 68.36 | 25.39
2019-10-01 | 10:03 | 30.5508 | 30.5508 | -0.09 | 0.91 | -0.63 | 0.37 | -0.65 | 0.35 | 68.36 | 25.39
2019-10-01 | 10:03 | 30.6523 | 30.6523 | -0.12 | 0.88 | -0.6 | 0.4 | -0.63 | 0.37 | 68.36 | 26.37
2019-10-01 | 10:03 | 30.7617 | 30.7617 | -0.12 | 0.88 | -0.58 | 0.42 | -0.63 | 0.37 | 68.36 | 26.37
2019-10-01 | 10:03 | 30.8594 | 30.8594 | 0.02 | 1.02 | -0.72 | 0.28 | -0.63 | 0.37 | 68.36 | 25.39
2019-10-01 | 10:03 | 30.9727 | 30.9727 | 0.04 | 1.04 | -0.75 | 0.25 | -0.62 | 0.38 | 67.38 | 25.39
2019-10-01 | 10:03 | 31.0703 | 31.0703 | 0.04 | 1.04 | -0.76 | 0.24 | -0.66 | 0.34 | 68.36 | 25.39
2019-10-01 | 10:03 | 31.1719 | 31.1719 | 0.04 | 1.04 | -0.76 | 0.24 | -0.65 | 0.35 | 67.38 | 26.37
2019-10-01 | 10:03 | 31.2695 | 31.2695 | 0.04 | 1.04 | -0.77 | 0.23 | -0.65 | 0.35 | 68.36 | 25.39
2019-10-01 | 10:03 | 31.3711 | 31.3711 | 0.04 | 1.04 | -0.78 | 0.22 | -0.66 | 0.34 | 67.38 | 25.39
2019-10-01 | 10:03 | 31.4727 | 31.4727 | 0.04 | 1.04 | -0.78 | 0.22 | -0.66 | 0.34 | 68.36 | 25.39
2019-10-01 | 10:03 | 31.6016 | 31.6016 | 0.05 | 1.05 | -0.78 | 0.22 | -0.66 | 0.34 | 69.34 | 26.37
2019-10-01 | 10:03 | 31.6914 | 31.6914 | 0.04 | 1.04 | -0.78 | 0.22 | -0.66 | 0.34 | 68.36 | 25.39
2019-10-01 | 10:03 | 31.7812 | 31.7812 | 0.04 | 1.04 | -0.77 | 0.23 | -0.67 | 0.33 | 69.34 | 26.37
2019-10-01 | 10:03 | 31.9023 | 31.9023 | 0.05 | 1.05 | -0.78 | 0.22 | -0.66 | 0.34 | 69.34 | 25.39
2019-10-01 | 10:03 | 32 | 32 | -0.03 | 0.97 | -0.69 | 0.31 | -0.65 | 0.35 | 70.31 | 25.39
2019-10-01 | 10:03 | 32.1094 | 32.1094 | -0.09 | 0.91 | -0.64 | 0.36 | -0.63 | 0.37 | 69.34 | 25.39
2019-10-01 | 10:03 | 32.1992 | 32.1992 | -0.12 | 0.88 | -0.6 | 0.4 | -0.63 | 0.37 | 68.36 | 25.39
2019-10-01 | 10:03 | 32.3008 | 32.3008 | -0.13 | 0.87 | -0.59 | 0.41 | -0.63 | 0.37 | 68.36 | 25.39
2019-10-01 | 10:03 | 32.4023 | 32.4023 | 0.03 | 1.03 | -0.75 | 0.25 | -0.62 | 0.38 | 69.34 | 26.37
2019-10-01 | 10:03 | 32.5 | 32.5 | 0.04 | 1.04 | -0.76 | 0.24 | -0.65 | 0.35 | 69.34 | 25.39
2019-10-01 | 10:03 | 32.6016 | 32.6016 | 0.04 | 1.04 | -0.76 | 0.24 | -0.64 | 0.36 | 68.36 | 25.39
2019-10-01 | 10:03 | 32.6992 | 32.6992 | 0.04 | 1.04 | -0.77 | 0.23 | -0.65 | 0.35 | 69.34 | 26.37
2019-10-01 | 10:03 | 32.8125 | 32.8125 | 0.05 | 1.05 | -0.78 | 0.22 | -0.65 | 0.35 | 69.34 | 26.37
2019-10-01 | 10:03 | 32.9102 | 32.9102 | 0.05 | 1.05 | -0.77 | 0.23 | -0.65 | 0.35 | 69.34 | 25.39
2019-10-01 | 10:03 | 33.0195 | 33.0195 | 0.05 | 1.05 | -0.77 | 0.23 | -0.65 | 0.35 | 69.34 | 26.37
2019-10-01 | 10:03 | 33.1211 | 33.1211 | 0.04 | 1.04 | -0.78 | 0.22 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 33.2227 | 33.2227 | 0.05 | 1.05 | -0.77 | 0.23 | -0.67 | 0.33 | 69.34 | 26.37
2019-10-01 | 10:03 | 33.3203 | 33.3203 | 0.05 | 1.05 | -0.78 | 0.22 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 33.4297 | 33.4297 | 0.06 | 1.06 | -0.78 | 0.22 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 33.5312 | 33.5312 | -0.07 | 0.93 | -0.67 | 0.33 | -0.64 | 0.36 | 70.31 | 25.39
2019-10-01 | 10:03 | 33.6523 | 33.6523 | -0.1 | 0.9 | -0.62 | 0.38 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 10:03 | 33.7617 | 33.7617 | -0.12 | 0.88 | -0.58 | 0.42 | -0.63 | 0.37 | 72.27 | 25.39
2019-10-01 | 10:03 | 33.8594 | 33.8594 | 0.01 | 1.01 | -0.79 | 0.21 | -0.62 | 0.38 | 71.29 | 27.34
2019-10-01 | 10:03 | 33.9609 | 33.9609 | 0.03 | 1.03 | -0.9 | 0.1 | -0.63 | 0.37 | 70.31 | 25.39
2019-10-01 | 10:03 | 34.0625 | 34.0625 | 0.04 | 1.04 | -0.89 | 0.11 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 34.1602 | 34.1602 | 0.04 | 1.04 | -0.86 | 0.14 | -0.64 | 0.36 | 71.29 | 27.34
2019-10-01 | 10:03 | 34.2695 | 34.2695 | 0.04 | 1.04 | -0.85 | 0.15 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 10:03 | 34.3516 | 34.3516 | 0.05 | 1.05 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:03 | 34.4609 | 34.4609 | 0.04 | 1.04 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:03 | 34.5625 | 34.5625 | 0.04 | 1.04 | -0.83 | 0.17 | -0.65 | 0.35 | 70.31 | 26.37
2019-10-01 | 10:03 | 34.6797 | 34.6797 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:03 | 34.793 | 34.793 | 0.05 | 1.05 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:03 | 34.8906 | 34.8906 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 34.9805 | 34.9805 | 0.01 | 1.01 | -0.78 | 0.22 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:03 | 35.0898 | 35.0898 | -0.1 | 0.9 | -0.66 | 0.34 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 35.1914 | 35.1914 | -0.12 | 0.88 | -0.65 | 0.35 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:03 | 35.293 | 35.293 | -0.11 | 0.89 | -0.64 | 0.36 | -0.63 | 0.37 | 71.29 | 25.39
2019-10-01 | 10:03 | 35.3906 | 35.3906 | 0.03 | 1.03 | -0.76 | 0.24 | -0.64 | 0.36 | 71.29 | 25.39
2019-10-01 | 10:03 | 35.4922 | 35.4922 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:03 | 35.582 | 35.582 | 0.04 | 1.04 | -0.78 | 0.22 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 35.6914 | 35.6914 | 0.04 | 1.04 | -0.77 | 0.23 | -0.65 | 0.35 | 71.29 | 25.39
2019-10-01 | 10:03 | 35.8008 | 35.8008 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:03 | 35.9219 | 35.9219 | 0.05 | 1.05 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 36.0195 | 36.0195 | 0.05 | 1.05 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 36.1094 | 36.1094 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 27.34
2019-10-01 | 10:03 | 36.1992 | 36.1992 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 36.3008 | 36.3008 | 0.05 | 1.05 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 36.4102 | 36.4102 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 36.5117 | 36.5117 | -0.05 | 0.95 | -0.8 | 0.2 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 36.6523 | 36.6523 | -0.1 | 0.9 | -0.75 | 0.25 | -0.65 | 0.35 | 75.2 | 26.37
2019-10-01 | 10:03 | 36.7305 | 36.7305 | -0.13 | 0.87 | -0.71 | 0.29 | -0.64 | 0.36 | 71.29 | 25.39
2019-10-01 | 10:03 | 36.8516 | 36.8516 | -0.12 | 0.88 | -0.68 | 0.32 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 10:03 | 36.9414 | 36.9414 | 0.04 | 1.04 | -0.82 | 0.18 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 10:03 | 37.0508 | 37.0508 | 0.04 | 1.04 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:03 | 37.1406 | 37.1406 | 0.04 | 1.04 | -0.82 | 0.18 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 37.25 | 37.25 | 0.04 | 1.04 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:03 | 37.3398 | 37.3398 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 37.4414 | 37.4414 | 0.06 | 1.06 | -0.83 | 0.17 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 37.5508 | 37.5508 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:03 | 37.6719 | 37.6719 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 37.7617 | 37.7617 | 0.05 | 1.05 | -0.83 | 0.17 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 37.8516 | 37.8516 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 37.9727 | 37.9727 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:03 | 38.082 | 38.082 | -0.05 | 0.95 | -0.71 | 0.29 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:03 | 38.1797 | 38.1797 | -0.11 | 0.89 | -0.67 | 0.33 | -0.65 | 0.35 | 71.29 | 25.39
2019-10-01 | 10:03 | 38.2812 | 38.2812 | -0.11 | 0.89 | -0.64 | 0.36 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:03 | 38.3711 | 38.3711 | 0.02 | 1.02 | -0.77 | 0.23 | -0.65 | 0.35 | 70.31 | 25.39
2019-10-01 | 10:03 | 38.4609 | 38.4609 | 0.04 | 1.04 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:03 | 38.5625 | 38.5625 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:03 | 38.6797 | 38.6797 | 0.04 | 1.04 | -0.8 | 0.2 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 38.7812 | 38.7812 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 38.8711 | 38.8711 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 38.9805 | 38.9805 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:03 | 39.082 | 39.082 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:03 | 39.1914 | 39.1914 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 39.2812 | 39.2812 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:03 | 39.3906 | 39.3906 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:03 | 39.5 | 39.5 | -0.02 | 0.98 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 39.6094 | 39.6094 | -0.1 | 0.9 | -0.67 | 0.33 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 39.6992 | 39.6992 | -0.12 | 0.88 | -0.64 | 0.36 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 39.8008 | 39.8008 | -0.12 | 0.88 | -0.62 | 0.38 | -0.63 | 0.37 | 71.29 | 23.44
2019-10-01 | 10:03 | 39.9023 | 39.9023 | 0.02 | 1.02 | -0.77 | 0.23 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 40 | 40 | 0.04 | 1.04 | -0.79 | 0.21 | -0.67 | 0.33 | 69.34 | 26.37
2019-10-01 | 10:03 | 40.1094 | 40.1094 | 0.04 | 1.04 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:03 | 40.2109 | 40.2109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 28.32
2019-10-01 | 10:03 | 40.332 | 40.332 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:03 | 40.4414 | 40.4414 | 0.04 | 1.04 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 40.5312 | 40.5312 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 40.6328 | 40.6328 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 40.7305 | 40.7305 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:03 | 40.8203 | 40.8203 | 0.05 | 1.05 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:03 | 40.9297 | 40.9297 | 0.06 | 1.06 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 27.34
2019-10-01 | 10:03 | 41.043 | 41.043 | -0.01 | 0.99 | -0.74 | 0.26 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:03 | 41.1328 | 41.1328 | -0.11 | 0.89 | -0.66 | 0.34 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 10:03 | 41.2422 | 41.2422 | -0.13 | 0.87 | -0.65 | 0.35 | -0.64 | 0.36 | 70.31 | 25.39
2019-10-01 | 10:03 | 41.3398 | 41.3398 | -0.02 | 0.98 | -0.71 | 0.29 | -0.64 | 0.36 | 71.29 | 26.37
2019-10-01 | 10:03 | 41.4609 | 41.4609 | 0.02 | 1.02 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 27.34
2019-10-01 | 10:03 | 41.5625 | 41.5625 | 0.03 | 1.03 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 26.37
2019-10-01 | 10:03 | 41.6523 | 41.6523 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 41.75 | 41.75 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 41.8516 | 41.8516 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 41.9609 | 41.9609 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 42.0625 | 42.0625 | 0.06 | 1.06 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:03 | 42.1602 | 42.1602 | 0.05 | 1.05 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 42.293 | 42.293 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 42.4023 | 42.4023 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 42.4922 | 42.4922 | 0.02 | 1.02 | -0.79 | 0.21 | -0.69 | 0.31 | 70.31 | 26.37
2019-10-01 | 10:03 | 42.5898 | 42.5898 | -0.08 | 0.92 | -0.68 | 0.32 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 42.6992 | 42.6992 | -0.12 | 0.88 | -0.66 | 0.34 | -0.66 | 0.34 | 70.31 | 26.37
2019-10-01 | 10:03 | 42.7812 | 42.7812 | -0.11 | 0.89 | -0.65 | 0.35 | -0.66 | 0.34 | 70.31 | 24.41
2019-10-01 | 10:03 | 42.8828 | 42.8828 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 71.29 | 24.41
2019-10-01 | 10:03 | 42.9805 | 42.9805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 24.41
2019-10-01 | 10:03 | 43.0898 | 43.0898 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 43.2109 | 43.2109 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 43.3203 | 43.3203 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 43.4219 | 43.4219 | 0.04 | 1.04 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 26.37
2019-10-01 | 10:03 | 43.5195 | 43.5195 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 43.6211 | 43.6211 | 0.04 | 1.04 | -0.8 | 0.2 | -0.7 | 0.3 | 70.31 | 25.39
2019-10-01 | 10:03 | 43.7305 | 43.7305 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 43.8203 | 43.8203 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 43.9219 | 43.9219 | 0.06 | 1.06 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 44.0117 | 44.0117 | -0.05 | 0.95 | -0.72 | 0.28 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:03 | 44.1211 | 44.1211 | -0.11 | 0.89 | -0.66 | 0.34 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 44.2227 | 44.2227 | -0.12 | 0.88 | -0.63 | 0.37 | -0.64 | 0.36 | 71.29 | 26.37
2019-10-01 | 10:03 | 44.332 | 44.332 | -0.13 | 0.87 | -0.63 | 0.37 | -0.62 | 0.38 | 71.29 | 24.41
2019-10-01 | 10:03 | 44.4219 | 44.4219 | 0.03 | 1.03 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:03 | 44.5312 | 44.5312 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 24.41
2019-10-01 | 10:03 | 44.6523 | 44.6523 | 0.04 | 1.04 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 44.75 | 44.75 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:03 | 44.8516 | 44.8516 | 0.04 | 1.04 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 44.9414 | 44.9414 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:03 | 45.0508 | 45.0508 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:03 | 45.1523 | 45.1523 | 0.05 | 1.05 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:03 | 45.2422 | 45.2422 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 45.3516 | 45.3516 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 72.27 | 24.41
2019-10-01 | 10:03 | 45.4492 | 45.4492 | 0.04 | 1.04 | -0.81 | 0.19 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:03 | 45.5508 | 45.5508 | -0.07 | 0.93 | -0.71 | 0.29 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:03 | 45.6523 | 45.6523 | -0.12 | 0.88 | -0.67 | 0.33 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 45.7617 | 45.7617 | -0.13 | 0.87 | -0.63 | 0.37 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 45.8594 | 45.8594 | 0.02 | 1.02 | -0.78 | 0.22 | -0.66 | 0.34 | 70.31 | 24.41
2019-10-01 | 10:03 | 45.9805 | 45.9805 | 0.04 | 1.04 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 46.082 | 46.082 | 0.04 | 1.04 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:03 | 46.1797 | 46.1797 | 0.04 | 1.04 | -0.81 | 0.19 | -0.66 | 0.34 | 70.31 | 26.37
2019-10-01 | 10:03 | 46.2812 | 46.2812 | 0.04 | 1.04 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 46.4023 | 46.4023 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:03 | 46.5 | 46.5 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 46.582 | 46.582 | 0.05 | 1.05 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:03 | 46.6797 | 46.6797 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:03 | 46.7812 | 46.7812 | 0.03 | 1.03 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:03 | 46.8906 | 46.8906 | 0.05 | 1.05 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 46.9922 | 46.9922 | -0.01 | 0.99 | -0.77 | 0.23 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:03 | 47.1016 | 47.1016 | -0.1 | 0.9 | -0.68 | 0.32 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 47.1992 | 47.1992 | -0.11 | 0.89 | -0.66 | 0.34 | -0.65 | 0.35 | 70.31 | 26.37
2019-10-01 | 10:03 | 47.3008 | 47.3008 | -0.13 | 0.87 | -0.66 | 0.34 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 10:03 | 47.4023 | 47.4023 | 0.04 | 1.04 | -0.8 | 0.2 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 47.5 | 47.5 | 0.03 | 1.03 | -0.81 | 0.19 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 47.6094 | 47.6094 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 47.7422 | 47.7422 | 0.04 | 1.04 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:03 | 47.8398 | 47.8398 | 0.04 | 1.04 | -0.81 | 0.19 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 47.9297 | 47.9297 | 0.04 | 1.04 | -0.81 | 0.19 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 48.0312 | 48.0312 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:03 | 48.1328 | 48.1328 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:03 | 48.25 | 48.25 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 48.3398 | 48.3398 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:03 | 48.4297 | 48.4297 | 0.04 | 1.04 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:03 | 48.543 | 48.543 | -0.04 | 0.96 | -0.74 | 0.26 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 48.6406 | 48.6406 | -0.11 | 0.89 | -0.67 | 0.33 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 48.7422 | 48.7422 | -0.13 | 0.87 | -0.68 | 0.32 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 48.8398 | 48.8398 | -0.04 | 0.96 | -0.75 | 0.25 | -0.64 | 0.36 | 71.29 | 25.39
2019-10-01 | 10:03 | 48.9414 | 48.9414 | 0.03 | 1.03 | -0.82 | 0.18 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:03 | 49.0703 | 49.0703 | 0.04 | 1.04 | -0.83 | 0.17 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 49.1602 | 49.1602 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 10:03 | 49.2617 | 49.2617 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:03 | 49.3711 | 49.3711 | 0.04 | 1.04 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:03 | 49.4609 | 49.4609 | 0.04 | 1.04 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:03 | 49.5625 | 49.5625 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 49.6602 | 49.6602 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:03 | 49.8203 | 49.8203 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 26.37
2019-10-01 | 10:03 | 49.9102 | 49.9102 | 0.06 | 1.06 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:03 | 50 | 50 | 0.01 | 1.01 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 50.0898 | 50.0898 | -0.1 | 0.9 | -0.7 | 0.3 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:03 | 50.2109 | 50.2109 | -0.13 | 0.87 | -0.7 | 0.3 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:03 | 50.2812 | 50.2812 | -0.14 | 0.86 | -0.7 | 0.3 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:03 | 50.3906 | 50.3906 | 0.03 | 1.03 | -0.81 | 0.19 | -0.66 | 0.34 | 71.29 | 24.41
2019-10-01 | 10:03 | 50.4922 | 50.4922 | 0.03 | 1.03 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:03 | 50.5898 | 50.5898 | 0.03 | 1.03 | -0.83 | 0.17 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 50.6914 | 50.6914 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 71.29 | 27.34
2019-10-01 | 10:03 | 50.793 | 50.793 | 0.04 | 1.04 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 50.9023 | 50.9023 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 51.0117 | 51.0117 | 0.04 | 1.04 | -0.82 | 0.18 | -0.7 | 0.3 | 71.29 | 26.37
2019-10-01 | 10:03 | 51.1211 | 51.1211 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 27.34
2019-10-01 | 10:03 | 51.2227 | 51.2227 | 0.05 | 1.05 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:03 | 51.3203 | 51.3203 | 0.05 | 1.05 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:03 | 51.4219 | 51.4219 | 0.04 | 1.04 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:03 | 51.5195 | 51.5195 | -0.04 | 0.96 | -0.76 | 0.24 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 51.6211 | 51.6211 | -0.11 | 0.89 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:03 | 51.7227 | 51.7227 | -0.14 | 0.86 | -0.75 | 0.25 | -0.65 | 0.35 | 71.29 | 25.39
2019-10-01 | 10:03 | 51.8203 | 51.8203 | -0.14 | 0.86 | -0.72 | 0.28 | -0.65 | 0.35 | 70.31 | 25.39
2019-10-01 | 10:03 | 51.9297 | 51.9297 | 0.02 | 1.02 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:03 | 52.0195 | 52.0195 | 0.04 | 1.04 | -0.86 | 0.14 | -0.66 | 0.34 | 71.29 | 27.34
2019-10-01 | 10:03 | 52.1328 | 52.1328 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 27.34
2019-10-01 | 10:03 | 52.2305 | 52.2305 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 10:03 | 52.3398 | 52.3398 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:03 | 52.4492 | 52.4492 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:03 | 52.543 | 52.543 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 52.6406 | 52.6406 | 0.05 | 1.05 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:03 | 52.75 | 52.75 | 0.04 | 1.04 | -0.84 | 0.16 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:03 | 52.8594 | 52.8594 | 0.05 | 1.05 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:03 | 52.9609 | 52.9609 | 0.04 | 1.04 | -0.83 | 0.17 | -0.7 | 0.3 | 70.31 | 25.39
2019-10-01 | 10:03 | 53.0625 | 53.0625 | -0.07 | 0.93 | -0.73 | 0.27 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:03 | 53.1602 | 53.1602 | -0.13 | 0.87 | -0.72 | 0.28 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:03 | 53.2617 | 53.2617 | -0.13 | 0.87 | -0.76 | 0.24 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 53.3711 | 53.3711 | 0.01 | 1.01 | -0.89 | 0.11 | -0.66 | 0.34 | 71.29 | 27.34
2019-10-01 | 10:03 | 53.4609 | 53.4609 | 0.03 | 1.03 | -0.89 | 0.11 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 53.5703 | 53.5703 | 0.04 | 1.04 | -0.87 | 0.13 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 53.7109 | 53.7109 | 0.03 | 1.03 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:03 | 53.8008 | 53.8008 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 53.9023 | 53.9023 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:03 | 54.0117 | 54.0117 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:03 | 54.082 | 54.082 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 54.2109 | 54.2109 | 0.04 | 1.04 | -0.84 | 0.16 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:03 | 54.3125 | 54.3125 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:03 | 54.4102 | 54.4102 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 54.5117 | 54.5117 | 0 | 1 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:03 | 54.6016 | 54.6016 | -0.1 | 0.9 | -0.76 | 0.24 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 10:03 | 54.7109 | 54.7109 | -0.11 | 0.89 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 54.8008 | 54.8008 | -0.13 | 0.87 | -0.75 | 0.25 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 54.9102 | 54.9102 | 0.01 | 1.01 | -0.88 | 0.12 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 55.0117 | 55.0117 | 0.04 | 1.04 | -0.87 | 0.13 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:03 | 55.1094 | 55.1094 | 0.03 | 1.03 | -0.85 | 0.15 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:03 | 55.2109 | 55.2109 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 55.332 | 55.332 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:03 | 55.4297 | 55.4297 | 0.04 | 1.04 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:03 | 55.5312 | 55.5312 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 55.6406 | 55.6406 | 0.04 | 1.04 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:03 | 55.7422 | 55.7422 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 24.41
2019-10-01 | 10:03 | 55.8398 | 55.8398 | 0.05 | 1.05 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:03 | 55.9297 | 55.9297 | 0.04 | 1.04 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 25.39
2019-10-01 | 10:03 | 56.043 | 56.043 | -0.03 | 0.97 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:03 | 56.1406 | 56.1406 | -0.12 | 0.88 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:03 | 56.2422 | 56.2422 | -0.13 | 0.87 | -0.75 | 0.25 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 56.3594 | 56.3594 | -0.08 | 0.92 | -0.84 | 0.16 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 56.4727 | 56.4727 | 0.02 | 1.02 | -0.89 | 0.11 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 56.5625 | 56.5625 | 0.03 | 1.03 | -0.89 | 0.11 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:03 | 56.6602 | 56.6602 | 0.04 | 1.04 | -0.87 | 0.13 | -0.66 | 0.34 | 71.29 | 24.41
2019-10-01 | 10:03 | 56.7617 | 56.7617 | 0.04 | 1.04 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 56.8516 | 56.8516 | 0.04 | 1.04 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 56.9609 | 56.9609 | 0.04 | 1.04 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 57.0625 | 57.0625 | 0.05 | 1.05 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:03 | 57.1602 | 57.1602 | 0.04 | 1.04 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 27.34
2019-10-01 | 10:03 | 57.2695 | 57.2695 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 23.44
2019-10-01 | 10:03 | 57.3711 | 57.3711 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 24.41
2019-10-01 | 10:03 | 57.4727 | 57.4727 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 57.5703 | 57.5703 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 57.6719 | 57.6719 | -0.13 | 0.87 | -0.78 | 0.22 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:03 | 57.7812 | 57.7812 | -0.13 | 0.87 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:03 | 57.8906 | 57.8906 | 0 | 1 | -0.91 | 0.09 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:03 | 57.9805 | 57.9805 | 0.03 | 1.03 | -0.9 | 0.1 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:03 | 58.082 | 58.082 | 0.03 | 1.03 | -0.88 | 0.12 | -0.66 | 0.34 | 70.31 | 27.34
2019-10-01 | 10:03 | 58.1914 | 58.1914 | 0.04 | 1.04 | -0.87 | 0.13 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 58.293 | 58.293 | 0.03 | 1.03 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 58.4023 | 58.4023 | 0.04 | 1.04 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 58.4922 | 58.4922 | 0.04 | 1.04 | -0.87 | 0.13 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 58.6211 | 58.6211 | 0.03 | 1.03 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 58.7227 | 58.7227 | 0.04 | 1.04 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 25.39
2019-10-01 | 10:04 | 58.8125 | 58.8125 | 0.05 | 1.05 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 58.9102 | 58.9102 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 59.0117 | 59.0117 | -0.03 | 0.97 | -0.8 | 0.2 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 59.1211 | 59.1211 | -0.12 | 0.88 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 59.2227 | 59.2227 | -0.14 | 0.86 | -0.79 | 0.21 | -0.65 | 0.35 | 71.29 | 25.39
2019-10-01 | 10:04 | 59.332 | 59.332 | -0.14 | 0.86 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 59.4297 | 59.4297 | 0.01 | 1.01 | -0.91 | 0.09 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 59.5312 | 59.5312 | 0.02 | 1.02 | -0.9 | 0.1 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 59.6328 | 59.6328 | 0.03 | 1.03 | -0.88 | 0.12 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 59.7305 | 59.7305 | 0.04 | 1.04 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 59.832 | 59.832 | 0.04 | 1.04 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 59.9414 | 59.9414 | 0.03 | 1.03 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 60.0508 | 60.0508 | 0.03 | 1.03 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 60.1523 | 60.1523 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 60.2422 | 60.2422 | 0.03 | 1.03 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 60.3516 | 60.3516 | 0.04 | 1.04 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 60.4492 | 60.4492 | 0.02 | 1.02 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 60.582 | 60.582 | -0.08 | 0.92 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 60.6914 | 60.6914 | -0.13 | 0.87 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 27.34
2019-10-01 | 10:04 | 60.793 | 60.793 | -0.14 | 0.86 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 60.8828 | 60.8828 | -0.02 | 0.98 | -0.93 | 0.07 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 60.9805 | 60.9805 | 0.02 | 1.02 | -0.91 | 0.09 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:04 | 61.082 | 61.082 | 0.01 | 1.01 | -0.88 | 0.12 | -0.67 | 0.33 | 70.31 | 23.44
2019-10-01 | 10:04 | 61.1719 | 61.1719 | 0.02 | 1.02 | -0.88 | 0.12 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 61.2812 | 61.2812 | 0.03 | 1.03 | -0.88 | 0.12 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:04 | 61.3828 | 61.3828 | 0.02 | 1.02 | -0.88 | 0.12 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 61.4805 | 61.4805 | 0.03 | 1.03 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 26.37
2019-10-01 | 10:04 | 61.582 | 61.582 | 0.03 | 1.03 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 61.6797 | 61.6797 | 0.02 | 1.02 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:04 | 61.793 | 61.793 | 0.02 | 1.02 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 61.9102 | 61.9102 | 0.03 | 1.03 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 62 | 62 | -0.01 | 0.99 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 62.0898 | 62.0898 | -0.13 | 0.87 | -0.8 | 0.2 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 62.1992 | 62.1992 | -0.15 | 0.85 | -0.8 | 0.2 | -0.66 | 0.34 | 70.31 | 26.37
2019-10-01 | 10:04 | 62.3125 | 62.3125 | -0.16 | 0.84 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:04 | 62.4102 | 62.4102 | -0.01 | 0.99 | -0.91 | 0.09 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:04 | 62.5117 | 62.5117 | 0.01 | 1.01 | -0.9 | 0.1 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 62.6094 | 62.6094 | 0.02 | 1.02 | -0.89 | 0.11 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 62.7109 | 62.7109 | 0 | 1 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 62.8125 | 62.8125 | 0.01 | 1.01 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:04 | 62.9219 | 62.9219 | 0.02 | 1.02 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 63.0195 | 63.0195 | 0.01 | 1.01 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 63.1211 | 63.1211 | 0.01 | 1.01 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 63.2227 | 63.2227 | 0.02 | 1.02 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 63.332 | 63.332 | 0 | 1 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 63.4297 | 63.4297 | 0.02 | 1.02 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:04 | 63.543 | 63.543 | -0.1 | 0.9 | -0.83 | 0.17 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 63.6406 | 63.6406 | -0.16 | 0.84 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 63.7422 | 63.7422 | -0.18 | 0.82 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 63.8398 | 63.8398 | -0.17 | 0.83 | -0.82 | 0.18 | -0.65 | 0.35 | 70.31 | 25.39
2019-10-01 | 10:04 | 63.9492 | 63.9492 | -0.01 | 0.99 | -0.92 | 0.08 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 64.043 | 64.043 | -0.02 | 0.98 | -0.9 | 0.1 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 64.1719 | 64.1719 | -0.04 | 0.96 | -0.89 | 0.11 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:04 | 64.2695 | 64.2695 | -0.01 | 0.99 | -0.89 | 0.11 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 64.3594 | 64.3594 | -0.01 | 0.99 | -0.89 | 0.11 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:04 | 64.4609 | 64.4609 | -0.01 | 0.99 | -0.88 | 0.12 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 64.5703 | 64.5703 | -0.01 | 0.99 | -0.87 | 0.13 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 10:04 | 64.6602 | 64.6602 | -0.01 | 0.99 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 64.7695 | 64.7695 | -0.01 | 0.99 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:04 | 64.8711 | 64.8711 | -0.01 | 0.99 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 64.9727 | 64.9727 | -0.02 | 0.98 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:04 | 65.082 | 65.082 | -0.15 | 0.85 | -0.82 | 0.18 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 65.1797 | 65.1797 | -0.17 | 0.83 | -0.84 | 0.16 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 65.2812 | 65.2812 | -0.19 | 0.81 | -0.82 | 0.18 | -0.68 | 0.32 | 71.29 | 23.44
2019-10-01 | 10:04 | 65.4023 | 65.4023 | -0.04 | 0.96 | -0.91 | 0.09 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 65.4922 | 65.4922 | -0.01 | 0.99 | -0.91 | 0.09 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 10:04 | 65.5898 | 65.5898 | -0.02 | 0.98 | -0.9 | 0.1 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 65.6992 | 65.6992 | -0.03 | 0.97 | -0.9 | 0.1 | -0.69 | 0.31 | 70.31 | 24.41
2019-10-01 | 10:04 | 65.8008 | 65.8008 | -0.03 | 0.97 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 65.9023 | 65.9023 | -0.04 | 0.96 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:04 | 66 | 66 | -0.04 | 0.96 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 66.1016 | 66.1016 | -0.03 | 0.97 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 66.2109 | 66.2109 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 24.41
2019-10-01 | 10:04 | 66.3125 | 66.3125 | -0.03 | 0.97 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 24.41
2019-10-01 | 10:04 | 66.4219 | 66.4219 | -0.04 | 0.96 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:04 | 66.5195 | 66.5195 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 66.6211 | 66.6211 | -0.16 | 0.84 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 66.7227 | 66.7227 | -0.21 | 0.79 | -0.82 | 0.18 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:04 | 66.8203 | 66.8203 | -0.21 | 0.79 | -0.82 | 0.18 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 66.9297 | 66.9297 | -0.05 | 0.95 | -0.94 | 0.06 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:04 | 67.0312 | 67.0312 | -0.06 | 0.94 | -0.91 | 0.09 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 67.1328 | 67.1328 | -0.04 | 0.96 | -0.89 | 0.11 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 67.2305 | 67.2305 | -0.04 | 0.96 | -0.88 | 0.12 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 67.3398 | 67.3398 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:04 | 67.4609 | 67.4609 | -0.03 | 0.97 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 67.5625 | 67.5625 | -0.04 | 0.96 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 24.41
2019-10-01 | 10:04 | 67.6523 | 67.6523 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 67.75 | 67.75 | -0.01 | 0.99 | -0.88 | 0.12 | -0.7 | 0.3 | 71.29 | 25.39
2019-10-01 | 10:04 | 67.8516 | 67.8516 | -0.01 | 0.99 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:04 | 67.9492 | 67.9492 | 0 | 1 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:04 | 68.0625 | 68.0625 | -0.11 | 0.89 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 68.1602 | 68.1602 | -0.19 | 0.81 | -0.83 | 0.17 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 68.2617 | 68.2617 | -0.19 | 0.81 | -0.81 | 0.19 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 68.3711 | 68.3711 | -0.08 | 0.92 | -0.92 | 0.08 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 68.4727 | 68.4727 | -0.04 | 0.96 | -0.92 | 0.08 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 68.5703 | 68.5703 | -0.02 | 0.98 | -0.9 | 0.1 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:04 | 68.6719 | 68.6719 | -0.03 | 0.97 | -0.9 | 0.1 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 68.7812 | 68.7812 | -0.03 | 0.97 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 68.8906 | 68.8906 | -0.02 | 0.98 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 68.9805 | 68.9805 | -0.01 | 0.99 | -0.89 | 0.11 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 69.1211 | 69.1211 | -0.01 | 0.99 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 69.2227 | 69.2227 | -0.01 | 0.99 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 26.37
2019-10-01 | 10:04 | 69.3125 | 69.3125 | -0.03 | 0.97 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 69.4102 | 69.4102 | -0.03 | 0.97 | -0.88 | 0.12 | -0.69 | 0.31 | 70.31 | 24.41
2019-10-01 | 10:04 | 69.5117 | 69.5117 | -0.01 | 0.99 | -0.86 | 0.14 | -0.7 | 0.3 | 71.29 | 26.37
2019-10-01 | 10:04 | 69.6211 | 69.6211 | -0.14 | 0.86 | -0.84 | 0.16 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 69.7227 | 69.7227 | -0.19 | 0.81 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 69.8125 | 69.8125 | -0.19 | 0.81 | -0.82 | 0.18 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:04 | 69.9414 | 69.9414 | -0.04 | 0.96 | -0.92 | 0.08 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 70.0117 | 70.0117 | -0.03 | 0.97 | -0.91 | 0.09 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 70.1094 | 70.1094 | -0.03 | 0.97 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 70.2227 | 70.2227 | -0.01 | 0.99 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 70.3203 | 70.3203 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 70.4219 | 70.4219 | -0.01 | 0.99 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 70.5195 | 70.5195 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 70.6406 | 70.6406 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 24.41
2019-10-01 | 10:04 | 70.7422 | 70.7422 | -0.01 | 0.99 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 26.37
2019-10-01 | 10:04 | 70.8398 | 70.8398 | -0.02 | 0.98 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 70.9492 | 70.9492 | -0.01 | 0.99 | -0.88 | 0.12 | -0.7 | 0.3 | 70.31 | 25.39
2019-10-01 | 10:04 | 71.043 | 71.043 | -0.11 | 0.89 | -0.8 | 0.2 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 71.1406 | 71.1406 | -0.18 | 0.82 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 71.2422 | 71.2422 | -0.19 | 0.81 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 71.3516 | 71.3516 | -0.19 | 0.81 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 71.4492 | 71.4492 | -0.04 | 0.96 | -0.9 | 0.1 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:04 | 71.5508 | 71.5508 | -0.03 | 0.97 | -0.88 | 0.12 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 71.6523 | 71.6523 | -0.02 | 0.98 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 71.7617 | 71.7617 | -0.03 | 0.97 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 71.8828 | 71.8828 | -0.03 | 0.97 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:04 | 71.9727 | 71.9727 | -0.01 | 0.99 | -0.87 | 0.13 | -0.7 | 0.3 | 71.29 | 25.39
2019-10-01 | 10:04 | 72.082 | 72.082 | -0.03 | 0.97 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 72.1719 | 72.1719 | -0.04 | 0.96 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 25.39
2019-10-01 | 10:04 | 72.2695 | 72.2695 | -0.03 | 0.97 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 72.3828 | 72.3828 | -0.04 | 0.96 | -0.85 | 0.15 | -0.7 | 0.3 | 72.27 | 23.44
2019-10-01 | 10:04 | 72.4805 | 72.4805 | -0.04 | 0.96 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 72.582 | 72.582 | -0.16 | 0.84 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 72.6992 | 72.6992 | -0.21 | 0.79 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 26.37
2019-10-01 | 10:04 | 72.8125 | 72.8125 | -0.21 | 0.79 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 26.37
2019-10-01 | 10:04 | 72.8906 | 72.8906 | -0.07 | 0.93 | -0.91 | 0.09 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 72.9922 | 72.9922 | -0.04 | 0.96 | -0.89 | 0.11 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 73.1016 | 73.1016 | -0.04 | 0.96 | -0.88 | 0.12 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 73.2109 | 73.2109 | -0.04 | 0.96 | -0.87 | 0.13 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 73.3008 | 73.3008 | -0.05 | 0.95 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 73.4023 | 73.4023 | -0.04 | 0.96 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 73.5195 | 73.5195 | -0.05 | 0.95 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 73.6406 | 73.6406 | -0.04 | 0.96 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 73.7227 | 73.7227 | -0.05 | 0.95 | -0.87 | 0.13 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 73.8125 | 73.8125 | -0.04 | 0.96 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 73.9102 | 73.9102 | -0.05 | 0.95 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 74.0195 | 74.0195 | -0.12 | 0.88 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 74.1211 | 74.1211 | -0.2 | 0.8 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 74.2227 | 74.2227 | -0.22 | 0.78 | -0.8 | 0.2 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 74.3203 | 74.3203 | -0.23 | 0.77 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:04 | 74.4297 | 74.4297 | -0.06 | 0.94 | -0.91 | 0.09 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 74.543 | 74.543 | -0.05 | 0.95 | -0.88 | 0.12 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 74.6406 | 74.6406 | -0.05 | 0.95 | -0.88 | 0.12 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:04 | 74.7422 | 74.7422 | -0.04 | 0.96 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 74.8398 | 74.8398 | -0.05 | 0.95 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 74.9492 | 74.9492 | -0.1 | 0.9 | -0.86 | 0.14 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:04 | 75.043 | 75.043 | -0.16 | 0.84 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 75.1523 | 75.1523 | -0.16 | 0.84 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 75.25 | 75.25 | -0.17 | 0.83 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 75.3516 | 75.3516 | -0.16 | 0.84 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 75.4492 | 75.4492 | -0.17 | 0.83 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 75.5898 | 75.5898 | -0.28 | 0.72 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 75.6719 | 75.6719 | -0.32 | 0.68 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 75.7695 | 75.7695 | -0.31 | 0.69 | -0.79 | 0.21 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 75.8711 | 75.8711 | -0.21 | 0.79 | -0.85 | 0.15 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 75.9727 | 75.9727 | -0.14 | 0.86 | -0.91 | 0.09 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 76.0703 | 76.0703 | -0.16 | 0.84 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 27.34
2019-10-01 | 10:04 | 76.1719 | 76.1719 | -0.17 | 0.83 | -0.89 | 0.11 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 76.2812 | 76.2812 | -0.18 | 0.82 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 76.3828 | 76.3828 | -0.16 | 0.84 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 76.4805 | 76.4805 | -0.16 | 0.84 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 76.582 | 76.582 | -0.16 | 0.84 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 76.6914 | 76.6914 | -0.16 | 0.84 | -0.85 | 0.15 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 76.8008 | 76.8008 | -0.16 | 0.84 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 76.9023 | 76.9023 | -0.15 | 0.85 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 77 | 77 | -0.18 | 0.82 | -0.83 | 0.17 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 77.1016 | 77.1016 | -0.28 | 0.72 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 77.2227 | 77.2227 | -0.31 | 0.69 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 77.3203 | 77.3203 | -0.3 | 0.7 | -0.8 | 0.2 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 77.4102 | 77.4102 | -0.16 | 0.84 | -0.91 | 0.09 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:04 | 77.5195 | 77.5195 | -0.16 | 0.84 | -0.89 | 0.11 | -0.67 | 0.33 | 70.31 | 26.37
2019-10-01 | 10:04 | 77.6211 | 77.6211 | -0.15 | 0.85 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 77.7227 | 77.7227 | -0.15 | 0.85 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 77.8398 | 77.8398 | -0.15 | 0.85 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:04 | 77.9492 | 77.9492 | -0.17 | 0.83 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 78.0312 | 78.0312 | -0.17 | 0.83 | -0.86 | 0.14 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 78.1328 | 78.1328 | -0.14 | 0.86 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 78.2305 | 78.2305 | -0.16 | 0.84 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 78.332 | 78.332 | -0.15 | 0.85 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 78.4414 | 78.4414 | -0.13 | 0.87 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 78.543 | 78.543 | -0.23 | 0.77 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 78.6406 | 78.6406 | -0.3 | 0.7 | -0.79 | 0.21 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 78.7422 | 78.7422 | -0.31 | 0.69 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 10:04 | 78.8398 | 78.8398 | -0.3 | 0.7 | -0.79 | 0.21 | -0.67 | 0.33 | 75.2 | 26.37
2019-10-01 | 10:04 | 78.9727 | 78.9727 | -0.14 | 0.86 | -0.9 | 0.1 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 79.082 | 79.082 | -0.11 | 0.89 | -0.88 | 0.12 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 79.1797 | 79.1797 | -0.12 | 0.88 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 79.2695 | 79.2695 | -0.1 | 0.9 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 79.3828 | 79.3828 | -0.11 | 0.89 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 79.4609 | 79.4609 | -0.11 | 0.89 | -0.87 | 0.13 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 79.5703 | 79.5703 | -0.12 | 0.88 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 79.6719 | 79.6719 | -0.11 | 0.89 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 79.7695 | 79.7695 | -0.11 | 0.89 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 79.8828 | 79.8828 | -0.1 | 0.9 | -0.84 | 0.16 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 79.9805 | 79.9805 | -0.11 | 0.89 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 80.1016 | 80.1016 | -0.22 | 0.78 | -0.79 | 0.21 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:04 | 80.2109 | 80.2109 | -0.27 | 0.73 | -0.82 | 0.18 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:04 | 80.3125 | 80.3125 | -0.28 | 0.72 | -0.79 | 0.21 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:04 | 80.4023 | 80.4023 | -0.15 | 0.85 | -0.89 | 0.11 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 80.5117 | 80.5117 | -0.12 | 0.88 | -0.9 | 0.1 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 80.6016 | 80.6016 | -0.11 | 0.89 | -0.88 | 0.12 | -0.69 | 0.31 | 73.24 | 27.34
2019-10-01 | 10:04 | 80.6992 | 80.6992 | -0.11 | 0.89 | -0.88 | 0.12 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 80.8125 | 80.8125 | -0.1 | 0.9 | -0.87 | 0.13 | -0.7 | 0.3 | 70.31 | 24.41
2019-10-01 | 10:04 | 80.9023 | 80.9023 | -0.1 | 0.9 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 81 | 81 | -0.1 | 0.9 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:04 | 81.1094 | 81.1094 | -0.09 | 0.91 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:04 | 81.1992 | 81.1992 | -0.09 | 0.91 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 81.3125 | 81.3125 | -0.09 | 0.91 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 81.4102 | 81.4102 | -0.11 | 0.89 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 26.37
2019-10-01 | 10:04 | 81.5195 | 81.5195 | -0.13 | 0.87 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:04 | 81.6211 | 81.6211 | -0.25 | 0.75 | -0.79 | 0.21 | -0.66 | 0.34 | 70.31 | 24.41
2019-10-01 | 10:04 | 81.7305 | 81.7305 | -0.28 | 0.72 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 10:04 | 81.832 | 81.832 | -0.29 | 0.71 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 28.32
2019-10-01 | 10:04 | 81.9414 | 81.9414 | -0.13 | 0.87 | -0.88 | 0.12 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:04 | 82.043 | 82.043 | -0.11 | 0.89 | -0.89 | 0.11 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 82.1523 | 82.1523 | -0.11 | 0.89 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 82.2617 | 82.2617 | -0.09 | 0.91 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:04 | 82.3398 | 82.3398 | -0.09 | 0.91 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 82.4414 | 82.4414 | -0.09 | 0.91 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 82.5508 | 82.5508 | -0.1 | 0.9 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 82.6523 | 82.6523 | -0.09 | 0.91 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 82.75 | 82.75 | -0.1 | 0.9 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 10:04 | 82.8594 | 82.8594 | -0.09 | 0.91 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 82.9609 | 82.9609 | -0.09 | 0.91 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 24.41
2019-10-01 | 10:04 | 83.0625 | 83.0625 | -0.2 | 0.8 | -0.79 | 0.21 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 83.1797 | 83.1797 | -0.27 | 0.73 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 83.3008 | 83.3008 | -0.27 | 0.73 | -0.8 | 0.2 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 83.3906 | 83.3906 | -0.19 | 0.81 | -0.85 | 0.15 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:04 | 83.4922 | 83.4922 | -0.12 | 0.88 | -0.9 | 0.1 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 83.5898 | 83.5898 | -0.13 | 0.87 | -0.88 | 0.12 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 83.6719 | 83.6719 | -0.11 | 0.89 | -0.87 | 0.13 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 83.7812 | 83.7812 | -0.09 | 0.91 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 83.8828 | 83.8828 | -0.1 | 0.9 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:04 | 83.9922 | 83.9922 | -0.09 | 0.91 | -0.87 | 0.13 | -0.68 | 0.32 | 70.31 | 24.41
2019-10-01 | 10:04 | 84.0898 | 84.0898 | -0.09 | 0.91 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 84.1914 | 84.1914 | -0.08 | 0.92 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 84.3125 | 84.3125 | -0.1 | 0.9 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 84.4219 | 84.4219 | -0.1 | 0.9 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 84.5195 | 84.5195 | -0.11 | 0.89 | -0.85 | 0.15 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 84.6211 | 84.6211 | -0.25 | 0.75 | -0.79 | 0.21 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 84.7305 | 84.7305 | -0.27 | 0.73 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 84.8516 | 84.8516 | -0.24 | 0.76 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 84.9492 | 84.9492 | -0.14 | 0.86 | -0.91 | 0.09 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:04 | 85.0508 | 85.0508 | -0.1 | 0.9 | -0.88 | 0.12 | -0.67 | 0.33 | 70.31 | 24.41
2019-10-01 | 10:04 | 85.1406 | 85.1406 | -0.1 | 0.9 | -0.87 | 0.13 | -0.66 | 0.34 | 70.31 | 25.39
2019-10-01 | 10:04 | 85.25 | 85.25 | -0.11 | 0.89 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 24.41
2019-10-01 | 10:04 | 85.3398 | 85.3398 | -0.1 | 0.9 | -0.86 | 0.14 | -0.68 | 0.32 | 70.31 | 25.39
2019-10-01 | 10:04 | 85.4492 | 85.4492 | -0.08 | 0.92 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 85.5508 | 85.5508 | -0.09 | 0.91 | -0.86 | 0.14 | -0.69 | 0.31 | 70.31 | 26.37
2019-10-01 | 10:04 | 85.6406 | 85.6406 | -0.09 | 0.91 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 85.7305 | 85.7305 | -0.08 | 0.92 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 85.8398 | 85.8398 | -0.09 | 0.91 | -0.86 | 0.14 | -0.67 | 0.33 | 70.31 | 25.39
2019-10-01 | 10:04 | 85.9492 | 85.9492 | -0.08 | 0.92 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 27.34
2019-10-01 | 10:04 | 86.043 | 86.043 | -0.16 | 0.84 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 86.1406 | 86.1406 | -0.24 | 0.76 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 86.25 | 86.25 | -0.26 | 0.74 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 86.3516 | 86.3516 | -0.27 | 0.73 | -0.79 | 0.21 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:04 | 86.4609 | 86.4609 | -0.12 | 0.88 | -0.89 | 0.11 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 86.5508 | 86.5508 | -0.1 | 0.9 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 86.6602 | 86.6602 | -0.08 | 0.92 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 27.34
2019-10-01 | 10:04 | 86.7812 | 86.7812 | -0.09 | 0.91 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 86.8828 | 86.8828 | -0.08 | 0.92 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 24.41
2019-10-01 | 10:04 | 86.9727 | 86.9727 | -0.08 | 0.92 | -0.86 | 0.14 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 87.082 | 87.082 | -0.07 | 0.93 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 87.1797 | 87.1797 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 87.2812 | 87.2812 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:04 | 87.3828 | 87.3828 | -0.06 | 0.94 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 27.34
2019-10-01 | 10:04 | 87.4805 | 87.4805 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 87.5898 | 87.5898 | -0.14 | 0.86 | -0.82 | 0.18 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 87.6797 | 87.6797 | -0.24 | 0.76 | -0.8 | 0.2 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 87.8008 | 87.8008 | -0.24 | 0.76 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:04 | 87.9102 | 87.9102 | -0.11 | 0.89 | -0.89 | 0.11 | -0.64 | 0.36 | 71.29 | 25.39
2019-10-01 | 10:04 | 88.0117 | 88.0117 | -0.08 | 0.92 | -0.88 | 0.12 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:04 | 88.1211 | 88.1211 | -0.06 | 0.94 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 88.2227 | 88.2227 | -0.06 | 0.94 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 88.3008 | 88.3008 | -0.06 | 0.94 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 88.4023 | 88.4023 | -0.06 | 0.94 | -0.85 | 0.15 | -0.69 | 0.31 | 70.31 | 25.39
2019-10-01 | 10:04 | 88.5 | 88.5 | -0.05 | 0.95 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 88.6094 | 88.6094 | -0.05 | 0.95 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 88.7109 | 88.7109 | -0.07 | 0.93 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 88.8398 | 88.8398 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 88.9414 | 88.9414 | -0.07 | 0.93 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 89.043 | 89.043 | -0.11 | 0.89 | -0.82 | 0.18 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 89.1328 | 89.1328 | -0.23 | 0.77 | -0.81 | 0.19 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 89.25 | 89.25 | -0.26 | 0.74 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:04 | 89.3398 | 89.3398 | -0.26 | 0.74 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:04 | 89.4297 | 89.4297 | -0.1 | 0.9 | -0.89 | 0.11 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 89.5312 | 89.5312 | -0.11 | 0.89 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 89.6406 | 89.6406 | -0.1 | 0.9 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 89.7695 | 89.7695 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 89.8711 | 89.8711 | -0.08 | 0.92 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 89.9727 | 89.9727 | -0.09 | 0.91 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 90.0703 | 90.0703 | -0.09 | 0.91 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 90.1523 | 90.1523 | -0.08 | 0.92 | -0.85 | 0.15 | -0.7 | 0.3 | 71.29 | 25.39
2019-10-01 | 10:04 | 90.2617 | 90.2617 | -0.07 | 0.93 | -0.84 | 0.16 | -0.7 | 0.3 | 72.27 | 25.39
2019-10-01 | 10:04 | 90.3516 | 90.3516 | -0.08 | 0.92 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 90.4609 | 90.4609 | -0.07 | 0.93 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 90.5703 | 90.5703 | -0.18 | 0.82 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 90.6719 | 90.6719 | -0.24 | 0.76 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 90.793 | 90.793 | -0.26 | 0.74 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 10:04 | 90.8906 | 90.8906 | -0.19 | 0.81 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:04 | 90.9805 | 90.9805 | -0.08 | 0.92 | -0.88 | 0.12 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 91.0703 | 91.0703 | -0.08 | 0.92 | -0.88 | 0.12 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 91.1797 | 91.1797 | -0.08 | 0.92 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 91.2812 | 91.2812 | -0.07 | 0.93 | -0.86 | 0.14 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 91.3906 | 91.3906 | -0.05 | 0.95 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 91.4922 | 91.4922 | -0.06 | 0.94 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 91.5898 | 91.5898 | -0.07 | 0.93 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 91.7227 | 91.7227 | -0.06 | 0.94 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 10:04 | 91.832 | 91.832 | -0.06 | 0.94 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 91.9102 | 91.9102 | -0.07 | 0.93 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 92 | 92 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 92.1016 | 92.1016 | -0.2 | 0.8 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 92.1992 | 92.1992 | -0.23 | 0.77 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 92.3125 | 92.3125 | -0.23 | 0.77 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 92.4102 | 92.4102 | -0.09 | 0.91 | -0.89 | 0.11 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 92.5195 | 92.5195 | -0.07 | 0.93 | -0.9 | 0.1 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 92.6328 | 92.6328 | -0.08 | 0.92 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 92.7305 | 92.7305 | -0.05 | 0.95 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 92.8203 | 92.8203 | -0.05 | 0.95 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 24.41
2019-10-01 | 10:04 | 92.9219 | 92.9219 | -0.05 | 0.95 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 24.41
2019-10-01 | 10:04 | 93.0508 | 93.0508 | -0.06 | 0.94 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 93.1406 | 93.1406 | -0.05 | 0.95 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 93.2305 | 93.2305 | -0.06 | 0.94 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 27.34
2019-10-01 | 10:04 | 93.3398 | 93.3398 | -0.05 | 0.95 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 93.4414 | 93.4414 | -0.05 | 0.95 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 10:04 | 93.5508 | 93.5508 | -0.13 | 0.87 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 93.6523 | 93.6523 | -0.22 | 0.78 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 93.75 | 93.75 | -0.23 | 0.77 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:04 | 93.8516 | 93.8516 | -0.24 | 0.76 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 93.9492 | 93.9492 | -0.08 | 0.92 | -0.89 | 0.11 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 94.0625 | 94.0625 | -0.06 | 0.94 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 94.1602 | 94.1602 | -0.07 | 0.93 | -0.88 | 0.12 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 94.2812 | 94.2812 | -0.06 | 0.94 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 94.3711 | 94.3711 | -0.06 | 0.94 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 10:04 | 94.4805 | 94.4805 | -0.06 | 0.94 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 94.582 | 94.582 | -0.04 | 0.96 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 94.6914 | 94.6914 | -0.05 | 0.95 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 94.793 | 94.793 | -0.04 | 0.96 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 94.8828 | 94.8828 | -0.05 | 0.95 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 94.9727 | 94.9727 | -0.06 | 0.94 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 95.082 | 95.082 | -0.17 | 0.83 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 10:04 | 95.1914 | 95.1914 | -0.22 | 0.78 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 95.2812 | 95.2812 | -0.22 | 0.78 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 24.41
2019-10-01 | 10:04 | 95.4102 | 95.4102 | -0.1 | 0.9 | -0.88 | 0.12 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 95.5312 | 95.5312 | -0.07 | 0.93 | -0.88 | 0.12 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 95.6094 | 95.6094 | -0.05 | 0.95 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 10:04 | 95.6992 | 95.6992 | -0.06 | 0.94 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 95.8008 | 95.8008 | -0.06 | 0.94 | -0.86 | 0.14 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 95.9102 | 95.9102 | -0.05 | 0.95 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 96.0117 | 96.0117 | -0.05 | 0.95 | -0.86 | 0.14 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 96.1094 | 96.1094 | -0.05 | 0.95 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 96.2227 | 96.2227 | -0.04 | 0.96 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:04 | 96.3125 | 96.3125 | -0.04 | 0.96 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 96.4219 | 96.4219 | -0.04 | 0.96 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 96.5195 | 96.5195 | -0.08 | 0.92 | -0.81 | 0.19 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 96.6211 | 96.6211 | -0.2 | 0.8 | -0.79 | 0.21 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 96.7227 | 96.7227 | -0.22 | 0.78 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 96.832 | 96.832 | -0.23 | 0.77 | -0.77 | 0.23 | -0.65 | 0.35 | 71.29 | 26.37
2019-10-01 | 10:04 | 96.9297 | 96.9297 | -0.08 | 0.92 | -0.88 | 0.12 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 10:04 | 97.043 | 97.043 | -0.06 | 0.94 | -0.87 | 0.13 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 97.1719 | 97.1719 | -0.04 | 0.96 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 97.2617 | 97.2617 | -0.06 | 0.94 | -0.86 | 0.14 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:04 | 97.3516 | 97.3516 | -0.06 | 0.94 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 97.4492 | 97.4492 | -0.05 | 0.95 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 97.5508 | 97.5508 | -0.04 | 0.96 | -0.87 | 0.13 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 97.6523 | 97.6523 | -0.05 | 0.95 | -0.84 | 0.16 | -0.66 | 0.34 | 71.29 | 26.37
2019-10-01 | 10:04 | 97.7695 | 97.7695 | -0.04 | 0.96 | -0.84 | 0.16 | -0.68 | 0.32 | 71.29 | 27.34
2019-10-01 | 10:04 | 97.8711 | 97.8711 | -0.06 | 0.94 | -0.85 | 0.15 | -0.69 | 0.31 | 71.29 | 27.34
2019-10-01 | 10:04 | 97.9727 | 97.9727 | -0.05 | 0.95 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 10:04 | 98.0703 | 98.0703 | -0.16 | 0.84 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 98.1719 | 98.1719 | -0.21 | 0.79 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 98.2695 | 98.2695 | -0.25 | 0.75 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 98.3828 | 98.3828 | -0.26 | 0.74 | -0.79 | 0.21 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:04 | 98.5 | 98.5 | -0.1 | 0.9 | -0.88 | 0.12 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 98.5898 | 98.5898 | -0.08 | 0.92 | -0.87 | 0.13 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 98.6914 | 98.6914 | -0.08 | 0.92 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 98.8008 | 98.8008 | -0.08 | 0.92 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 98.9023 | 98.9023 | -0.07 | 0.93 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 99 | 99 | -0.07 | 0.93 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 24.41
2019-10-01 | 10:04 | 99.1016 | 99.1016 | -0.07 | 0.93 | -0.85 | 0.15 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:04 | 99.1992 | 99.1992 | -0.08 | 0.92 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:04 | 99.3203 | 99.3203 | -0.07 | 0.93 | -0.86 | 0.14 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 99.4219 | 99.4219 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:04 | 99.5195 | 99.5195 | -0.1 | 0.9 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 99.6211 | 99.6211 | -0.22 | 0.78 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 99.7227 | 99.7227 | -0.25 | 0.75 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 99.8203 | 99.8203 | -0.27 | 0.73 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 99.9297 | 99.9297 | -0.13 | 0.87 | -0.88 | 0.12 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:04 | 100.0313 | 100.0313 | -0.12 | 0.88 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:04 | 100.1328 | 100.1328 | -0.09 | 0.91 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:04 | 100.2305 | 100.2305 | -0.1 | 0.9 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 100.3203 | 100.3203 | -0.09 | 0.91 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:04 | 100.4297 | 100.4297 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 100.5313 | 100.5313 | -0.08 | 0.92 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 10:04 | 100.6406 | 100.6406 | -0.08 | 0.92 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:04 | 100.7305 | 100.7305 | -0.07 | 0.93 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 100.8398 | 100.8398 | -0.08 | 0.92 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 100.9414 | 100.9414 | -0.1 | 0.9 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 25.39
2019-10-01 | 10:04 | 101.043 | 101.043 | -0.18 | 0.82 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 101.1406 | 101.1406 | -0.25 | 0.75 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 101.25 | 101.25 | -0.27 | 0.73 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 101.3398 | 101.3398 | -0.28 | 0.72 | -0.77 | 0.23 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:04 | 101.4492 | 101.4492 | -0.12 | 0.88 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 101.5625 | 101.5625 | -0.11 | 0.89 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 101.6602 | 101.6602 | -0.11 | 0.89 | -0.86 | 0.14 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 101.7617 | 101.7617 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 101.8711 | 101.8711 | -0.09 | 0.91 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 101.9922 | 101.9922 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 102.0898 | 102.0898 | -0.08 | 0.92 | -0.86 | 0.14 | -0.69 | 0.31 | 73.24 | 26.37
2019-10-01 | 10:04 | 102.1797 | 102.1797 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:04 | 102.293 | 102.293 | -0.09 | 0.91 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 102.3828 | 102.3828 | -0.09 | 0.91 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 102.4922 | 102.4922 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 102.6211 | 102.6211 | -0.21 | 0.79 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 102.6992 | 102.6992 | -0.27 | 0.73 | -0.79 | 0.21 | -0.65 | 0.35 | 71.29 | 25.39
2019-10-01 | 10:04 | 102.8125 | 102.8125 | -0.27 | 0.73 | -0.79 | 0.21 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 10:04 | 102.9023 | 102.9023 | -0.16 | 0.84 | -0.88 | 0.12 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 103.0117 | 103.0117 | -0.11 | 0.89 | -0.87 | 0.13 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 103.1211 | 103.1211 | -0.1 | 0.9 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 103.2227 | 103.2227 | -0.1 | 0.9 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 103.3203 | 103.3203 | -0.1 | 0.9 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 103.4102 | 103.4102 | -0.1 | 0.9 | -0.86 | 0.14 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 103.5117 | 103.5117 | -0.09 | 0.91 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 27.34
2019-10-01 | 10:04 | 103.6094 | 103.6094 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 10:04 | 103.7109 | 103.7109 | -0.09 | 0.91 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 103.8203 | 103.8203 | -0.08 | 0.92 | -0.85 | 0.15 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 103.9219 | 103.9219 | -0.08 | 0.92 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 104.0195 | 104.0195 | -0.14 | 0.86 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 104.1328 | 104.1328 | -0.23 | 0.77 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:04 | 104.2305 | 104.2305 | -0.26 | 0.74 | -0.76 | 0.24 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 10:04 | 104.332 | 104.332 | -0.26 | 0.74 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:04 | 104.4414 | 104.4414 | -0.12 | 0.88 | -0.88 | 0.12 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 104.5508 | 104.5508 | -0.1 | 0.9 | -0.86 | 0.14 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 104.6406 | 104.6406 | -0.09 | 0.91 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 104.7422 | 104.7422 | -0.09 | 0.91 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 104.8516 | 104.8516 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 10:04 | 104.9414 | 104.9414 | -0.09 | 0.91 | -0.84 | 0.16 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:04 | 105.0508 | 105.0508 | -0.08 | 0.92 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 105.1602 | 105.1602 | -0.08 | 0.92 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 105.2617 | 105.2617 | -0.09 | 0.91 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:04 | 105.3711 | 105.3711 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 105.4609 | 105.4609 | -0.08 | 0.92 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 105.5703 | 105.5703 | -0.17 | 0.83 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 105.6719 | 105.6719 | -0.26 | 0.74 | -0.79 | 0.21 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 105.7813 | 105.7813 | -0.27 | 0.73 | -0.76 | 0.24 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:04 | 105.8828 | 105.8828 | -0.26 | 0.74 | -0.76 | 0.24 | -0.64 | 0.36 | 72.27 | 24.41
2019-10-01 | 10:04 | 105.9922 | 105.9922 | -0.12 | 0.88 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 10:04 | 106.082 | 106.082 | -0.1 | 0.9 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 106.1797 | 106.1797 | -0.1 | 0.9 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 106.2813 | 106.2813 | -0.08 | 0.92 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:04 | 106.3906 | 106.3906 | -0.08 | 0.92 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 106.4922 | 106.4922 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 106.6016 | 106.6016 | -0.07 | 0.93 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 106.7109 | 106.7109 | -0.08 | 0.92 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 106.8008 | 106.8008 | -0.08 | 0.92 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 106.9023 | 106.9023 | -0.07 | 0.93 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 107.0117 | 107.0117 | -0.09 | 0.91 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 107.1016 | 107.1016 | -0.2 | 0.8 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 10:04 | 107.2109 | 107.2109 | -0.24 | 0.76 | -0.76 | 0.24 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 107.3203 | 107.3203 | -0.25 | 0.75 | -0.78 | 0.22 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 107.4219 | 107.4219 | -0.11 | 0.89 | -0.87 | 0.13 | -0.64 | 0.36 | 72.27 | 23.44
2019-10-01 | 10:04 | 107.5195 | 107.5195 | -0.1 | 0.9 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 107.6211 | 107.6211 | -0.1 | 0.9 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 107.7305 | 107.7305 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 107.832 | 107.832 | -0.08 | 0.92 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 107.9297 | 107.9297 | -0.08 | 0.92 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 25.39
2019-10-01 | 10:04 | 108.0313 | 108.0313 | -0.07 | 0.93 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 108.1328 | 108.1328 | -0.08 | 0.92 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 108.2305 | 108.2305 | -0.07 | 0.93 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:04 | 108.3398 | 108.3398 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 108.4414 | 108.4414 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 108.543 | 108.543 | -0.13 | 0.87 | -0.79 | 0.21 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 108.6523 | 108.6523 | -0.23 | 0.77 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 108.7422 | 108.7422 | -0.26 | 0.74 | -0.75 | 0.25 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 10:04 | 108.8516 | 108.8516 | -0.26 | 0.74 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 10:04 | 108.9609 | 108.9609 | -0.11 | 0.89 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 10:04 | 109.0625 | 109.0625 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 109.1914 | 109.1914 | -0.09 | 0.91 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 10:04 | 109.293 | 109.293 | -0.09 | 0.91 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 109.3906 | 109.3906 | -0.08 | 0.92 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 109.4922 | 109.4922 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 10:04 | 109.5898 | 109.5898 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 109.6914 | 109.6914 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 109.793 | 109.793 | -0.07 | 0.93 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 24.41
2019-10-01 | 10:04 | 109.8906 | 109.8906 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 109.9922 | 109.9922 | -0.07 | 0.93 | -0.82 | 0.18 | -0.7 | 0.3 | 72.27 | 25.39
2019-10-01 | 10:04 | 110.1094 | 110.1094 | -0.19 | 0.81 | -0.77 | 0.23 | -0.68 | 0.32 | 74.22 | 27.34
2019-10-01 | 10:04 | 110.2109 | 110.2109 | -0.24 | 0.76 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 110.3125 | 110.3125 | -0.24 | 0.76 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 28.32
2019-10-01 | 10:04 | 110.3906 | 110.3906 | -0.14 | 0.86 | -0.84 | 0.16 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 110.5 | 110.5 | -0.1 | 0.9 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:04 | 110.6016 | 110.6016 | -0.09 | 0.91 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 110.6992 | 110.6992 | -0.07 | 0.93 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 110.8008 | 110.8008 | -0.08 | 0.92 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 110.9102 | 110.9102 | -0.07 | 0.93 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:04 | 111.0117 | 111.0117 | -0.08 | 0.92 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 111.1094 | 111.1094 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 111.2422 | 111.2422 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 111.3516 | 111.3516 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 24.41
2019-10-01 | 10:04 | 111.4492 | 111.4492 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 111.5508 | 111.5508 | -0.1 | 0.9 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 111.6328 | 111.6328 | -0.22 | 0.78 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 111.7305 | 111.7305 | -0.22 | 0.78 | -0.78 | 0.22 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:04 | 111.8398 | 111.8398 | -0.24 | 0.76 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 111.9414 | 111.9414 | -0.11 | 0.89 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 112.043 | 112.043 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 112.1797 | 112.1797 | -0.07 | 0.93 | -0.86 | 0.14 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:04 | 112.25 | 112.25 | -0.07 | 0.93 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 112.3711 | 112.3711 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 112.4492 | 112.4492 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:04 | 112.5508 | 112.5508 | -0.07 | 0.93 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 112.6523 | 112.6523 | -0.06 | 0.94 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 112.7617 | 112.7617 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 112.8594 | 112.8594 | -0.06 | 0.94 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 10:04 | 112.9609 | 112.9609 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 113.0625 | 113.0625 | -0.16 | 0.84 | -0.79 | 0.21 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:04 | 113.1719 | 113.1719 | -0.22 | 0.78 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 113.2813 | 113.2813 | -0.23 | 0.77 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:04 | 113.3828 | 113.3828 | -0.24 | 0.76 | -0.84 | 0.16 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:04 | 113.4805 | 113.4805 | -0.08 | 0.92 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 113.582 | 113.582 | -0.09 | 0.91 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:04 | 113.6914 | 113.6914 | -0.07 | 0.93 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 113.7813 | 113.7813 | -0.07 | 0.93 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:04 | 113.9023 | 113.9023 | -0.06 | 0.94 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 114 | 114 | -0.06 | 0.94 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:04 | 114.1094 | 114.1094 | -0.07 | 0.93 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 25.39
2019-10-01 | 10:04 | 114.1992 | 114.1992 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 114.3008 | 114.3008 | -0.04 | 0.96 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 114.4297 | 114.4297 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 27.34
2019-10-01 | 10:04 | 114.5313 | 114.5313 | -0.06 | 0.94 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 114.6328 | 114.6328 | -0.18 | 0.82 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 10:04 | 114.7227 | 114.7227 | -0.23 | 0.77 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:04 | 114.832 | 114.832 | -0.22 | 0.78 | -0.78 | 0.22 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 10:04 | 114.9492 | 114.9492 | -0.09 | 0.91 | -0.87 | 0.13 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 115.0508 | 115.0508 | -0.07 | 0.93 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 115.1328 | 115.1328 | -0.06 | 0.94 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 115.2227 | 115.2227 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 115.3203 | 115.3203 | -0.06 | 0.94 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 115.4297 | 115.4297 | -0.05 | 0.95 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:04 | 115.5313 | 115.5313 | -0.05 | 0.95 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 115.6406 | 115.6406 | -0.05 | 0.95 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 115.7422 | 115.7422 | -0.05 | 0.95 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 115.8398 | 115.8398 | -0.04 | 0.96 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 10:04 | 115.9492 | 115.9492 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 116.0508 | 116.0508 | -0.08 | 0.92 | -0.8 | 0.2 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:04 | 116.1523 | 116.1523 | -0.2 | 0.8 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:04 | 116.25 | 116.25 | -0.24 | 0.76 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:04 | 116.3594 | 116.3594 | -0.25 | 0.75 | -0.77 | 0.23 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:04 | 116.4609 | 116.4609 | -0.09 | 0.91 | -0.87 | 0.13 | -0.65 | 0.35 | 74.22 | 27.34
2019-10-01 | 10:04 | 116.5625 | 116.5625 | -0.08 | 0.92 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 10:04 | 116.6602 | 116.6602 | -0.07 | 0.93 | -0.85 | 0.15 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:04 | 116.793 | 116.793 | -0.06 | 0.94 | -0.83 | 0.17 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:04 | 116.8906 | 116.8906 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-10-01 | 10:04 | 116.9922 | 116.9922 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 117.0898 | 117.0898 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 71.29 | 26.37
2019-10-01 | 10:04 | 117.1992 | 117.1992 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 117.293 | 117.293 | -0.04 | 0.96 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:04 | 117.3906 | 117.3906 | -0.05 | 0.95 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:04 | 117.4922 | 117.4922 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:04 | 117.582 | 117.582 | -0.15 | 0.85 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 10:04 | 117.7109 | 117.7109 | -0.23 | 0.77 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:04 | 117.832 | 117.832 | -0.24 | 0.76 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:04 | 117.9102 | 117.9102 | -0.16 | 0.84 | -0.81 | 0.19 | -0.64 | 0.36 | 72.27 | 26.37
2019-10-01 | 10:04 | 118.0117 | 118.0117 | -0.08 | 0.92 | -0.85 | 0.15 | -0.64 | 0.36 | 73.24 | 27.34
2019-10-01 | 10:04 | 118.1094 | 118.1094 | -0.06 | 0.94 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:04 | 118.2109 | 118.2109 | -0.07 | 0.93 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:04 | 118.3125 | 118.3125 | -0.07 | 0.93 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 10:04 | 118.4102 | 118.4102 | -0.06 | 0.94 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 118.5117 | 118.5117 | -0.07 | 0.93 | -0.84 | 0.16 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:04 | 118.6094 | 118.6094 | -0.06 | 0.94 | -0.83 | 0.17 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:04 | 118.7227 | 118.7227 | -0.05 | 0.95 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:04 | 118.8203 | 118.8203 | -0.04 | 0.96 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 27.34
2019-10-01 | 10:04 | 118.9219 | 118.9219 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:04 | 119.0195 | 119.0195 | -0.07 | 0.93 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:04 | 119.1406 | 119.1406 | -0.19 | 0.81 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 119.25 | 119.25 | -0.22 | 0.78 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 119.3398 | 119.3398 | -0.24 | 0.76 | -0.78 | 0.22 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 119.4414 | 119.4414 | -0.1 | 0.9 | -0.86 | 0.14 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 119.543 | 119.543 | -0.07 | 0.93 | -0.86 | 0.14 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:05 | 119.6523 | 119.6523 | -0.06 | 0.94 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:05 | 119.75 | 119.75 | -0.06 | 0.94 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 119.8516 | 119.8516 | -0.05 | 0.95 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:05 | 119.9805 | 119.9805 | -0.06 | 0.94 | -0.85 | 0.15 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 10:05 | 120.082 | 120.082 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 10:05 | 120.1719 | 120.1719 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 120.2617 | 120.2617 | -0.05 | 0.95 | -0.83 | 0.17 | -0.68 | 0.32 | 74.22 | 27.34
2019-10-01 | 10:05 | 120.3711 | 120.3711 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:05 | 120.4727 | 120.4727 | -0.04 | 0.96 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:05 | 120.5703 | 120.5703 | -0.1 | 0.9 | -0.8 | 0.2 | -0.69 | 0.31 | 73.24 | 26.37
2019-10-01 | 10:05 | 120.6797 | 120.6797 | -0.19 | 0.81 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 120.7813 | 120.7813 | -0.22 | 0.78 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 120.8711 | 120.8711 | -0.22 | 0.78 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 120.9805 | 120.9805 | -0.08 | 0.92 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 121.0898 | 121.0898 | -0.07 | 0.93 | -0.86 | 0.14 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 121.1914 | 121.1914 | -0.07 | 0.93 | -0.85 | 0.15 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 121.3125 | 121.3125 | -0.06 | 0.94 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:05 | 121.4023 | 121.4023 | -0.06 | 0.94 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 121.5117 | 121.5117 | -0.05 | 0.95 | -0.85 | 0.15 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 121.6016 | 121.6016 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 121.6914 | 121.6914 | -0.04 | 0.96 | -0.84 | 0.16 | -0.69 | 0.31 | 73.24 | 26.37
2019-10-01 | 10:05 | 121.8008 | 121.8008 | -0.05 | 0.95 | -0.83 | 0.17 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:05 | 121.9297 | 121.9297 | -0.04 | 0.96 | -0.85 | 0.15 | -0.69 | 0.31 | 73.24 | 25.39
2019-10-01 | 10:05 | 122.0313 | 122.0313 | -0.03 | 0.97 | -0.83 | 0.17 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:05 | 122.1211 | 122.1211 | -0.15 | 0.85 | -0.8 | 0.2 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 10:05 | 122.2109 | 122.2109 | -0.22 | 0.78 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 122.3203 | 122.3203 | -0.22 | 0.78 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 122.4102 | 122.4102 | -0.1 | 0.9 | -0.87 | 0.13 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 122.5313 | 122.5313 | -0.07 | 0.93 | -0.87 | 0.13 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 122.6406 | 122.6406 | -0.05 | 0.95 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 122.7305 | 122.7305 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 122.832 | 122.832 | -0.05 | 0.95 | -0.85 | 0.15 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 122.9492 | 122.9492 | -0.05 | 0.95 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 123.043 | 123.043 | -0.04 | 0.96 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 123.1406 | 123.1406 | -0.05 | 0.95 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 123.2305 | 123.2305 | -0.04 | 0.96 | -0.85 | 0.15 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 10:05 | 123.3516 | 123.3516 | -0.04 | 0.96 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:05 | 123.4609 | 123.4609 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 123.5625 | 123.5625 | -0.08 | 0.92 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 123.6523 | 123.6523 | -0.2 | 0.8 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 10:05 | 123.7617 | 123.7617 | -0.21 | 0.79 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 123.8594 | 123.8594 | -0.23 | 0.77 | -0.78 | 0.22 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 123.9609 | 123.9609 | -0.08 | 0.92 | -0.87 | 0.13 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 124.0625 | 124.0625 | -0.05 | 0.95 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 124.1719 | 124.1719 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 10:05 | 124.2695 | 124.2695 | -0.05 | 0.95 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 124.4219 | 124.4219 | -0.05 | 0.95 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 124.5 | 124.5 | -0.05 | 0.95 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 124.6016 | 124.6016 | -0.04 | 0.96 | -0.83 | 0.17 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:05 | 124.6914 | 124.6914 | -0.05 | 0.95 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 124.8008 | 124.8008 | -0.03 | 0.97 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:05 | 124.9023 | 124.9023 | -0.04 | 0.96 | -0.84 | 0.16 | -0.69 | 0.31 | 72.27 | 26.37
2019-10-01 | 10:05 | 124.9922 | 124.9922 | -0.03 | 0.97 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 10:05 | 125.0898 | 125.0898 | -0.13 | 0.87 | -0.8 | 0.2 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 10:05 | 125.1914 | 125.1914 | -0.22 | 0.78 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 125.3008 | 125.3008 | -0.23 | 0.77 | -0.77 | 0.23 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 10:05 | 125.4023 | 125.4023 | -0.17 | 0.83 | -0.81 | 0.19 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 10:05 | 125.5 | 125.5 | -0.07 | 0.93 | -0.86 | 0.14 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 125.6016 | 125.6016 | -0.05 | 0.95 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 125.7109 | 125.7109 | -0.04 | 0.96 | -0.85 | 0.15 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 125.8125 | 125.8125 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 125.9102 | 125.9102 | -0.04 | 0.96 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:05 | 126.0117 | 126.0117 | -0.04 | 0.96 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 126.1211 | 126.1211 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 27.34
2019-10-01 | 10:05 | 126.2227 | 126.2227 | -0.04 | 0.96 | -0.84 | 0.16 | -0.69 | 0.31 | 74.22 | 25.39
2019-10-01 | 10:05 | 126.332 | 126.332 | -0.04 | 0.96 | -0.83 | 0.17 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 126.4219 | 126.4219 | -0.05 | 0.95 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 126.5313 | 126.5313 | -0.06 | 0.94 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:05 | 126.6328 | 126.6328 | -0.18 | 0.82 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 10:05 | 126.7422 | 126.7422 | -0.22 | 0.78 | -0.78 | 0.22 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 126.8398 | 126.8398 | -0.22 | 0.78 | -0.78 | 0.22 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 126.9609 | 126.9609 | -0.08 | 0.92 | -0.86 | 0.14 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 127.0625 | 127.0625 | -0.08 | 0.92 | -0.86 | 0.14 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 127.1523 | 127.1523 | -0.07 | 0.93 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 127.2695 | 127.2695 | -0.07 | 0.93 | -0.83 | 0.17 | -0.65 | 0.35 | 73.24 | 24.41
2019-10-01 | 10:05 | 127.3594 | 127.3594 | -0.07 | 0.93 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 127.4492 | 127.4492 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 74.22 | 26.37
2019-10-01 | 10:05 | 127.5625 | 127.5625 | -0.06 | 0.94 | -0.83 | 0.17 | -0.66 | 0.34 | 71.29 | 25.39
2019-10-01 | 10:05 | 127.6602 | 127.6602 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 127.7617 | 127.7617 | -0.07 | 0.93 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:05 | 127.8711 | 127.8711 | -0.05 | 0.95 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 127.9727 | 127.9727 | -0.06 | 0.94 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 128.0703 | 128.0703 | -0.12 | 0.88 | -0.8 | 0.2 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 128.1719 | 128.1719 | -0.22 | 0.78 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 128.2813 | 128.2813 | -0.23 | 0.77 | -0.76 | 0.24 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 128.4102 | 128.4102 | -0.23 | 0.77 | -0.77 | 0.23 | -0.63 | 0.37 | 74.22 | 27.34
2019-10-01 | 10:05 | 128.5117 | 128.5117 | -0.1 | 0.9 | -0.84 | 0.16 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:05 | 128.5898 | 128.5898 | -0.08 | 0.92 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 128.6992 | 128.6992 | -0.07 | 0.93 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 128.793 | 128.793 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 128.8906 | 128.8906 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 129.0117 | 129.0117 | -0.06 | 0.94 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 129.1094 | 129.1094 | -0.05 | 0.95 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 129.2109 | 129.2109 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:05 | 129.3125 | 129.3125 | -0.06 | 0.94 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:05 | 129.4023 | 129.4023 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 129.5117 | 129.5117 | -0.07 | 0.93 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:05 | 129.6094 | 129.6094 | -0.18 | 0.82 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:05 | 129.7227 | 129.7227 | -0.24 | 0.76 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:05 | 129.8203 | 129.8203 | -0.23 | 0.77 | -0.77 | 0.23 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 129.9297 | 129.9297 | -0.12 | 0.88 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 130.0195 | 130.0195 | -0.1 | 0.9 | -0.85 | 0.15 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 130.1328 | 130.1328 | -0.08 | 0.92 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 130.2305 | 130.2305 | -0.08 | 0.92 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 130.332 | 130.332 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 130.4297 | 130.4297 | -0.07 | 0.93 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 130.543 | 130.543 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 71.29 | 26.37
2019-10-01 | 10:05 | 130.6406 | 130.6406 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:05 | 130.7422 | 130.7422 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 130.8516 | 130.8516 | -0.07 | 0.93 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 130.9492 | 130.9492 | -0.06 | 0.94 | -0.83 | 0.17 | -0.69 | 0.31 | 73.24 | 26.37
2019-10-01 | 10:05 | 131.0508 | 131.0508 | -0.09 | 0.91 | -0.8 | 0.2 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:05 | 131.1523 | 131.1523 | -0.21 | 0.79 | -0.77 | 0.23 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 131.2617 | 131.2617 | -0.24 | 0.76 | -0.76 | 0.24 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 10:05 | 131.3594 | 131.3594 | -0.24 | 0.76 | -0.74 | 0.26 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 131.4609 | 131.4609 | -0.1 | 0.9 | -0.85 | 0.15 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 131.5625 | 131.5625 | -0.09 | 0.91 | -0.85 | 0.15 | -0.67 | 0.33 | 71.29 | 25.39
2019-10-01 | 10:05 | 131.6719 | 131.6719 | -0.08 | 0.92 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 131.8008 | 131.8008 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 25.39
2019-10-01 | 10:05 | 131.9023 | 131.9023 | -0.07 | 0.93 | -0.83 | 0.17 | -0.69 | 0.31 | 72.27 | 25.39
2019-10-01 | 10:05 | 132 | 132 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:05 | 132.0898 | 132.0898 | -0.06 | 0.94 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 132.1992 | 132.1992 | -0.06 | 0.94 | -0.82 | 0.18 | -0.67 | 0.33 | 71.29 | 26.37
2019-10-01 | 10:05 | 132.293 | 132.293 | -0.06 | 0.94 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 132.3906 | 132.3906 | -0.06 | 0.94 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 27.34
2019-10-01 | 10:05 | 132.4922 | 132.4922 | -0.05 | 0.95 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 132.5898 | 132.5898 | -0.17 | 0.83 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 132.6914 | 132.6914 | -0.23 | 0.77 | -0.76 | 0.24 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 132.793 | 132.793 | -0.25 | 0.75 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 132.9023 | 132.9023 | -0.23 | 0.77 | -0.77 | 0.23 | -0.65 | 0.35 | 71.29 | 25.39
2019-10-01 | 10:05 | 133 | 133 | -0.08 | 0.92 | -0.84 | 0.16 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:05 | 133.1094 | 133.1094 | -0.08 | 0.92 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 133.2109 | 133.2109 | -0.07 | 0.93 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 133.3125 | 133.3125 | -0.06 | 0.94 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 133.4297 | 133.4297 | -0.07 | 0.93 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 133.5313 | 133.5313 | -0.05 | 0.95 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 28.32
2019-10-01 | 10:05 | 133.6328 | 133.6328 | -0.05 | 0.95 | -0.84 | 0.16 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:05 | 133.7227 | 133.7227 | -0.07 | 0.93 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 27.34
2019-10-01 | 10:05 | 133.832 | 133.832 | -0.05 | 0.95 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 133.9297 | 133.9297 | -0.05 | 0.95 | -0.82 | 0.18 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 134.0313 | 134.0313 | -0.09 | 0.91 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 24.41
2019-10-01 | 10:05 | 134.1523 | 134.1523 | -0.23 | 0.77 | -0.78 | 0.22 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 134.25 | 134.25 | -0.26 | 0.74 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 10:05 | 134.3594 | 134.3594 | -0.28 | 0.72 | -0.75 | 0.25 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 134.4492 | 134.4492 | -0.14 | 0.86 | -0.84 | 0.16 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 134.5625 | 134.5625 | -0.12 | 0.88 | -0.83 | 0.17 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 134.6523 | 134.6523 | -0.13 | 0.87 | -0.83 | 0.17 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:05 | 134.75 | 134.75 | -0.12 | 0.88 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 28.32
2019-10-01 | 10:05 | 134.8516 | 134.8516 | -0.11 | 0.89 | -0.83 | 0.17 | -0.68 | 0.32 | 72.27 | 26.37
2019-10-01 | 10:05 | 134.9492 | 134.9492 | -0.11 | 0.89 | -0.81 | 0.19 | -0.68 | 0.32 | 71.29 | 25.39
2019-10-01 | 10:05 | 135.082 | 135.082 | -0.11 | 0.89 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 135.1602 | 135.1602 | -0.11 | 0.89 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 135.2695 | 135.2695 | -0.09 | 0.91 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 135.3711 | 135.3711 | -0.08 | 0.92 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 135.4727 | 135.4727 | -0.09 | 0.91 | -0.83 | 0.17 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 135.5703 | 135.5703 | -0.15 | 0.85 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 135.6797 | 135.6797 | -0.25 | 0.75 | -0.76 | 0.24 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 135.7813 | 135.7813 | -0.27 | 0.73 | -0.75 | 0.25 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 135.8906 | 135.8906 | -0.28 | 0.72 | -0.76 | 0.24 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 135.9922 | 135.9922 | -0.13 | 0.87 | -0.86 | 0.14 | -0.67 | 0.33 | 72.27 | 27.34
2019-10-01 | 10:05 | 136.0898 | 136.0898 | -0.11 | 0.89 | -0.84 | 0.16 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 10:05 | 136.1914 | 136.1914 | -0.1 | 0.9 | -0.83 | 0.17 | -0.66 | 0.34 | 72.27 | 28.32
2019-10-01 | 10:05 | 136.293 | 136.293 | -0.14 | 0.86 | -0.82 | 0.18 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 136.3906 | 136.3906 | -0.12 | 0.88 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 136.5 | 136.5 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 136.6211 | 136.6211 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 25.39
2019-10-01 | 10:05 | 136.6992 | 136.6992 | -0.09 | 0.91 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 136.8203 | 136.8203 | -0.12 | 0.88 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 136.9219 | 136.9219 | -0.09 | 0.91 | -0.82 | 0.18 | -0.68 | 0.32 | 73.24 | 26.37
2019-10-01 | 10:05 | 137.043 | 137.043 | -0.09 | 0.91 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 137.1328 | 137.1328 | -0.17 | 0.83 | -0.78 | 0.22 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 10:05 | 137.2305 | 137.2305 | -0.24 | 0.76 | -0.74 | 0.26 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 137.3398 | 137.3398 | -0.26 | 0.74 | -0.76 | 0.24 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 137.4297 | 137.4297 | -0.13 | 0.87 | -0.84 | 0.16 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 137.5313 | 137.5313 | -0.1 | 0.9 | -0.85 | 0.15 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:05 | 137.6328 | 137.6328 | -0.09 | 0.91 | -0.84 | 0.16 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 137.7305 | 137.7305 | -0.1 | 0.9 | -0.84 | 0.16 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 137.8398 | 137.8398 | -0.13 | 0.87 | -0.83 | 0.17 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 137.9414 | 137.9414 | -0.12 | 0.88 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 138.0625 | 138.0625 | -0.09 | 0.91 | -0.83 | 0.17 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 138.1719 | 138.1719 | -0.07 | 0.93 | -0.82 | 0.18 | -0.67 | 0.33 | 74.22 | 27.34
2019-10-01 | 10:05 | 138.2695 | 138.2695 | -0.08 | 0.92 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 138.3828 | 138.3828 | -0.08 | 0.92 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 138.4492 | 138.4492 | -0.09 | 0.91 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 28.32
2019-10-01 | 10:05 | 138.5625 | 138.5625 | -0.1 | 0.9 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 24.41
2019-10-01 | 10:05 | 138.6523 | 138.6523 | -0.21 | 0.79 | -0.76 | 0.24 | -0.65 | 0.35 | 74.22 | 27.34
2019-10-01 | 10:05 | 138.7695 | 138.7695 | -0.24 | 0.76 | -0.75 | 0.25 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:05 | 138.8711 | 138.8711 | -0.24 | 0.76 | -0.74 | 0.26 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 138.9805 | 138.9805 | -0.11 | 0.89 | -0.85 | 0.15 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 10:05 | 139.0898 | 139.0898 | -0.1 | 0.9 | -0.83 | 0.17 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 139.1914 | 139.1914 | -0.1 | 0.9 | -0.82 | 0.18 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 139.2813 | 139.2813 | -0.09 | 0.91 | -0.82 | 0.18 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 139.3828 | 139.3828 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 139.4805 | 139.4805 | -0.12 | 0.88 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 25.39
2019-10-01 | 10:05 | 139.582 | 139.582 | -0.13 | 0.87 | -0.82 | 0.18 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 139.6797 | 139.6797 | -0.11 | 0.89 | -0.82 | 0.18 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:05 | 139.7813 | 139.7813 | -0.1 | 0.9 | -0.81 | 0.19 | -0.68 | 0.32 | 73.24 | 25.39
2019-10-01 | 10:05 | 139.9023 | 139.9023 | -0.1 | 0.9 | -0.81 | 0.19 | -0.67 | 0.33 | 72.27 | 26.37
2019-10-01 | 10:05 | 140 | 140 | -0.08 | 0.92 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 140.1211 | 140.1211 | -0.11 | 0.89 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 25.39
2019-10-01 | 10:05 | 140.2422 | 140.2422 | -0.2 | 0.8 | -0.75 | 0.25 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 140.332 | 140.332 | -0.23 | 0.77 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 140.4297 | 140.4297 | -0.25 | 0.75 | -0.73 | 0.27 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 140.5313 | 140.5313 | -0.11 | 0.89 | -0.83 | 0.17 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 140.6211 | 140.6211 | -0.11 | 0.89 | -0.82 | 0.18 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 140.7422 | 140.7422 | -0.1 | 0.9 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 140.8203 | 140.8203 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 24.41
2019-10-01 | 10:05 | 140.9297 | 140.9297 | -0.12 | 0.88 | -0.81 | 0.19 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 10:05 | 141.0313 | 141.0313 | -0.11 | 0.89 | -0.81 | 0.19 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 141.1328 | 141.1328 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 25.39
2019-10-01 | 10:05 | 141.2617 | 141.2617 | -0.09 | 0.91 | -0.8 | 0.2 | -0.67 | 0.33 | 72.27 | 24.41
2019-10-01 | 10:05 | 141.3516 | 141.3516 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 141.4492 | 141.4492 | -0.1 | 0.9 | -0.81 | 0.19 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 141.5508 | 141.5508 | -0.13 | 0.87 | -0.79 | 0.21 | -0.67 | 0.33 | 74.22 | 26.37
2019-10-01 | 10:05 | 141.6602 | 141.6602 | -0.24 | 0.76 | -0.74 | 0.26 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:05 | 141.7617 | 141.7617 | -0.26 | 0.74 | -0.73 | 0.27 | -0.64 | 0.36 | 74.22 | 27.34
2019-10-01 | 10:05 | 141.8594 | 141.8594 | -0.25 | 0.75 | -0.73 | 0.27 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 141.9492 | 141.9492 | -0.12 | 0.88 | -0.83 | 0.17 | -0.63 | 0.37 | 72.27 | 26.37
2019-10-01 | 10:05 | 142.0625 | 142.0625 | -0.12 | 0.88 | -0.81 | 0.19 | -0.64 | 0.36 | 72.27 | 27.34
2019-10-01 | 10:05 | 142.1602 | 142.1602 | -0.11 | 0.89 | -0.81 | 0.19 | -0.66 | 0.34 | 72.27 | 26.37
2019-10-01 | 10:05 | 142.2617 | 142.2617 | -0.11 | 0.89 | -0.79 | 0.21 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:05 | 142.3828 | 142.3828 | -0.1 | 0.9 | -0.8 | 0.2 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:05 | 142.4727 | 142.4727 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 142.5625 | 142.5625 | -0.11 | 0.89 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 142.6719 | 142.6719 | -0.09 | 0.91 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 142.7617 | 142.7617 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 142.8711 | 142.8711 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:05 | 142.9727 | 142.9727 | -0.09 | 0.91 | -0.8 | 0.2 | -0.67 | 0.33 | 73.24 | 26.37
2019-10-01 | 10:05 | 143.082 | 143.082 | -0.13 | 0.87 | -0.77 | 0.23 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 143.1797 | 143.1797 | -0.23 | 0.77 | -0.74 | 0.26 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 10:05 | 143.2813 | 143.2813 | -0.26 | 0.74 | -0.71 | 0.29 | -0.63 | 0.37 | 74.22 | 26.37
2019-10-01 | 10:05 | 143.3828 | 143.3828 | -0.25 | 0.75 | -0.73 | 0.27 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 10:05 | 143.4922 | 143.4922 | -0.11 | 0.89 | -0.82 | 0.18 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 143.6211 | 143.6211 | -0.11 | 0.89 | -0.81 | 0.19 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:05 | 143.7109 | 143.7109 | -0.1 | 0.9 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 143.8008 | 143.8008 | -0.08 | 0.92 | -0.81 | 0.19 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 143.9023 | 143.9023 | -0.09 | 0.91 | -0.8 | 0.2 | -0.66 | 0.34 | 74.22 | 26.37
2019-10-01 | 10:05 | 144 | 144 | -0.09 | 0.91 | -0.79 | 0.21 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:05 | 144.1016 | 144.1016 | -0.08 | 0.92 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 144.2227 | 144.2227 | -0.08 | 0.92 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 27.34
2019-10-01 | 10:05 | 144.3203 | 144.3203 | -0.08 | 0.92 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 144.4219 | 144.4219 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 72.27 | 27.34
2019-10-01 | 10:05 | 144.543 | 144.543 | -0.08 | 0.92 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 144.6211 | 144.6211 | -0.16 | 0.84 | -0.74 | 0.26 | -0.65 | 0.35 | 72.27 | 26.37
2019-10-01 | 10:05 | 144.7422 | 144.7422 | -0.22 | 0.78 | -0.75 | 0.25 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 10:05 | 144.8516 | 144.8516 | -0.25 | 0.75 | -0.7 | 0.3 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 10:05 | 144.9492 | 144.9492 | -0.12 | 0.88 | -0.78 | 0.22 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 10:05 | 145.0508 | 145.0508 | -0.11 | 0.89 | -0.81 | 0.19 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 145.1406 | 145.1406 | -0.09 | 0.91 | -0.8 | 0.2 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 145.25 | 145.25 | -0.08 | 0.92 | -0.8 | 0.2 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 145.3398 | 145.3398 | -0.09 | 0.91 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 26.37
2019-10-01 | 10:05 | 145.4414 | 145.4414 | -0.08 | 0.92 | -0.79 | 0.21 | -0.66 | 0.34 | 74.22 | 25.39
2019-10-01 | 10:05 | 145.5508 | 145.5508 | -0.08 | 0.92 | -0.79 | 0.21 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:05 | 145.6406 | 145.6406 | -0.08 | 0.92 | -0.79 | 0.21 | -0.65 | 0.35 | 72.27 | 25.39
2019-10-01 | 10:05 | 145.7422 | 145.7422 | -0.09 | 0.91 | -0.8 | 0.2 | -0.66 | 0.34 | 72.27 | 25.39
2019-10-01 | 10:05 | 145.8516 | 145.8516 | -0.07 | 0.93 | -0.79 | 0.21 | -0.67 | 0.33 | 73.24 | 27.34
2019-10-01 | 10:05 | 145.9492 | 145.9492 | -0.07 | 0.93 | -0.79 | 0.21 | -0.66 | 0.34 | 73.24 | 27.34
2019-10-01 | 10:05 | 146.0625 | 146.0625 | -0.12 | 0.88 | -0.76 | 0.24 | -0.66 | 0.34 | 74.22 | 27.34
2019-10-01 | 10:05 | 146.1602 | 146.1602 | -0.23 | 0.77 | -0.7 | 0.3 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 10:05 | 146.2617 | 146.2617 | -0.24 | 0.76 | -0.7 | 0.3 | -0.61 | 0.39 | 73.24 | 27.34
2019-10-01 | 10:05 | 146.3594 | 146.3594 | -0.25 | 0.75 | -0.7 | 0.3 | -0.62 | 0.38 | 74.22 | 25.39
2019-10-01 | 10:05 | 146.4609 | 146.4609 | -0.1 | 0.9 | -0.81 | 0.19 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 10:05 | 146.5703 | 146.5703 | -0.09 | 0.91 | -0.8 | 0.2 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 10:05 | 146.6719 | 146.6719 | -0.08 | 0.92 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 146.7695 | 146.7695 | -0.1 | 0.9 | -0.79 | 0.21 | -0.62 | 0.38 | 74.22 | 25.39
2019-10-01 | 10:05 | 146.8711 | 146.8711 | -0.08 | 0.92 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 146.9805 | 146.9805 | -0.06 | 0.94 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 25.39
2019-10-01 | 10:05 | 147.0898 | 147.0898 | -0.07 | 0.93 | -0.78 | 0.22 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 10:05 | 147.1797 | 147.1797 | -0.08 | 0.92 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 10:05 | 147.293 | 147.293 | -0.07 | 0.93 | -0.79 | 0.21 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 10:05 | 147.3906 | 147.3906 | -0.07 | 0.93 | -0.78 | 0.22 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 147.4922 | 147.4922 | -0.07 | 0.93 | -0.79 | 0.21 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 10:05 | 147.6016 | 147.6016 | -0.14 | 0.86 | -0.72 | 0.28 | -0.63 | 0.37 | 75.2 | 27.34
2019-10-01 | 10:05 | 147.6992 | 147.6992 | -0.23 | 0.77 | -0.7 | 0.3 | -0.62 | 0.38 | 73.24 | 26.37
2019-10-01 | 10:05 | 147.8008 | 147.8008 | -0.24 | 0.76 | -0.69 | 0.31 | -0.62 | 0.38 | 74.22 | 27.34
2019-10-01 | 10:05 | 147.9023 | 147.9023 | -0.24 | 0.76 | -0.68 | 0.32 | -0.62 | 0.38 | 74.22 | 26.37
2019-10-01 | 10:05 | 148.0117 | 148.0117 | -0.1 | 0.9 | -0.8 | 0.2 | -0.63 | 0.37 | 72.27 | 25.39
2019-10-01 | 10:05 | 148.1094 | 148.1094 | -0.09 | 0.91 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 10:05 | 148.2227 | 148.2227 | -0.09 | 0.91 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 10:05 | 148.3203 | 148.3203 | -0.08 | 0.92 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 148.4219 | 148.4219 | -0.09 | 0.91 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 27.34
2019-10-01 | 10:05 | 148.5313 | 148.5313 | -0.08 | 0.92 | -0.78 | 0.22 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 148.6211 | 148.6211 | -0.08 | 0.92 | -0.78 | 0.22 | -0.64 | 0.36 | 73.24 | 25.39
2019-10-01 | 10:05 | 148.7305 | 148.7305 | -0.08 | 0.92 | -0.79 | 0.21 | -0.64 | 0.36 | 75.2 | 26.37
2019-10-01 | 10:05 | 148.832 | 148.832 | -0.07 | 0.93 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 148.9219 | 148.9219 | -0.07 | 0.93 | -0.79 | 0.21 | -0.65 | 0.35 | 73.24 | 27.34
2019-10-01 | 10:05 | 149.0313 | 149.0313 | -0.07 | 0.93 | -0.78 | 0.22 | -0.65 | 0.35 | 73.24 | 26.37
2019-10-01 | 10:05 | 149.1406 | 149.1406 | -0.19 | 0.81 | -0.7 | 0.3 | -0.63 | 0.37 | 73.24 | 27.34
2019-10-01 | 10:05 | 149.2422 | 149.2422 | -0.21 | 0.79 | -0.67 | 0.33 | -0.62 | 0.38 | 73.24 | 25.39
2019-10-01 | 10:05 | 149.3398 | 149.3398 | -0.24 | 0.76 | -0.67 | 0.33 | -0.61 | 0.39 | 73.24 | 27.34
2019-10-01 | 10:05 | 149.4492 | 149.4492 | -0.1 | 0.9 | -0.79 | 0.21 | -0.62 | 0.38 | 74.22 | 26.37
2019-10-01 | 10:05 | 149.5625 | 149.5625 | -0.09 | 0.91 | -0.79 | 0.21 | -0.6 | 0.4 | 73.24 | 27.34
2019-10-01 | 10:05 | 149.6719 | 149.6719 | -0.09 | 0.91 | -0.78 | 0.22 | -0.63 | 0.37 | 74.22 | 25.39
2019-10-01 | 10:05 | 149.7695 | 149.7695 | -0.09 | 0.91 | -0.79 | 0.21 | -0.64 | 0.36 | 73.24 | 27.34
2019-10-01 | 10:05 | 149.8594 | 149.8594 | -0.08 | 0.92 | -0.77 | 0.23 | -0.63 | 0.37 | 73.24 | 27.34
2019-10-01 | 10:05 | 149.9805 | 149.9805 | -0.07 | 0.93 | -0.78 | 0.22 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 10:05 | 150.1016 | 150.1016 | -0.07 | 0.93 | -0.78 | 0.22 | -0.62 | 0.38 | 73.24 | 25.39
2019-10-01 | 10:05 | 150.1992 | 150.1992 | -0.07 | 0.93 | -0.77 | 0.23 | -0.64 | 0.36 | 72.27 | 25.39
2019-10-01 | 10:05 | 150.2813 | 150.2813 | -0.06 | 0.94 | -0.77 | 0.23 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 150.3828 | 150.3828 | -0.07 | 0.93 | -0.77 | 0.23 | -0.64 | 0.36 | 73.24 | 26.37
2019-10-01 | 10:05 | 150.4922 | 150.4922 | -0.07 | 0.93 | -0.76 | 0.24 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 10:05 | 150.5898 | 150.5898 | -0.13 | 0.87 | -0.72 | 0.28 | -0.64 | 0.36 | 74.22 | 25.39
2019-10-01 | 10:05 | 150.6914 | 150.6914 | -0.22 | 0.78 | -0.67 | 0.33 | -0.62 | 0.38 | 74.22 | 26.37
2019-10-01 | 10:05 | 150.7813 | 150.7813 | -0.22 | 0.78 | -0.67 | 0.33 | -0.62 | 0.38 | 73.24 | 26.37
2019-10-01 | 10:05 | 150.8828 | 150.8828 | -0.23 | 0.77 | -0.67 | 0.33 | -0.61 | 0.39 | 73.24 | 25.39
2019-10-01 | 10:05 | 150.9922 | 150.9922 | -0.09 | 0.91 | -0.78 | 0.22 | -0.62 | 0.38 | 73.24 | 25.39
2019-10-01 | 10:05 | 151.1094 | 151.1094 | -0.1 | 0.9 | -0.78 | 0.22 | -0.62 | 0.38 | 73.24 | 26.37
2019-10-01 | 10:05 | 151.2227 | 151.2227 | -0.09 | 0.91 | -0.77 | 0.23 | -0.62 | 0.38 | 72.27 | 26.37
2019-10-01 | 10:05 | 151.3008 | 151.3008 | -0.08 | 0.92 | -0.76 | 0.24 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 10:05 | 151.4102 | 151.4102 | -0.08 | 0.92 | -0.76 | 0.24 | -0.64 | 0.36 | 74.22 | 26.37
2019-10-01 | 10:05 | 151.5195 | 151.5195 | -0.08 | 0.92 | -0.76 | 0.24 | -0.62 | 0.38 | 73.24 | 26.37
2019-10-01 | 10:05 | 151.6094 | 151.6094 | -0.07 | 0.93 | -0.76 | 0.24 | -0.63 | 0.37 | 74.22 | 25.39
2019-10-01 | 10:05 | 151.7109 | 151.7109 | -0.08 | 0.92 | -0.77 | 0.23 | -0.63 | 0.37 | 75.2 | 25.39
2019-10-01 | 10:05 | 151.8125 | 151.8125 | -0.08 | 0.92 | -0.77 | 0.23 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 10:05 | 151.9219 | 151.9219 | -0.06 | 0.94 | -0.76 | 0.24 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 10:05 | 152.0313 | 152.0313 | -0.07 | 0.93 | -0.76 | 0.24 | -0.62 | 0.38 | 74.22 | 27.34
2019-10-01 | 10:05 | 152.1211 | 152.1211 | -0.17 | 0.83 | -0.66 | 0.34 | -0.6 | 0.4 | 73.24 | 26.37
2019-10-01 | 10:05 | 152.2422 | 152.2422 | -0.21 | 0.79 | -0.65 | 0.35 | -0.58 | 0.42 | 74.22 | 26.37
2019-10-01 | 10:05 | 152.3594 | 152.3594 | -0.23 | 0.77 | -0.66 | 0.34 | -0.58 | 0.42 | 72.27 | 24.41
2019-10-01 | 10:05 | 152.4414 | 152.4414 | -0.15 | 0.85 | -0.72 | 0.28 | -0.59 | 0.41 | 73.24 | 25.39
2019-10-01 | 10:05 | 152.543 | 152.543 | -0.1 | 0.9 | -0.77 | 0.23 | -0.6 | 0.4 | 73.24 | 26.37
2019-10-01 | 10:05 | 152.6602 | 152.6602 | -0.09 | 0.91 | -0.77 | 0.23 | -0.62 | 0.38 | 75.2 | 25.39
2019-10-01 | 10:05 | 152.75 | 152.75 | -0.08 | 0.92 | -0.77 | 0.23 | -0.61 | 0.39 | 73.24 | 27.34
2019-10-01 | 10:05 | 152.8398 | 152.8398 | -0.08 | 0.92 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 27.34
2019-10-01 | 10:05 | 152.9414 | 152.9414 | -0.1 | 0.9 | -0.76 | 0.24 | -0.62 | 0.38 | 75.2 | 25.39
2019-10-01 | 10:05 | 153.0508 | 153.0508 | -0.11 | 0.89 | -0.76 | 0.24 | -0.63 | 0.37 | 73.24 | 25.39
2019-10-01 | 10:05 | 153.1523 | 153.1523 | -0.11 | 0.89 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 25.39
2019-10-01 | 10:05 | 153.25 | 153.25 | -0.1 | 0.9 | -0.75 | 0.25 | -0.62 | 0.38 | 73.24 | 25.39
2019-10-01 | 10:05 | 153.3398 | 153.3398 | -0.1 | 0.9 | -0.75 | 0.25 | -0.62 | 0.38 | 73.24 | 25.39
2019-10-01 | 10:05 | 153.4727 | 153.4727 | -0.09 | 0.91 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 25.39
2019-10-01 | 10:05 | 153.5703 | 153.5703 | -0.11 | 0.89 | -0.72 | 0.28 | -0.63 | 0.37 | 73.24 | 26.37
2019-10-01 | 10:05 | 153.6602 | 153.6602 | -0.2 | 0.8 | -0.65 | 0.35 | -0.59 | 0.41 | 74.22 | 26.37
2019-10-01 | 10:05 | 153.7617 | 153.7617 | -0.21 | 0.79 | -0.64 | 0.36 | -0.59 | 0.41 | 74.22 | 26.37
2019-10-01 | 10:05 | 153.8711 | 153.8711 | -0.23 | 0.77 | -0.65 | 0.35 | -0.6 | 0.4 | 73.24 | 27.34
2019-10-01 | 10:05 | 153.9609 | 153.9609 | -0.1 | 0.9 | -0.76 | 0.24 | -0.6 | 0.4 | 75.2 | 27.34
2019-10-01 | 10:05 | 154.0703 | 154.0703 | -0.1 | 0.9 | -0.75 | 0.25 | -0.61 | 0.39 | 73.24 | 26.37
2019-10-01 | 10:05 | 154.1797 | 154.1797 | -0.09 | 0.91 | -0.75 | 0.25 | -0.61 | 0.39 | 75.2 | 25.39
2019-10-01 | 10:05 | 154.2813 | 154.2813 | -0.07 | 0.93 | -0.76 | 0.24 | -0.61 | 0.39 | 73.24 | 25.39
2019-10-01 | 10:05 | 154.3828 | 154.3828 | -0.08 | 0.92 | -0.75 | 0.25 | -0.62 | 0.38 | 73.24 | 25.39
2019-10-01 | 10:05 | 154.5 | 154.5 | -0.08 | 0.92 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 26.37
2019-10-01 | 10:05 | 154.6094 | 154.6094 | -0.07 | 0.93 | -0.75 | 0.25 | -0.62 | 0.38 | 73.24 | 25.39
2019-10-01 | 10:05 | 154.6992 | 154.6992 | -0.08 | 0.92 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 26.37
2019-10-01 | 10:05 | 154.8008 | 154.8008 | -0.07 | 0.93 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 26.37
2019-10-01 | 10:05 | 154.9023 | 154.9023 | -0.08 | 0.92 | -0.75 | 0.25 | -0.63 | 0.37 | 73.24 | 27.34
2019-10-01 | 10:05 | 154.9922 | 154.9922 | -0.07 | 0.93 | -0.74 | 0.26 | -0.61 | 0.39 | 75.2 | 27.34
2019-10-01 | 10:05 | 155.1016 | 155.1016 | -0.15 | 0.85 | -0.67 | 0.33 | -0.61 | 0.39 | 74.22 | 25.39
2019-10-01 | 10:05 | 155.2109 | 155.2109 | -0.2 | 0.8 | -0.64 | 0.36 | -0.59 | 0.41 | 74.22 | 27.34
2019-10-01 | 10:05 | 155.332 | 155.332 | -0.21 | 0.79 | -0.63 | 0.37 | -0.57 | 0.43 | 74.22 | 25.39
2019-10-01 | 10:05 | 155.4414 | 155.4414 | -0.22 | 0.78 | -0.63 | 0.37 | -0.57 | 0.43 | 73.24 | 25.39
2019-10-01 | 10:05 | 155.5195 | 155.5195 | -0.08 | 0.92 | -0.76 | 0.24 | -0.6 | 0.4 | 74.22 | 25.39
2019-10-01 | 10:05 | 155.6328 | 155.6328 | -0.09 | 0.91 | -0.75 | 0.25 | -0.6 | 0.4 | 73.24 | 25.39
2019-10-01 | 10:05 | 155.7305 | 155.7305 | -0.08 | 0.92 | -0.74 | 0.26 | -0.59 | 0.41 | 74.22 | 25.39
2019-10-01 | 10:05 | 155.8203 | 155.8203 | -0.08 | 0.92 | -0.74 | 0.26 | -0.58 | 0.42 | 75.2 | 25.39
2019-10-01 | 10:05 | 155.9219 | 155.9219 | -0.08 | 0.92 | -0.75 | 0.25 | -0.61 | 0.39 | 73.24 | 25.39
2019-10-01 | 10:05 | 156.0195 | 156.0195 | -0.07 | 0.93 | -0.75 | 0.25 | -0.6 | 0.4 | 75.2 | 25.39
2019-10-01 | 10:05 | 156.1406 | 156.1406 | -0.08 | 0.92 | -0.74 | 0.26 | -0.61 | 0.39 | 73.24 | 25.39
2019-10-01 | 10:05 | 156.2422 | 156.2422 | -0.07 | 0.93 | -0.74 | 0.26 | -0.62 | 0.38 | 74.22 | 26.37
2019-10-01 | 10:05 | 156.3398 | 156.3398 | -0.05 | 0.95 | -0.74 | 0.26 | -0.61 | 0.39 | 73.24 | 26.37
2019-10-01 | 10:05 | 156.4609 | 156.4609 | -0.06 | 0.94 | -0.75 | 0.25 | -0.63 | 0.37 | 74.22 | 26.37
2019-10-01 | 10:05 | 156.5625 | 156.5625 | -0.07 | 0.93 | -0.72 | 0.28 | -0.62 | 0.38 | 74.22 | 27.34
2019-10-01 | 10:05 | 156.6602 | 156.6602 | -0.16 | 0.84 | -0.65 | 0.35 | -0.6 | 0.4 | 74.22 | 27.34
2019-10-01 | 10:05 | 156.7695 | 156.7695 | -0.2 | 0.8 | -0.62 | 0.38 | -0.58 | 0.42 | 75.2 | 25.39
2019-10-01 | 10:05 | 156.8711 | 156.8711 | -0.21 | 0.79 | -0.62 | 0.38 | -0.57 | 0.43 | 74.22 | 25.39
2019-10-01 | 10:05 | 156.9609 | 156.9609 | -0.1 | 0.9 | -0.72 | 0.28 | -0.59 | 0.41 | 73.24 | 25.39
2019-10-01 | 10:05 | 157.0625 | 157.0625 | -0.07 | 0.93 | -0.75 | 0.25 | -0.59 | 0.41 | 73.24 | 25.39
2019-10-01 | 10:05 | 157.1602 | 157.1602 | -0.08 | 0.92 | -0.74 | 0.26 | -0.6 | 0.4 | 74.22 | 27.34
2019-10-01 | 10:05 | 157.25 | 157.25 | -0.07 | 0.93 | -0.74 | 0.26 | -0.6 | 0.4 | 73.24 | 25.39
2019-10-01 | 10:05 | 157.3594 | 157.3594 | -0.06 | 0.94 | -0.74 | 0.26 | -0.6 | 0.4 | 74.22 | 25.39
2019-10-01 | 10:05 | 157.4609 | 157.4609 | -0.06 | 0.94 | -0.75 | 0.25 | -0.61 | 0.39 | 74.22 | 25.39
2019-10-01 | 10:05 | 157.5625 | 157.5625 | -0.05 | 0.95 | -0.73 | 0.27 | -0.6 | 0.4 | 73.24 | 25.39
2019-10-01 | 10:05 | 157.6719 | 157.6719 | -0.04 | 0.96 | -0.75 | 0.25 | -0.62 | 0.38 | 74.22 | 27.34
2019-10-01 | 10:05 | 157.7695 | 157.7695 | -0.05 | 0.95 | -0.74 | 0.26 | -0.6 | 0.4 | 75.2 | 25.39
2019-10-01 | 10:05 | 157.8711 | 157.8711 | -0.05 | 0.95 | -0.73 | 0.27 | -0.61 | 0.39 | 74.22 | 26.37
2019-10-01 | 10:05 | 157.9805 | 157.9805 | -0.05 | 0.95 | -0.74 | 0.26 | -0.61 | 0.39 | 74.22 | 26.37
2019-10-01 | 10:05 | 158.082 | 158.082 | -0.12 | 0.88 | -0.68 | 0.32 | -0.6 | 0.4 | 74.22 | 26.37
2019-10-01 | 10:05 | 158.1797 | 158.1797 | -0.18 | 0.82 | -0.62 | 0.38 | -0.57 | 0.43 | 74.22 | 26.37
2019-10-01 | 10:05 | 158.2813 | 158.2813 | -0.19 | 0.81 | -0.62 | 0.38 | -0.56 | 0.44 | 75.2 | 25.39
2019-10-01 | 10:05 | 158.3906 | 158.3906 | -0.2 | 0.8 | -0.61 | 0.39 | -0.56 | 0.44 | 74.22 | 25.39
2019-10-01 | 10:05 | 158.4922 | 158.4922 | -0.07 | 0.93 | -0.73 | 0.27 | -0.58 | 0.42 | 74.22 | 26.37
2019-10-01 | 10:05 | 158.5898 | 158.5898 | -0.07 | 0.93 | -0.73 | 0.27 | -0.59 | 0.41 | 74.22 | 25.39
2019-10-01 | 10:05 | 158.6992 | 158.6992 | -0.05 | 0.95 | -0.73 | 0.27 | -0.61 | 0.39 | 74.22 | 26.37
2019-10-01 | 10:05 | 158.8008 | 158.8008 | -0.05 | 0.95 | -0.73 | 0.27 | -0.6 | 0.4 | 74.22 | 27.34
2019-10-01 | 10:05 | 158.9023 | 158.9023 | -0.05 | 0.95 | -0.73 | 0.27 | -0.61 | 0.39 | 74.22 | 26.37
2019-10-01 | 10:05 | 159.0117 | 159.0117 | -0.06 | 0.94 | -0.73 | 0.27 | -0.6 | 0.4 | 74.22 | 25.39
2019-10-01 | 10:05 | 159.1094 | 159.1094 | -0.05 | 0.95 | -0.72 | 0.28 | -0.6 | 0.4 | 75.2 | 25.39
2019-10-01 | 10:05 | 159.2109 | 159.2109 | -0.04 | 0.96 | -0.73 | 0.27 | -0.59 | 0.41 | 73.24 | 25.39
2019-10-01 | 10:05 | 159.3125 | 159.3125 | -0.04 | 0.96 | -0.72 | 0.28 | -0.6 | 0.4 | 75.2 | 25.39
2019-10-01 | 10:05 | 159.4219 | 159.4219 | -0.06 | 0.94 | -0.73 | 0.27 | -0.6 | 0.4 | 74.22 | 26.37
2019-10-01 | 10:05 | 159.5313 | 159.5313 | -0.04 | 0.96 | -0.73 | 0.27 | -0.6 | 0.4 | 75.2 | 26.37
2019-10-01 | 10:05 | 159.6211 | 159.6211 | -0.15 | 0.85 | -0.64 | 0.36 | -0.6 | 0.4 | 74.22 | 26.37
2019-10-01 | 10:05 | 159.7227 | 159.7227 | -0.18 | 0.82 | -0.61 | 0.39 | -0.56 | 0.44 | 74.22 | 27.34
2019-10-01 | 10:05 | 159.8203 | 159.8203 | -0.19 | 0.81 | -0.61 | 0.39 | -0.57 | 0.43 | 74.22 | 26.37
2019-10-01 | 10:05 | 159.9297 | 159.9297 | -0.12 | 0.88 | -0.65 | 0.35 | -0.56 | 0.44 | 74.22 | 25.39
2019-10-01 | 10:05 | 160.0313 | 160.0313 | -0.06 | 0.94 | -0.73 | 0.27 | -0.59 | 0.41 | 74.22 | 26.37
2019-10-01 | 10:05 | 160.1328 | 160.1328 | -0.05 | 0.95 | -0.73 | 0.27 | -0.58 | 0.42 | 74.22 | 26.37
2019-10-01 | 10:05 | 160.2422 | 160.2422 | -0.06 | 0.94 | -0.73 | 0.27 | -0.59 | 0.41 | 75.2 | 25.39
2019-10-01 | 10:05 | 160.3516 | 160.3516 | -0.06 | 0.94 | -0.73 | 0.27 | -0.6 | 0.4 | 74.22 | 26.37
2019-10-01 | 10:05 | 160.4492 | 160.4492 | -0.06 | 0.94 | -0.73 | 0.27 | -0.59 | 0.41 | 73.24 | 25.39
2019-10-01 | 10:05 | 160.5508 | 160.5508 | -0.05 | 0.95 | -0.72 | 0.28 | -0.6 | 0.4 | 73.24 | 27.34
2019-10-01 | 10:05 | 160.6406 | 160.6406 | -0.04 | 0.96 | -0.73 | 0.27 | -0.59 | 0.41 | 73.24 | 27.34
2019-10-01 | 10:05 | 160.7813 | 160.7813 | -0.04 | 0.96 | -0.72 | 0.28 | -0.59 | 0.41 | 74.22 | 26.37
2019-10-01 | 10:05 | 160.8594 | 160.8594 | -0.03 | 0.97 | -0.73 | 0.27 | -0.61 | 0.39 | 74.22 | 26.37
2019-10-01 | 10:05 | 160.9609 | 160.9609 | -0.04 | 0.96 | -0.73 | 0.27 | -0.59 | 0.41 | 74.22 | 29.3
2019-10-01 | 10:05 | 161.0625 | 161.0625 | -0.09 | 0.91 | -0.69 | 0.31 | -0.61 | 0.39 | 76.17 | 27.34
2019-10-01 | 10:05 | 161.1602 | 161.1602 | -0.17 | 0.83 | -0.62 | 0.38 | -0.59 | 0.41 | 74.22 | 26.37
2019-10-01 | 10:05 | 161.2695 | 161.2695 | -0.17 | 0.83 | -0.61 | 0.39 | -0.57 | 0.43 | 75.2 | 26.37
2019-10-01 | 10:05 | 161.3711 | 161.3711 | -0.19 | 0.81 | -0.6 | 0.4 | -0.55 | 0.45 | 74.22 | 25.39
2019-10-01 | 10:05 | 161.4805 | 161.4805 | -0.07 | 0.93 | -0.71 | 0.29 | -0.57 | 0.43 | 75.2 | 25.39
2019-10-01 | 10:05 | 161.582 | 161.582 | -0.05 | 0.95 | -0.72 | 0.28 | -0.58 | 0.42 | 73.24 | 25.39
2019-10-01 | 10:05 | 161.6797 | 161.6797 | -0.06 | 0.94 | -0.72 | 0.28 | -0.59 | 0.41 | 75.2 | 29.3
2019-10-01 | 10:05 | 161.7813 | 161.7813 | -0.05 | 0.95 | -0.72 | 0.28 | -0.6 | 0.4 | 74.22 | 28.32
2019-10-01 | 10:05 | 161.9102 | 161.9102 | -0.05 | 0.95 | -0.72 | 0.28 | -0.58 | 0.42 | 75.2 | 27.34
2019-10-01 | 10:05 | 162.0117 | 162.0117 | -0.06 | 0.94 | -0.71 | 0.29 | -0.58 | 0.42 | 73.24 | 25.39
2019-10-01 | 10:05 | 162.1094 | 162.1094 | -0.05 | 0.95 | -0.72 | 0.28 | -0.57 | 0.43 | 73.24 | 24.41
2019-10-01 | 10:05 | 162.2109 | 162.2109 | -0.05 | 0.95 | -0.72 | 0.28 | -0.58 | 0.42 | 74.22 | 26.37
2019-10-01 | 10:05 | 162.293 | 162.293 | -0.05 | 0.95 | -0.72 | 0.28 | -0.59 | 0.41 | 74.22 | 25.39
2019-10-01 | 10:05 | 162.4023 | 162.4023 | -0.05 | 0.95 | -0.72 | 0.28 | -0.58 | 0.42 | 75.2 | 28.32
2019-10-01 | 10:05 | 162.5 | 162.5 | -0.05 | 0.95 | -0.72 | 0.28 | -0.58 | 0.42 | 75.2 | 28.32
2019-10-01 | 10:05 | 162.6016 | 162.6016 | -0.13 | 0.87 | -0.64 | 0.36 | -0.58 | 0.42 | 76.17 | 26.37
2019-10-01 | 10:05 | 162.6992 | 162.6992 | -0.18 | 0.82 | -0.61 | 0.39 | -0.56 | 0.44 | 75.2 | 28.32
2019-10-01 | 10:05 | 162.8125 | 162.8125 | -0.18 | 0.82 | -0.59 | 0.41 | -0.55 | 0.45 | 75.2 | 26.37
2019-10-01 | 10:05 | 162.9102 | 162.9102 | -0.19 | 0.81 | -0.59 | 0.41 | -0.53 | 0.47 | 74.22 | 27.34
2019-10-01 | 10:05 | 163.0117 | 163.0117 | -0.06 | 0.94 | -0.71 | 0.29 | -0.56 | 0.44 | 74.22 | 25.39
2019-10-01 | 10:05 | 163.1094 | 163.1094 | -0.06 | 0.94 | -0.71 | 0.29 | -0.58 | 0.42 | 74.22 | 27.34
2019-10-01 | 10:05 | 163.2109 | 163.2109 | -0.06 | 0.94 | -0.7 | 0.3 | -0.58 | 0.42 | 74.22 | 28.32
2019-10-01 | 10:05 | 163.3203 | 163.3203 | -0.05 | 0.95 | -0.71 | 0.29 | -0.56 | 0.44 | 74.22 | 28.32
2019-10-01 | 10:05 | 163.4219 | 163.4219 | -0.06 | 0.94 | -0.71 | 0.29 | -0.57 | 0.43 | 74.22 | 26.37
2019-10-01 | 10:05 | 163.5313 | 163.5313 | -0.05 | 0.95 | -0.7 | 0.3 | -0.58 | 0.42 | 74.22 | 25.39
2019-10-01 | 10:05 | 163.6328 | 163.6328 | -0.04 | 0.96 | -0.71 | 0.29 | -0.57 | 0.43 | 74.22 | 24.41
2019-10-01 | 10:05 | 163.7305 | 163.7305 | -0.04 | 0.96 | -0.7 | 0.3 | -0.57 | 0.43 | 73.24 | 25.39
2019-10-01 | 10:05 | 163.832 | 163.832 | -0.05 | 0.95 | -0.7 | 0.3 | -0.56 | 0.44 | 75.2 | 25.39
2019-10-01 | 10:05 | 163.9297 | 163.9297 | -0.04 | 0.96 | -0.69 | 0.31 | -0.57 | 0.43 | 75.2 | 29.3
2019-10-01 | 10:05 | 164.043 | 164.043 | -0.06 | 0.94 | -0.68 | 0.32 | -0.59 | 0.41 | 75.2 | 28.32
2019-10-01 | 10:05 | 164.1406 | 164.1406 | -0.16 | 0.84 | -0.62 | 0.38 | -0.57 | 0.43 | 74.22 | 26.37
2019-10-01 | 10:05 | 164.2422 | 164.2422 | -0.17 | 0.83 | -0.6 | 0.4 | -0.54 | 0.46 | 75.2 | 27.34
2019-10-01 | 10:05 | 164.3398 | 164.3398 | -0.19 | 0.81 | -0.58 | 0.42 | -0.53 | 0.47 | 75.2 | 25.39
2019-10-01 | 10:05 | 164.4492 | 164.4492 | -0.08 | 0.92 | -0.68 | 0.32 | -0.55 | 0.45 | 74.22 | 25.39
2019-10-01 | 10:05 | 164.5625 | 164.5625 | -0.06 | 0.94 | -0.71 | 0.29 | -0.57 | 0.43 | 74.22 | 26.37
2019-10-01 | 10:05 | 164.6719 | 164.6719 | -0.05 | 0.95 | -0.71 | 0.29 | -0.56 | 0.44 | 75.2 | 29.3
2019-10-01 | 10:05 | 164.7695 | 164.7695 | -0.06 | 0.94 | -0.71 | 0.29 | -0.56 | 0.44 | 75.2 | 28.32
2019-10-01 | 10:05 | 164.8711 | 164.8711 | -0.06 | 0.94 | -0.7 | 0.3 | -0.58 | 0.42 | 74.22 | 24.41
2019-10-01 | 10:05 | 164.9609 | 164.9609 | -0.06 | 0.94 | -0.7 | 0.3 | -0.57 | 0.43 | 75.2 | 26.37
2019-10-01 | 10:05 | 165.0898 | 165.0898 | -0.06 | 0.94 | -0.69 | 0.31 | -0.56 | 0.44 | 74.22 | 24.41
2019-10-01 | 10:05 | 165.2109 | 165.2109 | -0.06 | 0.94 | -0.71 | 0.29 | -0.57 | 0.43 | 74.22 | 25.39
2019-10-01 | 10:05 | 165.3008 | 165.3008 | -0.05 | 0.95 | -0.69 | 0.31 | -0.59 | 0.41 | 74.22 | 25.39
2019-10-01 | 10:05 | 165.3828 | 165.3828 | -0.04 | 0.96 | -0.71 | 0.29 | -0.58 | 0.42 | 75.2 | 27.34
2019-10-01 | 10:05 | 165.4805 | 165.4805 | -0.05 | 0.95 | -0.7 | 0.3 | -0.56 | 0.44 | 74.22 | 29.3
2019-10-01 | 10:05 | 165.582 | 165.582 | -0.11 | 0.89 | -0.62 | 0.38 | -0.55 | 0.45 | 75.2 | 27.34
2019-10-01 | 10:05 | 165.6797 | 165.6797 | -0.17 | 0.83 | -0.59 | 0.41 | -0.55 | 0.45 | 74.22 | 26.37
2019-10-01 | 10:05 | 165.793 | 165.793 | -0.18 | 0.82 | -0.58 | 0.42 | -0.53 | 0.47 | 76.17 | 25.39
2019-10-01 | 10:05 | 165.9023 | 165.9023 | -0.19 | 0.81 | -0.56 | 0.44 | -0.55 | 0.45 | 75.2 | 25.39
2019-10-01 | 10:05 | 165.9922 | 165.9922 | -0.06 | 0.94 | -0.68 | 0.32 | -0.54 | 0.46 | 73.24 | 25.39
2019-10-01 | 10:05 | 166.1016 | 166.1016 | -0.04 | 0.96 | -0.69 | 0.31 | -0.56 | 0.44 | 74.22 | 26.37
2019-10-01 | 10:05 | 166.1992 | 166.1992 | -0.05 | 0.95 | -0.7 | 0.3 | -0.56 | 0.44 | 76.17 | 29.3
2019-10-01 | 10:05 | 166.3203 | 166.3203 | -0.05 | 0.95 | -0.7 | 0.3 | -0.57 | 0.43 | 75.2 | 29.3
2019-10-01 | 10:05 | 166.4297 | 166.4297 | -0.05 | 0.95 | -0.69 | 0.31 | -0.55 | 0.45 | 74.22 | 27.34
2019-10-01 | 10:05 | 166.5117 | 166.5117 | -0.04 | 0.96 | -0.7 | 0.3 | -0.57 | 0.43 | 74.22 | 26.37
2019-10-01 | 10:05 | 166.6211 | 166.6211 | -0.04 | 0.96 | -0.69 | 0.31 | -0.57 | 0.43 | 74.22 | 25.39
2019-10-01 | 10:05 | 166.75 | 166.75 | -0.03 | 0.97 | -0.69 | 0.31 | -0.58 | 0.42 | 74.22 | 25.39
2019-10-01 | 10:05 | 166.832 | 166.832 | -0.03 | 0.97 | -0.7 | 0.3 | -0.56 | 0.44 | 74.22 | 24.41
2019-10-01 | 10:05 | 166.9102 | 166.9102 | -0.04 | 0.96 | -0.68 | 0.32 | -0.57 | 0.43 | 74.22 | 27.34
2019-10-01 | 10:05 | 167.0195 | 167.0195 | -0.05 | 0.95 | -0.68 | 0.32 | -0.57 | 0.43 | 74.22 | 28.32
2019-10-01 | 10:05 | 167.1211 | 167.1211 | -0.13 | 0.87 | -0.59 | 0.41 | -0.56 | 0.44 | 76.17 | 33.2
2019-10-01 | 10:05 | 167.2305 | 167.2305 | -0.18 | 0.82 | -0.58 | 0.42 | -0.55 | 0.45 | 75.2 | 27.34
2019-10-01 | 10:05 | 167.332 | 167.332 | -0.19 | 0.81 | -0.56 | 0.44 | -0.52 | 0.48 | 74.22 | 24.41
2019-10-01 | 10:05 | 167.4297 | 167.4297 | -0.16 | 0.84 | -0.62 | 0.38 | -0.52 | 0.48 | 74.22 | 26.37
2019-10-01 | 10:05 | 167.543 | 167.543 | -0.05 | 0.95 | -0.72 | 0.28 | -0.55 | 0.45 | 75.2 | 26.37
2019-10-01 | 10:05 | 167.6328 | 167.6328 | -0.05 | 0.95 | -0.73 | 0.27 | -0.56 | 0.44 | 75.2 | 26.37
2019-10-01 | 10:05 | 167.7617 | 167.7617 | -0.04 | 0.96 | -0.71 | 0.29 | -0.56 | 0.44 | 74.22 | 28.32
2019-10-01 | 10:05 | 167.8516 | 167.8516 | -0.04 | 0.96 | -0.73 | 0.27 | -0.56 | 0.44 | 74.22 | 27.34
2019-10-01 | 10:05 | 167.9727 | 167.9727 | -0.03 | 0.97 | -0.71 | 0.29 | -0.55 | 0.45 | 75.2 | 26.37
2019-10-01 | 10:05 | 168.0703 | 168.0703 | -0.03 | 0.97 | -0.71 | 0.29 | -0.56 | 0.44 | 74.22 | 24.41
2019-10-01 | 10:05 | 168.1523 | 168.1523 | -0.03 | 0.97 | -0.71 | 0.29 | -0.56 | 0.44 | 75.2 | 26.37
2019-10-01 | 10:05 | 168.25 | 168.25 | -0.04 | 0.96 | -0.71 | 0.29 | -0.56 | 0.44 | 73.24 | 25.39
2019-10-01 | 10:05 | 168.3594 | 168.3594 | -0.04 | 0.96 | -0.69 | 0.31 | -0.56 | 0.44 | 74.22 | 25.39
2019-10-01 | 10:05 | 168.4609 | 168.4609 | -0.03 | 0.97 | -0.69 | 0.31 | -0.56 | 0.44 | 75.2 | 29.3
2019-10-01 | 10:05 | 168.5625 | 168.5625 | -0.09 | 0.91 | -0.66 | 0.34 | -0.55 | 0.45 | 75.2 | 29.3
2019-10-01 | 10:05 | 168.6602 | 168.6602 | -0.15 | 0.85 | -0.59 | 0.41 | -0.52 | 0.48 | 76.17 | 27.34
2019-10-01 | 10:05 | 168.7695 | 168.7695 | -0.18 | 0.82 | -0.62 | 0.38 | -0.53 | 0.47 | 76.17 | 27.34
2019-10-01 | 10:05 | 168.8711 | 168.8711 | -0.19 | 0.81 | -0.63 | 0.37 | -0.53 | 0.47 | 76.17 | 26.37
2019-10-01 | 10:05 | 168.9922 | 168.9922 | -0.07 | 0.93 | -0.74 | 0.26 | -0.53 | 0.47 | 75.2 | 25.39
2019-10-01 | 10:05 | 169.082 | 169.082 | -0.04 | 0.96 | -0.72 | 0.28 | -0.55 | 0.45 | 75.2 | 26.37
2019-10-01 | 10:05 | 169.1719 | 169.1719 | -0.05 | 0.95 | -0.72 | 0.28 | -0.55 | 0.45 | 74.22 | 28.32
2019-10-01 | 10:05 | 169.293 | 169.293 | -0.03 | 0.97 | -0.71 | 0.29 | -0.55 | 0.45 | 74.22 | 29.3
2019-10-01 | 10:05 | 169.4102 | 169.4102 | -0.03 | 0.97 | -0.7 | 0.3 | -0.56 | 0.44 | 74.22 | 20.51
2019-10-01 | 10:05 | 169.5 | 169.5 | -0.03 | 0.97 | -0.7 | 0.3 | -0.55 | 0.45 | 75.2 | 26.37
2019-10-01 | 10:05 | 169.6094 | 169.6094 | -0.03 | 0.97 | -0.7 | 0.3 | -0.53 | 0.47 | 75.2 | 25.39
2019-10-01 | 10:05 | 169.7305 | 169.7305 | -0.04 | 0.96 | -0.7 | 0.3 | -0.55 | 0.45 | 74.22 | 25.39
2019-10-01 | 10:05 | 169.8203 | 169.8203 | -0.02 | 0.98 | -0.69 | 0.31 | -0.56 | 0.44 | 75.2 | 26.37
2019-10-01 | 10:05 | 169.9023 | 169.9023 | -0.03 | 0.97 | -0.69 | 0.31 | -0.54 | 0.46 | 74.22 | 27.34
2019-10-01 | 10:05 | 170 | 170 | -0.03 | 0.97 | -0.68 | 0.32 | -0.55 | 0.45 | 76.17 | 28.32
2019-10-01 | 10:05 | 170.1016 | 170.1016 | -0.14 | 0.86 | -0.61 | 0.39 | -0.54 | 0.46 | 75.2 | 27.34
2019-10-01 | 10:05 | 170.1992 | 170.1992 | -0.15 | 0.85 | -0.59 | 0.41 | -0.52 | 0.48 | 75.2 | 27.34
2019-10-01 | 10:05 | 170.3125 | 170.3125 | -0.18 | 0.82 | -0.6 | 0.4 | -0.52 | 0.48 | 74.22 | 26.37
2019-10-01 | 10:05 | 170.4102 | 170.4102 | -0.17 | 0.83 | -0.6 | 0.4 | -0.51 | 0.49 | 75.2 | 25.39
2019-10-01 | 10:05 | 170.5195 | 170.5195 | -0.05 | 0.95 | -0.7 | 0.3 | -0.52 | 0.48 | 74.22 | 26.37
2019-10-01 | 10:05 | 170.6211 | 170.6211 | -0.04 | 0.96 | -0.69 | 0.31 | -0.55 | 0.45 | 74.22 | 27.34
2019-10-01 | 10:05 | 170.7227 | 170.7227 | -0.04 | 0.96 | -0.69 | 0.31 | -0.54 | 0.46 | 75.2 | 29.3
2019-10-01 | 10:05 | 170.8203 | 170.8203 | -0.04 | 0.96 | -0.68 | 0.32 | -0.54 | 0.46 | 75.2 | 28.32
2019-10-01 | 10:05 | 170.9219 | 170.9219 | -0.04 | 0.96 | -0.68 | 0.32 | -0.54 | 0.46 | 75.2 | 26.37
2019-10-01 | 10:05 | 171.0313 | 171.0313 | -0.04 | 0.96 | -0.68 | 0.32 | -0.54 | 0.46 | 74.22 | 26.37
2019-10-01 | 10:05 | 171.1328 | 171.1328 | -0.01 | 0.99 | -0.67 | 0.33 | -0.54 | 0.46 | 74.22 | 26.37
2019-10-01 | 10:05 | 171.2305 | 171.2305 | -0.03 | 0.97 | -0.68 | 0.32 | -0.54 | 0.46 | 76.17 | 25.39
2019-10-01 | 10:05 | 171.332 | 171.332 | -0.04 | 0.96 | -0.67 | 0.33 | -0.54 | 0.46 | 75.2 | 26.37
2019-10-01 | 10:05 | 171.4414 | 171.4414 | -0.04 | 0.96 | -0.66 | 0.34 | -0.54 | 0.46 | 75.2 | 28.32
2019-10-01 | 10:05 | 171.5703 | 171.5703 | -0.08 | 0.92 | -0.64 | 0.36 | -0.55 | 0.45 | 75.2 | 29.3
2019-10-01 | 10:05 | 171.6719 | 171.6719 | -0.14 | 0.86 | -0.58 | 0.42 | -0.51 | 0.49 | 76.17 | 12.7
2019-10-01 | 10:05 | 171.7617 | 171.7617 | -0.16 | 0.84 | -0.56 | 0.44 | -0.52 | 0.48 | 75.2 | 26.37
2019-10-01 | 10:05 | 171.8594 | 171.8594 | -0.17 | 0.83 | -0.55 | 0.45 | -0.5 | 0.5 | 74.22 | 25.39
2019-10-01 | 10:05 | 171.9609 | 171.9609 | -0.06 | 0.94 | -0.64 | 0.36 | -0.51 | 0.49 | 74.22 | 26.37
2019-10-01 | 10:05 | 172.0508 | 172.0508 | -0.06 | 0.94 | -0.66 | 0.34 | -0.54 | 0.46 | 75.2 | 27.34
2019-10-01 | 10:05 | 172.1602 | 172.1602 | -0.05 | 0.95 | -0.66 | 0.34 | -0.53 | 0.47 | 75.2 | 28.32
2019-10-01 | 10:05 | 172.2617 | 172.2617 | -0.05 | 0.95 | -0.66 | 0.34 | -0.52 | 0.48 | 75.2 | 29.3
2019-10-01 | 10:05 | 172.3711 | 172.3711 | -0.04 | 0.96 | -0.65 | 0.35 | -0.53 | 0.47 | 75.2 | 27.34
2019-10-01 | 10:05 | 172.4609 | 172.4609 | -0.03 | 0.97 | -0.66 | 0.34 | -0.53 | 0.47 | 75.2 | 26.37
2019-10-01 | 10:05 | 172.5703 | 172.5703 | -0.04 | 0.96 | -0.66 | 0.34 | -0.54 | 0.46 | 75.2 | 25.39
2019-10-01 | 10:05 | 172.6719 | 172.6719 | -0.04 | 0.96 | -0.65 | 0.35 | -0.53 | 0.47 | 76.17 | 26.37
2019-10-01 | 10:05 | 172.7695 | 172.7695 | -0.02 | 0.98 | -0.66 | 0.34 | -0.54 | 0.46 | 74.22 | 26.37
2019-10-01 | 10:05 | 172.8906 | 172.8906 | -0.04 | 0.96 | -0.65 | 0.35 | -0.54 | 0.46 | 74.22 | 24.41
2019-10-01 | 10:05 | 173 | 173 | -0.03 | 0.97 | -0.65 | 0.35 | -0.55 | 0.45 | 76.17 | 29.3
2019-10-01 | 10:05 | 173.1016 | 173.1016 | -0.11 | 0.89 | -0.58 | 0.42 | -0.52 | 0.48 | 77.15 | 28.32
2019-10-01 | 10:05 | 173.2227 | 173.2227 | -0.15 | 0.85 | -0.56 | 0.44 | -0.51 | 0.49 | 76.17 | 26.37
2019-10-01 | 10:05 | 173.3125 | 173.3125 | -0.18 | 0.82 | -0.55 | 0.45 | -0.51 | 0.49 | 75.2 | 25.39
2019-10-01 | 10:05 | 173.3906 | 173.3906 | -0.17 | 0.83 | -0.54 | 0.46 | -0.5 | 0.5 | 77.15 | 27.34
2019-10-01 | 10:05 | 173.5 | 173.5 | -0.06 | 0.94 | -0.65 | 0.35 | -0.51 | 0.49 | 75.2 | 26.37
2019-10-01 | 10:05 | 173.6016 | 173.6016 | -0.06 | 0.94 | -0.64 | 0.36 | -0.54 | 0.46 | 75.2 | 25.39
2019-10-01 | 10:05 | 173.7227 | 173.7227 | -0.05 | 0.95 | -0.65 | 0.35 | -0.52 | 0.48 | 75.2 | 29.3
2019-10-01 | 10:05 | 173.8125 | 173.8125 | -0.05 | 0.95 | -0.65 | 0.35 | -0.52 | 0.48 | 75.2 | 29.3
2019-10-01 | 10:05 | 173.9023 | 173.9023 | -0.04 | 0.96 | -0.64 | 0.36 | -0.52 | 0.48 | 74.22 | 25.39
2019-10-01 | 10:05 | 174.0195 | 174.0195 | -0.02 | 0.98 | -0.64 | 0.36 | -0.53 | 0.47 | 75.2 | 25.39
2019-10-01 | 10:05 | 174.1094 | 174.1094 | -0.04 | 0.96 | -0.64 | 0.36 | -0.51 | 0.49 | 74.22 | 25.39
2019-10-01 | 10:05 | 174.2305 | 174.2305 | -0.04 | 0.96 | -0.64 | 0.36 | -0.53 | 0.47 | 74.22 | 26.37
2019-10-01 | 10:05 | 174.3398 | 174.3398 | -0.03 | 0.97 | -0.65 | 0.35 | -0.52 | 0.48 | 75.2 | 25.39
2019-10-01 | 10:05 | 174.4414 | 174.4414 | -0.04 | 0.96 | -0.64 | 0.36 | -0.52 | 0.48 | 75.2 | 27.34
2019-10-01 | 10:05 | 174.5195 | 174.5195 | -0.05 | 0.95 | -0.64 | 0.36 | -0.54 | 0.46 | 75.2 | 29.3
2019-10-01 | 10:05 | 174.6211 | 174.6211 | -0.12 | 0.88 | -0.55 | 0.45 | -0.52 | 0.48 | 75.2 | 38.09
2019-10-01 | 10:05 | 174.7305 | 174.7305 | -0.15 | 0.85 | -0.55 | 0.45 | -0.49 | 0.51 | 76.17 | 26.37
2019-10-01 | 10:05 | 174.8594 | 174.8594 | -0.17 | 0.83 | -0.55 | 0.45 | -0.49 | 0.51 | 75.2 | 26.37
2019-10-01 | 10:05 | 174.9609 | 174.9609 | -0.18 | 0.82 | -0.53 | 0.47 | -0.49 | 0.51 | 74.22 | 25.39
2019-10-01 | 10:05 | 175.0625 | 175.0625 | -0.05 | 0.95 | -0.64 | 0.36 | -0.51 | 0.49 | 74.22 | 25.39
2019-10-01 | 10:05 | 175.1523 | 175.1523 | -0.05 | 0.95 | -0.64 | 0.36 | -0.52 | 0.48 | 76.17 | 42.97
2019-10-01 | 10:05 | 175.2617 | 175.2617 | -0.04 | 0.96 | -0.62 | 0.38 | -0.52 | 0.48 | 75.2 | 28.32
2019-10-01 | 10:05 | 175.3594 | 175.3594 | -0.04 | 0.96 | -0.63 | 0.37 | -0.51 | 0.49 | 76.17 | 27.34
2019-10-01 | 10:05 | 175.4727 | 175.4727 | -0.04 | 0.96 | -0.63 | 0.37 | -0.51 | 0.49 | 76.17 | 26.37
2019-10-01 | 10:05 | 175.5625 | 175.5625 | -0.05 | 0.95 | -0.64 | 0.36 | -0.53 | 0.47 | 75.2 | 25.39
2019-10-01 | 10:05 | 175.6523 | 175.6523 | -0.04 | 0.96 | -0.64 | 0.36 | -0.54 | 0.46 | 75.2 | 25.39
2019-10-01 | 10:05 | 175.7617 | 175.7617 | -0.03 | 0.97 | -0.63 | 0.37 | -0.53 | 0.47 | 74.22 | 25.39
2019-10-01 | 10:05 | 175.8594 | 175.8594 | -0.02 | 0.98 | -0.63 | 0.37 | -0.52 | 0.48 | 75.2 | 25.39
2019-10-01 | 10:05 | 175.9609 | 175.9609 | -0.04 | 0.96 | -0.62 | 0.38 | -0.52 | 0.48 | 76.17 | 28.32
2019-10-01 | 10:05 | 176.0625 | 176.0625 | -0.1 | 0.9 | -0.58 | 0.42 | -0.53 | 0.47 | 75.2 | 28.32
2019-10-01 | 10:05 | 176.1602 | 176.1602 | -0.15 | 0.85 | -0.53 | 0.47 | -0.52 | 0.48 | 75.2 | 26.37
2019-10-01 | 10:05 | 176.2695 | 176.2695 | -0.16 | 0.84 | -0.54 | 0.46 | -0.49 | 0.51 | 77.15 | 26.37
2019-10-01 | 10:05 | 176.3828 | 176.3828 | -0.18 | 0.82 | -0.52 | 0.48 | -0.5 | 0.5 | 75.2 | 26.37
2019-10-01 | 10:05 | 176.4922 | 176.4922 | -0.06 | 0.94 | -0.63 | 0.37 | -0.51 | 0.49 | 74.22 | 26.37
2019-10-01 | 10:05 | 176.582 | 176.582 | -0.04 | 0.96 | -0.63 | 0.37 | -0.52 | 0.48 | 75.2 | 26.37
2019-10-01 | 10:05 | 176.6914 | 176.6914 | -0.04 | 0.96 | -0.64 | 0.36 | -0.52 | 0.48 | 75.2 | 28.32
2019-10-01 | 10:05 | 176.793 | 176.793 | -0.04 | 0.96 | -0.63 | 0.37 | -0.52 | 0.48 | 75.2 | 29.3
2019-10-01 | 10:05 | 176.8906 | 176.8906 | -0.04 | 0.96 | -0.63 | 0.37 | -0.52 | 0.48 | 75.2 | 25.39
2019-10-01 | 10:05 | 176.9922 | 176.9922 | -0.03 | 0.97 | -0.64 | 0.36 | -0.51 | 0.49 | 74.22 | 26.37
2019-10-01 | 10:05 | 177.0898 | 177.0898 | -0.03 | 0.97 | -0.63 | 0.37 | -0.53 | 0.47 | 75.2 | 25.39
2019-10-01 | 10:05 | 177.1914 | 177.1914 | -0.02 | 0.98 | -0.64 | 0.36 | -0.53 | 0.47 | 76.17 | 26.37
2019-10-01 | 10:05 | 177.3125 | 177.3125 | -0.04 | 0.96 | -0.64 | 0.36 | -0.52 | 0.48 | 75.2 | 26.37
2019-10-01 | 10:05 | 177.4219 | 177.4219 | -0.03 | 0.97 | -0.63 | 0.37 | -0.52 | 0.48 | 76.17 | 28.32
2019-10-01 | 10:05 | 177.5195 | 177.5195 | -0.02 | 0.98 | -0.62 | 0.38 | -0.53 | 0.47 | 75.2 | 29.3
2019-10-01 | 10:05 | 177.6211 | 177.6211 | -0.12 | 0.88 | -0.56 | 0.44 | -0.51 | 0.49 | 76.17 | 27.34
2019-10-01 | 10:05 | 177.7109 | 177.7109 | -0.14 | 0.86 | -0.55 | 0.45 | -0.49 | 0.51 | 75.2 | 26.37
2019-10-01 | 10:05 | 177.8125 | 177.8125 | -0.16 | 0.84 | -0.53 | 0.47 | -0.49 | 0.51 | 75.2 | 25.39
2019-10-01 | 10:05 | 177.9219 | 177.9219 | -0.15 | 0.85 | -0.53 | 0.47 | -0.48 | 0.52 | 75.2 | 26.37
2019-10-01 | 10:05 | 178.0195 | 178.0195 | -0.06 | 0.94 | -0.62 | 0.38 | -0.5 | 0.5 | 74.22 | 27.34
2019-10-01 | 10:05 | 178.1211 | 178.1211 | -0.05 | 0.95 | -0.62 | 0.38 | -0.5 | 0.5 | 75.2 | 51.76
2019-10-01 | 10:06 | 178.2227 | 178.2227 | -0.05 | 0.95 | -0.64 | 0.36 | -0.52 | 0.48 | 75.2 | 28.32
2019-10-01 | 10:06 | 178.332 | 178.332 | -0.04 | 0.96 | -0.63 | 0.37 | -0.51 | 0.49 | 75.2 | 27.34
2019-10-01 | 10:06 | 178.4492 | 178.4492 | -0.03 | 0.97 | -0.62 | 0.38 | -0.52 | 0.48 | 75.2 | 27.34
2019-10-01 | 10:06 | 178.543 | 178.543 | -0.03 | 0.97 | -0.63 | 0.37 | -0.52 | 0.48 | 75.2 | 25.39
2019-10-01 | 10:06 | 178.6328 | 178.6328 | -0.02 | 0.98 | -0.62 | 0.38 | -0.51 | 0.49 | 74.22 | 25.39
2019-10-01 | 10:06 | 178.7422 | 178.7422 | -0.03 | 0.97 | -0.62 | 0.38 | -0.52 | 0.48 | 75.2 | 26.37
2019-10-01 | 10:06 | 178.8398 | 178.8398 | -0.03 | 0.97 | -0.63 | 0.37 | -0.53 | 0.47 | 75.2 | 25.39
2019-10-01 | 10:06 | 178.9414 | 178.9414 | -0.03 | 0.97 | -0.62 | 0.38 | -0.51 | 0.49 | 75.2 | 29.3
2019-10-01 | 10:06 | 179.043 | 179.043 | -0.07 | 0.93 | -0.59 | 0.41 | -0.51 | 0.49 | 76.17 | 29.3
2019-10-01 | 10:06 | 179.1523 | 179.1523 | -0.14 | 0.86 | -0.52 | 0.48 | -0.49 | 0.51 | 75.2 | 26.37
2019-10-01 | 10:06 | 179.25 | 179.25 | -0.16 | 0.84 | -0.52 | 0.48 | -0.48 | 0.52 | 76.17 | 27.34
2019-10-01 | 10:06 | 179.3711 | 179.3711 | -0.16 | 0.84 | -0.51 | 0.49 | -0.46 | 0.54 | 75.2 | 25.39
2019-10-01 | 10:06 | 179.4727 | 179.4727 | -0.07 | 0.93 | -0.6 | 0.4 | -0.49 | 0.51 | 76.17 | 25.39
2019-10-01 | 10:06 | 179.5703 | 179.5703 | -0.04 | 0.96 | -0.63 | 0.37 | -0.49 | 0.51 | 75.2 | 26.37
2019-10-01 | 10:06 | 179.6797 | 179.6797 | -0.04 | 0.96 | -0.61 | 0.39 | -0.51 | 0.49 | 75.2 | 27.34
2019-10-01 | 10:06 | 179.793 | 179.793 | -0.03 | 0.97 | -0.61 | 0.39 | -0.51 | 0.49 | 75.2 | 29.3
2019-10-01 | 10:06 | 179.8828 | 179.8828 | -0.04 | 0.96 | -0.63 | 0.37 | -0.5 | 0.5 | 76.17 | 49.8
2019-10-01 | 10:06 | 179.9805 | 179.9805 | -0.03 | 0.97 | -0.62 | 0.38 | -0.5 | 0.5 | 77.15 | 26.37
2019-10-01 | 10:06 | 180.082 | 180.082 | -0.03 | 0.97 | -0.62 | 0.38 | -0.51 | 0.49 | 76.17 | 27.34
2019-10-01 | 10:06 | 180.2227 | 180.2227 | -0.04 | 0.96 | -0.61 | 0.39 | -0.51 | 0.49 | 75.2 | 26.37
2019-10-01 | 10:06 | 180.3125 | 180.3125 | -0.03 | 0.97 | -0.61 | 0.39 | -0.5 | 0.5 | 75.2 | 26.37
2019-10-01 | 10:06 | 180.3906 | 180.3906 | -0.02 | 0.98 | -0.61 | 0.39 | -0.52 | 0.48 | 76.17 | 27.34
2019-10-01 | 10:06 | 180.4805 | 180.4805 | -0.01 | 0.99 | -0.61 | 0.39 | -0.52 | 0.48 | 77.15 | 29.3
2019-10-01 | 10:06 | 180.582 | 180.582 | -0.11 | 0.89 | -0.56 | 0.44 | -0.51 | 0.49 | 76.17 | 28.32
2019-10-01 | 10:06 | 180.6914 | 180.6914 | -0.13 | 0.87 | -0.52 | 0.48 | -0.48 | 0.52 | 75.2 | 26.37
2019-10-01 | 10:06 | 180.793 | 180.793 | -0.16 | 0.84 | -0.54 | 0.46 | -0.48 | 0.52 | 75.2 | 26.37
2019-10-01 | 10:06 | 180.9023 | 180.9023 | -0.16 | 0.84 | -0.53 | 0.47 | -0.47 | 0.53 | 75.2 | 26.37
2019-10-01 | 10:06 | 181 | 181 | -0.05 | 0.95 | -0.62 | 0.38 | -0.5 | 0.5 | 75.2 | 26.37
2019-10-01 | 10:06 | 181.1328 | 181.1328 | -0.03 | 0.97 | -0.62 | 0.38 | -0.49 | 0.51 | 75.2 | 26.37
2019-10-01 | 10:06 | 181.1992 | 181.1992 | -0.02 | 0.98 | -0.63 | 0.37 | -0.5 | 0.5 | 75.2 | 28.32
2019-10-01 | 10:06 | 181.332 | 181.332 | -0.04 | 0.96 | -0.62 | 0.38 | -0.5 | 0.5 | 75.2 | 29.3
2019-10-01 | 10:06 | 181.4219 | 181.4219 | -0.03 | 0.97 | -0.6 | 0.4 | -0.51 | 0.49 | 74.22 | 25.39
2019-10-01 | 10:06 | 181.5508 | 181.5508 | -0.03 | 0.97 | -0.62 | 0.38 | -0.5 | 0.5 | 75.2 | 27.34
2019-10-01 | 10:06 | 181.6523 | 181.6523 | -0.02 | 0.98 | -0.61 | 0.39 | -0.5 | 0.5 | 74.22 | 25.39
2019-10-01 | 10:06 | 181.7305 | 181.7305 | -0.03 | 0.97 | -0.61 | 0.39 | -0.51 | 0.49 | 76.17 | 25.39
2019-10-01 | 10:06 | 181.8203 | 181.8203 | -0.02 | 0.98 | -0.61 | 0.39 | -0.5 | 0.5 | 76.17 | 26.37
2019-10-01 | 10:06 | 181.9219 | 181.9219 | -0.01 | 0.99 | -0.59 | 0.41 | -0.49 | 0.51 | 75.2 | 28.32
2019-10-01 | 10:06 | 182.0313 | 182.0313 | -0.04 | 0.96 | -0.59 | 0.41 | -0.51 | 0.49 | 76.17 | 29.3
2019-10-01 | 10:06 | 182.1328 | 182.1328 | -0.12 | 0.88 | -0.53 | 0.47 | -0.5 | 0.5 | 77.15 | 27.34
2019-10-01 | 10:06 | 182.2305 | 182.2305 | -0.14 | 0.86 | -0.53 | 0.47 | -0.46 | 0.54 | 76.17 | 25.39
2019-10-01 | 10:06 | 182.332 | 182.332 | -0.15 | 0.85 | -0.53 | 0.47 | -0.46 | 0.54 | 75.2 | 25.39
2019-10-01 | 10:06 | 182.4414 | 182.4414 | -0.15 | 0.85 | -0.51 | 0.49 | -0.46 | 0.54 | 76.17 | 25.39
2019-10-01 | 10:06 | 182.5313 | 182.5313 | -0.04 | 0.96 | -0.62 | 0.38 | -0.47 | 0.53 | 75.2 | 26.37
2019-10-01 | 10:06 | 182.6406 | 182.6406 | -0.03 | 0.97 | -0.61 | 0.39 | -0.49 | 0.51 | 74.22 | 27.34
2019-10-01 | 10:06 | 182.7422 | 182.7422 | -0.04 | 0.96 | -0.61 | 0.39 | -0.5 | 0.5 | 75.2 | 29.3
2019-10-01 | 10:06 | 182.8516 | 182.8516 | -0.03 | 0.97 | -0.6 | 0.4 | -0.5 | 0.5 | 75.2 | 27.34
2019-10-01 | 10:06 | 182.9609 | 182.9609 | -0.02 | 0.98 | -0.62 | 0.38 | -0.49 | 0.51 | 75.2 | 26.37
2019-10-01 | 10:06 | 183.0625 | 183.0625 | -0.03 | 0.97 | -0.61 | 0.39 | -0.5 | 0.5 | 75.2 | 25.39
2019-10-01 | 10:06 | 183.1602 | 183.1602 | -0.03 | 0.97 | -0.61 | 0.39 | -0.49 | 0.51 | 75.2 | 25.39
2019-10-01 | 10:06 | 183.2695 | 183.2695 | -0.02 | 0.98 | -0.6 | 0.4 | -0.5 | 0.5 | 77.15 | 26.37
2019-10-01 | 10:06 | 183.3711 | 183.3711 | -0.02 | 0.98 | -0.61 | 0.39 | -0.48 | 0.52 | 75.2 | 25.39
2019-10-01 | 10:06 | 183.4609 | 183.4609 | -0.02 | 0.98 | -0.6 | 0.4 | -0.51 | 0.49 | 75.2 | 29.3
2019-10-01 | 10:06 | 183.5625 | 183.5625 | -0.1 | 0.9 | -0.54 | 0.46 | -0.5 | 0.5 | 76.17 | 29.3
2019-10-01 | 10:06 | 183.6719 | 183.6719 | -0.13 | 0.87 | -0.52 | 0.48 | -0.48 | 0.52 | 75.2 | 26.37
2019-10-01 | 10:06 | 183.793 | 183.793 | -0.14 | 0.86 | -0.51 | 0.49 | -0.47 | 0.53 | 77.15 | 25.39
2019-10-01 | 10:06 | 183.8906 | 183.8906 | -0.16 | 0.84 | -0.51 | 0.49 | -0.47 | 0.53 | 76.17 | 25.39
2019-10-01 | 10:06 | 184 | 184 | -0.05 | 0.95 | -0.59 | 0.41 | -0.48 | 0.52 | 76.17 | 27.34
2019-10-01 | 10:06 | 184.0898 | 184.0898 | -0.05 | 0.95 | -0.6 | 0.4 | -0.49 | 0.51 | 75.2 | 25.39
2019-10-01 | 10:06 | 184.1797 | 184.1797 | -0.03 | 0.97 | -0.6 | 0.4 | -0.49 | 0.51 | 77.15 | 28.32
2019-10-01 | 10:06 | 184.293 | 184.293 | -0.03 | 0.97 | -0.59 | 0.41 | -0.49 | 0.51 | 76.17 | 29.3
2019-10-01 | 10:06 | 184.3828 | 184.3828 | -0.03 | 0.97 | -0.61 | 0.39 | -0.48 | 0.52 | 77.15 | 26.37
2019-10-01 | 10:06 | 184.4922 | 184.4922 | -0.01 | 0.99 | -0.59 | 0.41 | -0.5 | 0.5 | 75.2 | 27.34
2019-10-01 | 10:06 | 184.6211 | 184.6211 | -0.02 | 0.98 | -0.61 | 0.39 | -0.49 | 0.51 | 77.15 | 25.39
2019-10-01 | 10:06 | 184.7109 | 184.7109 | -0.02 | 0.98 | -0.6 | 0.4 | -0.48 | 0.52 | 74.22 | 24.41
2019-10-01 | 10:06 | 184.8203 | 184.8203 | -0.02 | 0.98 | -0.61 | 0.39 | -0.49 | 0.51 | 75.2 | 25.39
2019-10-01 | 10:06 | 184.9102 | 184.9102 | -0.02 | 0.98 | -0.61 | 0.39 | -0.49 | 0.51 | 77.15 | 28.32
2019-10-01 | 10:06 | 185.0195 | 185.0195 | -0.03 | 0.97 | -0.58 | 0.42 | -0.49 | 0.51 | 75.2 | 29.3
2019-10-01 | 10:06 | 185.1211 | 185.1211 | -0.1 | 0.9 | -0.52 | 0.48 | -0.5 | 0.5 | 75.2 | 27.34
2019-10-01 | 10:06 | 185.2109 | 185.2109 | -0.14 | 0.86 | -0.51 | 0.49 | -0.46 | 0.54 | 76.17 | 26.37
2019-10-01 | 10:06 | 185.3125 | 185.3125 | -0.15 | 0.85 | -0.52 | 0.48 | -0.46 | 0.54 | 75.2 | 26.37
2019-10-01 | 10:06 | 185.4102 | 185.4102 | -0.15 | 0.85 | -0.51 | 0.49 | -0.46 | 0.54 | 75.2 | 25.39
2019-10-01 | 10:06 | 185.5195 | 185.5195 | -0.04 | 0.96 | -0.6 | 0.4 | -0.48 | 0.52 | 75.2 | 25.39
2019-10-01 | 10:06 | 185.6211 | 185.6211 | -0.04 | 0.96 | -0.59 | 0.41 | -0.48 | 0.52 | 75.2 | 26.37
2019-10-01 | 10:06 | 185.7305 | 185.7305 | -0.04 | 0.96 | -0.59 | 0.41 | -0.49 | 0.51 | 75.2 | 28.32
2019-10-01 | 10:06 | 185.8516 | 185.8516 | -0.06 | 0.94 | -0.6 | 0.4 | -0.48 | 0.52 | 76.17 | 29.3
2019-10-01 | 10:06 | 185.9492 | 185.9492 | -0.08 | 0.92 | -0.58 | 0.42 | -0.48 | 0.52 | 76.17 | 26.37
2019-10-01 | 10:06 | 186.043 | 186.043 | -0.07 | 0.93 | -0.59 | 0.41 | -0.48 | 0.52 | 76.17 | 26.37
2019-10-01 | 10:06 | 186.1523 | 186.1523 | -0.07 | 0.93 | -0.58 | 0.42 | -0.47 | 0.53 | 76.17 | 25.39
2019-10-01 | 10:06 | 186.2617 | 186.2617 | -0.07 | 0.93 | -0.59 | 0.41 | -0.49 | 0.51 | 76.17 | 25.39
2019-10-01 | 10:06 | 186.3711 | 186.3711 | -0.06 | 0.94 | -0.59 | 0.41 | -0.49 | 0.51 | 75.2 | 26.37
2019-10-01 | 10:06 | 186.4492 | 186.4492 | -0.07 | 0.93 | -0.59 | 0.41 | -0.49 | 0.51 | 76.17 | 28.32
2019-10-01 | 10:06 | 186.5508 | 186.5508 | -0.12 | 0.88 | -0.54 | 0.46 | -0.48 | 0.52 | 75.2 | 28.32
2019-10-01 | 10:06 | 186.6523 | 186.6523 | -0.16 | 0.84 | -0.51 | 0.49 | -0.46 | 0.54 | 76.17 | 40.04
2019-10-01 | 10:06 | 186.75 | 186.75 | -0.17 | 0.83 | -0.5 | 0.5 | -0.47 | 0.53 | 76.17 | 27.34
2019-10-01 | 10:06 | 186.8516 | 186.8516 | -0.18 | 0.82 | -0.5 | 0.5 | -0.44 | 0.56 | 75.2 | 24.41
2019-10-01 | 10:06 | 186.9727 | 186.9727 | -0.11 | 0.89 | -0.55 | 0.45 | -0.45 | 0.55 | 75.2 | 26.37
2019-10-01 | 10:06 | 187.0703 | 187.0703 | -0.1 | 0.9 | -0.59 | 0.41 | -0.47 | 0.53 | 75.2 | 25.39
2019-10-01 | 10:06 | 187.1719 | 187.1719 | -0.07 | 0.93 | -0.57 | 0.43 | -0.47 | 0.53 | 75.2 | 26.37
2019-10-01 | 10:06 | 187.2813 | 187.2813 | -0.07 | 0.93 | -0.58 | 0.42 | -0.46 | 0.54 | 76.17 | 29.3
2019-10-01 | 10:06 | 187.3828 | 187.3828 | -0.07 | 0.93 | -0.58 | 0.42 | -0.48 | 0.52 | 76.17 | 27.34
2019-10-01 | 10:06 | 187.4805 | 187.4805 | -0.07 | 0.93 | -0.58 | 0.42 | -0.46 | 0.54 | 75.2 | 26.37
2019-10-01 | 10:06 | 187.582 | 187.582 | -0.08 | 0.92 | -0.58 | 0.42 | -0.48 | 0.52 | 76.17 | 24.41
2019-10-01 | 10:06 | 187.6797 | 187.6797 | -0.07 | 0.93 | -0.58 | 0.42 | -0.47 | 0.53 | 75.2 | 25.39
2019-10-01 | 10:06 | 187.8125 | 187.8125 | -0.07 | 0.93 | -0.57 | 0.43 | -0.49 | 0.51 | 76.17 | 26.37
2019-10-01 | 10:06 | 187.9023 | 187.9023 | -0.06 | 0.94 | -0.58 | 0.42 | -0.48 | 0.52 | 77.15 | 25.39
2019-10-01 | 10:06 | 188 | 188 | -0.07 | 0.93 | -0.57 | 0.43 | -0.47 | 0.53 | 75.2 | 28.32
2019-10-01 | 10:06 | 188.1016 | 188.1016 | -0.14 | 0.86 | -0.51 | 0.49 | -0.48 | 0.52 | 75.2 | 29.3
2019-10-01 | 10:06 | 188.1992 | 188.1992 | -0.17 | 0.83 | -0.49 | 0.51 | -0.44 | 0.56 | 77.15 | 26.37
2019-10-01 | 10:06 | 188.3125 | 188.3125 | -0.17 | 0.83 | -0.5 | 0.5 | -0.44 | 0.56 | 76.17 | 25.39
2019-10-01 | 10:06 | 188.4219 | 188.4219 | -0.17 | 0.83 | -0.49 | 0.51 | -0.45 | 0.55 | 75.2 | 25.39
2019-10-01 | 10:06 | 188.5 | 188.5 | -0.09 | 0.91 | -0.58 | 0.42 | -0.46 | 0.54 | 75.2 | 25.39
2019-10-01 | 10:06 | 188.6016 | 188.6016 | -0.09 | 0.91 | -0.58 | 0.42 | -0.47 | 0.53 | 74.22 | 24.41
2019-10-01 | 10:06 | 188.6914 | 188.6914 | -0.08 | 0.92 | -0.59 | 0.41 | -0.46 | 0.54 | 75.2 | 28.32
2019-10-01 | 10:06 | 188.8125 | 188.8125 | -0.07 | 0.93 | -0.57 | 0.43 | -0.47 | 0.53 | 76.17 | 28.32
2019-10-01 | 10:06 | 188.9297 | 188.9297 | -0.08 | 0.92 | -0.58 | 0.42 | -0.47 | 0.53 | 76.17 | 50.78
2019-10-01 | 10:06 | 189.0195 | 189.0195 | -0.08 | 0.92 | -0.58 | 0.42 | -0.46 | 0.54 | 74.22 | 26.37
2019-10-01 | 10:06 | 189.1094 | 189.1094 | -0.07 | 0.93 | -0.59 | 0.41 | -0.46 | 0.54 | 75.2 | 24.41
2019-10-01 | 10:06 | 189.2109 | 189.2109 | -0.07 | 0.93 | -0.58 | 0.42 | -0.48 | 0.52 | 75.2 | 25.39
2019-10-01 | 10:06 | 189.3203 | 189.3203 | -0.07 | 0.93 | -0.57 | 0.43 | -0.48 | 0.52 | 74.22 | 25.39
2019-10-01 | 10:06 | 189.4297 | 189.4297 | -0.06 | 0.94 | -0.58 | 0.42 | -0.49 | 0.51 | 76.17 | 42.97
2019-10-01 | 10:06 | 189.5313 | 189.5313 | -0.09 | 0.91 | -0.57 | 0.43 | -0.48 | 0.52 | 75.2 | 28.32
2019-10-01 | 10:06 | 189.6328 | 189.6328 | -0.14 | 0.86 | -0.5 | 0.5 | -0.46 | 0.54 | 75.2 | 27.34
2019-10-01 | 10:06 | 189.7305 | 189.7305 | -0.18 | 0.82 | -0.49 | 0.51 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:06 | 189.832 | 189.832 | -0.18 | 0.82 | -0.5 | 0.5 | -0.44 | 0.56 | 74.22 | 24.41
2019-10-01 | 10:06 | 189.9414 | 189.9414 | -0.17 | 0.83 | -0.49 | 0.51 | -0.43 | 0.57 | 75.2 | 26.37
2019-10-01 | 10:06 | 190.043 | 190.043 | -0.1 | 0.9 | -0.59 | 0.41 | -0.47 | 0.53 | 74.22 | 24.41
2019-10-01 | 10:06 | 190.1406 | 190.1406 | -0.08 | 0.92 | -0.57 | 0.43 | -0.46 | 0.54 | 76.17 | 25.39
2019-10-01 | 10:06 | 190.2422 | 190.2422 | -0.08 | 0.92 | -0.58 | 0.42 | -0.46 | 0.54 | 75.2 | 28.32
2019-10-01 | 10:06 | 190.3398 | 190.3398 | -0.07 | 0.93 | -0.57 | 0.43 | -0.46 | 0.54 | 76.17 | 28.32
2019-10-01 | 10:06 | 190.4492 | 190.4492 | -0.07 | 0.93 | -0.57 | 0.43 | -0.45 | 0.55 | 75.2 | 25.39
2019-10-01 | 10:06 | 190.5508 | 190.5508 | -0.07 | 0.93 | -0.58 | 0.42 | -0.47 | 0.53 | 74.22 | 25.39
2019-10-01 | 10:06 | 190.6719 | 190.6719 | -0.07 | 0.93 | -0.57 | 0.43 | -0.47 | 0.53 | 74.22 | 24.41
2019-10-01 | 10:06 | 190.7695 | 190.7695 | -0.06 | 0.94 | -0.58 | 0.42 | -0.46 | 0.54 | 76.17 | 25.39
2019-10-01 | 10:06 | 190.8906 | 190.8906 | -0.06 | 0.94 | -0.58 | 0.42 | -0.48 | 0.52 | 75.2 | 24.41
2019-10-01 | 10:06 | 191.0195 | 191.0195 | -0.06 | 0.94 | -0.58 | 0.42 | -0.46 | 0.54 | 75.2 | 27.34
2019-10-01 | 10:06 | 191.1211 | 191.1211 | -0.12 | 0.88 | -0.53 | 0.47 | -0.47 | 0.53 | 75.2 | 29.3
2019-10-01 | 10:06 | 191.1992 | 191.1992 | -0.16 | 0.84 | -0.51 | 0.49 | -0.44 | 0.56 | 75.2 | 51.76
2019-10-01 | 10:06 | 191.293 | 191.293 | -0.17 | 0.83 | -0.52 | 0.48 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:06 | 191.4023 | 191.4023 | -0.18 | 0.82 | -0.52 | 0.48 | -0.44 | 0.56 | 76.17 | 24.41
2019-10-01 | 10:06 | 191.5117 | 191.5117 | -0.09 | 0.91 | -0.59 | 0.41 | -0.45 | 0.55 | 74.22 | 25.39
2019-10-01 | 10:06 | 191.6211 | 191.6211 | -0.08 | 0.92 | -0.58 | 0.42 | -0.45 | 0.55 | 74.22 | 25.39
2019-10-01 | 10:06 | 191.6914 | 191.6914 | -0.06 | 0.94 | -0.59 | 0.41 | -0.47 | 0.53 | 75.2 | 31.25
2019-10-01 | 10:06 | 191.7813 | 191.7813 | -0.07 | 0.93 | -0.57 | 0.43 | -0.46 | 0.54 | 75.2 | 29.3
2019-10-01 | 10:06 | 191.9219 | 191.9219 | -0.06 | 0.94 | -0.59 | 0.41 | -0.47 | 0.53 | 75.2 | 26.37
2019-10-01 | 10:06 | 191.9922 | 191.9922 | -0.05 | 0.95 | -0.57 | 0.43 | -0.45 | 0.55 | 75.2 | 26.37
2019-10-01 | 10:06 | 192.1094 | 192.1094 | -0.04 | 0.96 | -0.58 | 0.42 | -0.44 | 0.56 | 76.17 | 26.37
2019-10-01 | 10:06 | 192.2227 | 192.2227 | -0.04 | 0.96 | -0.58 | 0.42 | -0.45 | 0.55 | 76.17 | 25.39
2019-10-01 | 10:06 | 192.3203 | 192.3203 | -0.05 | 0.95 | -0.57 | 0.43 | -0.46 | 0.54 | 75.2 | 25.39
2019-10-01 | 10:06 | 192.4102 | 192.4102 | -0.05 | 0.95 | -0.58 | 0.42 | -0.47 | 0.53 | 75.2 | 25.39
2019-10-01 | 10:06 | 192.5195 | 192.5195 | -0.04 | 0.96 | -0.58 | 0.42 | -0.46 | 0.54 | 75.2 | 28.32
2019-10-01 | 10:06 | 192.6211 | 192.6211 | -0.14 | 0.86 | -0.5 | 0.5 | -0.47 | 0.53 | 75.2 | 28.32
2019-10-01 | 10:06 | 192.7109 | 192.7109 | -0.15 | 0.85 | -0.51 | 0.49 | -0.45 | 0.55 | 75.2 | 25.39
2019-10-01 | 10:06 | 192.832 | 192.832 | -0.16 | 0.84 | -0.51 | 0.49 | -0.45 | 0.55 | 74.22 | 25.39
2019-10-01 | 10:06 | 192.9219 | 192.9219 | -0.16 | 0.84 | -0.51 | 0.49 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:06 | 193.043 | 193.043 | -0.07 | 0.93 | -0.6 | 0.4 | -0.45 | 0.55 | 75.2 | 25.39
2019-10-01 | 10:06 | 193.1523 | 193.1523 | -0.07 | 0.93 | -0.59 | 0.41 | -0.46 | 0.54 | 76.17 | 24.41
2019-10-01 | 10:06 | 193.2227 | 193.2227 | -0.08 | 0.92 | -0.58 | 0.42 | -0.45 | 0.55 | 76.17 | 28.32
2019-10-01 | 10:06 | 193.332 | 193.332 | -0.06 | 0.94 | -0.58 | 0.42 | -0.45 | 0.55 | 77.15 | 29.3
2019-10-01 | 10:06 | 193.4492 | 193.4492 | -0.05 | 0.95 | -0.59 | 0.41 | -0.46 | 0.54 | 75.2 | 25.39
2019-10-01 | 10:06 | 193.5703 | 193.5703 | -0.05 | 0.95 | -0.57 | 0.43 | -0.45 | 0.55 | 75.2 | 27.34
2019-10-01 | 10:06 | 193.6602 | 193.6602 | -0.06 | 0.94 | -0.57 | 0.43 | -0.46 | 0.54 | 74.22 | 24.41
2019-10-01 | 10:06 | 193.7617 | 193.7617 | -0.05 | 0.95 | -0.57 | 0.43 | -0.47 | 0.53 | 75.2 | 26.37
2019-10-01 | 10:06 | 193.8516 | 193.8516 | -0.05 | 0.95 | -0.58 | 0.42 | -0.45 | 0.55 | 76.17 | 27.34
2019-10-01 | 10:06 | 193.9414 | 193.9414 | -0.04 | 0.96 | -0.58 | 0.42 | -0.47 | 0.53 | 76.17 | 27.34
2019-10-01 | 10:06 | 194.043 | 194.043 | -0.1 | 0.9 | -0.52 | 0.48 | -0.45 | 0.55 | 76.17 | 29.3
2019-10-01 | 10:06 | 194.1523 | 194.1523 | -0.14 | 0.86 | -0.49 | 0.51 | -0.45 | 0.55 | 78.12 | 35.16
2019-10-01 | 10:06 | 194.25 | 194.25 | -0.15 | 0.85 | -0.5 | 0.5 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:06 | 194.3594 | 194.3594 | -0.16 | 0.84 | -0.5 | 0.5 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:06 | 194.4727 | 194.4727 | -0.14 | 0.86 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 194.5625 | 194.5625 | -0.06 | 0.94 | -0.6 | 0.4 | -0.46 | 0.54 | 76.17 | 24.41
2019-10-01 | 10:06 | 194.6602 | 194.6602 | -0.07 | 0.93 | -0.58 | 0.42 | -0.45 | 0.55 | 75.2 | 33.2
2019-10-01 | 10:06 | 194.7617 | 194.7617 | -0.04 | 0.96 | -0.58 | 0.42 | -0.45 | 0.55 | 75.2 | 29.3
2019-10-01 | 10:06 | 194.8711 | 194.8711 | -0.04 | 0.96 | -0.58 | 0.42 | -0.46 | 0.54 | 76.17 | 26.37
2019-10-01 | 10:06 | 194.9727 | 194.9727 | -0.05 | 0.95 | -0.57 | 0.43 | -0.45 | 0.55 | 75.2 | 25.39
2019-10-01 | 10:06 | 195.082 | 195.082 | -0.06 | 0.94 | -0.58 | 0.42 | -0.44 | 0.56 | 74.22 | 24.41
2019-10-01 | 10:06 | 195.1797 | 195.1797 | -0.05 | 0.95 | -0.57 | 0.43 | -0.45 | 0.55 | 75.2 | 24.41
2019-10-01 | 10:06 | 195.2813 | 195.2813 | -0.04 | 0.96 | -0.56 | 0.44 | -0.46 | 0.54 | 75.2 | 24.41
2019-10-01 | 10:06 | 195.4023 | 195.4023 | -0.04 | 0.96 | -0.57 | 0.43 | -0.44 | 0.56 | 75.2 | 26.37
2019-10-01 | 10:06 | 195.5117 | 195.5117 | -0.04 | 0.96 | -0.57 | 0.43 | -0.46 | 0.54 | 75.2 | 29.3
2019-10-01 | 10:06 | 195.6094 | 195.6094 | -0.12 | 0.88 | -0.51 | 0.49 | -0.44 | 0.56 | 76.17 | 28.32
2019-10-01 | 10:06 | 195.7109 | 195.7109 | -0.15 | 0.85 | -0.49 | 0.51 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:06 | 195.8008 | 195.8008 | -0.15 | 0.85 | -0.51 | 0.49 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:06 | 195.9023 | 195.9023 | -0.16 | 0.84 | -0.51 | 0.49 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:06 | 196.0195 | 196.0195 | -0.07 | 0.93 | -0.58 | 0.42 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:06 | 196.1094 | 196.1094 | -0.06 | 0.94 | -0.59 | 0.41 | -0.44 | 0.56 | 75.2 | 26.37
2019-10-01 | 10:06 | 196.2227 | 196.2227 | -0.05 | 0.95 | -0.56 | 0.44 | -0.44 | 0.56 | 77.15 | 28.32
2019-10-01 | 10:06 | 196.3125 | 196.3125 | -0.05 | 0.95 | -0.56 | 0.44 | -0.43 | 0.57 | 76.17 | 29.3
2019-10-01 | 10:06 | 196.4102 | 196.4102 | -0.04 | 0.96 | -0.57 | 0.43 | -0.44 | 0.56 | 76.17 | 26.37
2019-10-01 | 10:06 | 196.5195 | 196.5195 | -0.04 | 0.96 | -0.57 | 0.43 | -0.45 | 0.55 | 77.15 | 26.37
2019-10-01 | 10:06 | 196.6328 | 196.6328 | -0.04 | 0.96 | -0.57 | 0.43 | -0.44 | 0.56 | 75.2 | 24.41
2019-10-01 | 10:06 | 196.7227 | 196.7227 | -0.04 | 0.96 | -0.57 | 0.43 | -0.45 | 0.55 | 76.17 | 24.41
2019-10-01 | 10:06 | 196.832 | 196.832 | -0.04 | 0.96 | -0.56 | 0.44 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:06 | 196.9492 | 196.9492 | -0.04 | 0.96 | -0.56 | 0.44 | -0.44 | 0.56 | 75.2 | 28.32
2019-10-01 | 10:06 | 197.0313 | 197.0313 | -0.05 | 0.95 | -0.54 | 0.46 | -0.45 | 0.55 | 75.2 | 29.3
2019-10-01 | 10:06 | 197.1406 | 197.1406 | -0.13 | 0.87 | -0.5 | 0.5 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 197.2305 | 197.2305 | -0.15 | 0.85 | -0.48 | 0.52 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:06 | 197.3398 | 197.3398 | -0.15 | 0.85 | -0.48 | 0.52 | -0.42 | 0.58 | 76.17 | 25.39
2019-10-01 | 10:06 | 197.4492 | 197.4492 | -0.16 | 0.84 | -0.51 | 0.49 | -0.41 | 0.59 | 76.17 | 27.34
2019-10-01 | 10:06 | 197.5508 | 197.5508 | -0.06 | 0.94 | -0.58 | 0.42 | -0.44 | 0.56 | 76.17 | 26.37
2019-10-01 | 10:06 | 197.6406 | 197.6406 | -0.05 | 0.95 | -0.57 | 0.43 | -0.45 | 0.55 | 76.17 | 27.34
2019-10-01 | 10:06 | 197.7422 | 197.7422 | -0.04 | 0.96 | -0.57 | 0.43 | -0.44 | 0.56 | 77.15 | 28.32
2019-10-01 | 10:06 | 197.8516 | 197.8516 | -0.05 | 0.95 | -0.56 | 0.44 | -0.45 | 0.55 | 75.2 | 48.83
2019-10-01 | 10:06 | 197.9492 | 197.9492 | -0.04 | 0.96 | -0.56 | 0.44 | -0.43 | 0.57 | 77.15 | 27.34
2019-10-01 | 10:06 | 198.0508 | 198.0508 | -0.04 | 0.96 | -0.56 | 0.44 | -0.46 | 0.54 | 76.17 | 24.41
2019-10-01 | 10:06 | 198.1602 | 198.1602 | -0.04 | 0.96 | -0.56 | 0.44 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:06 | 198.2617 | 198.2617 | -0.04 | 0.96 | -0.57 | 0.43 | -0.45 | 0.55 | 76.17 | 27.34
2019-10-01 | 10:06 | 198.3594 | 198.3594 | -0.03 | 0.97 | -0.57 | 0.43 | -0.46 | 0.54 | 76.17 | 27.34
2019-10-01 | 10:06 | 198.4609 | 198.4609 | -0.04 | 0.96 | -0.55 | 0.45 | -0.45 | 0.55 | 75.2 | 28.32
2019-10-01 | 10:06 | 198.5703 | 198.5703 | -0.09 | 0.91 | -0.5 | 0.5 | -0.44 | 0.56 | 75.2 | 27.34
2019-10-01 | 10:06 | 198.6719 | 198.6719 | -0.14 | 0.86 | -0.49 | 0.51 | -0.43 | 0.57 | 75.2 | 26.37
2019-10-01 | 10:06 | 198.7695 | 198.7695 | -0.14 | 0.86 | -0.5 | 0.5 | -0.41 | 0.59 | 74.22 | 24.41
2019-10-01 | 10:06 | 198.8828 | 198.8828 | -0.15 | 0.85 | -0.5 | 0.5 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 199 | 199 | -0.08 | 0.92 | -0.58 | 0.42 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:06 | 199.1016 | 199.1016 | -0.06 | 0.94 | -0.59 | 0.41 | -0.43 | 0.57 | 75.2 | 51.76
2019-10-01 | 10:06 | 199.1914 | 199.1914 | -0.06 | 0.94 | -0.56 | 0.44 | -0.44 | 0.56 | 76.17 | 28.32
2019-10-01 | 10:06 | 199.293 | 199.293 | -0.04 | 0.96 | -0.57 | 0.43 | -0.44 | 0.56 | 75.2 | 27.34
2019-10-01 | 10:06 | 199.3906 | 199.3906 | -0.05 | 0.95 | -0.58 | 0.42 | -0.45 | 0.55 | 76.17 | 26.37
2019-10-01 | 10:06 | 199.5117 | 199.5117 | -0.04 | 0.96 | -0.56 | 0.44 | -0.46 | 0.54 | 75.2 | 25.39
2019-10-01 | 10:06 | 199.6016 | 199.6016 | -0.05 | 0.95 | -0.56 | 0.44 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:06 | 199.7227 | 199.7227 | -0.03 | 0.97 | -0.57 | 0.43 | -0.45 | 0.55 | 75.2 | 24.41
2019-10-01 | 10:06 | 199.8398 | 199.8398 | -0.04 | 0.96 | -0.56 | 0.44 | -0.45 | 0.55 | 75.2 | 25.39
2019-10-01 | 10:06 | 199.9219 | 199.9219 | -0.02 | 0.98 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 29.3
2019-10-01 | 10:06 | 200.0117 | 200.0117 | -0.04 | 0.96 | -0.55 | 0.45 | -0.45 | 0.55 | 76.17 | 28.32
2019-10-01 | 10:06 | 200.1016 | 200.1016 | -0.12 | 0.88 | -0.49 | 0.51 | -0.44 | 0.56 | 77.15 | 27.34
2019-10-01 | 10:06 | 200.2109 | 200.2109 | -0.14 | 0.86 | -0.5 | 0.5 | -0.43 | 0.57 | 76.17 | 26.37
2019-10-01 | 10:06 | 200.3125 | 200.3125 | -0.13 | 0.87 | -0.51 | 0.49 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:06 | 200.4219 | 200.4219 | -0.15 | 0.85 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:06 | 200.5195 | 200.5195 | -0.06 | 0.94 | -0.61 | 0.39 | -0.42 | 0.58 | 74.22 | 24.41
2019-10-01 | 10:06 | 200.6211 | 200.6211 | -0.05 | 0.95 | -0.59 | 0.41 | -0.44 | 0.56 | 75.2 | 28.32
2019-10-01 | 10:06 | 200.7227 | 200.7227 | -0.05 | 0.95 | -0.58 | 0.42 | -0.43 | 0.57 | 75.2 | 28.32
2019-10-01 | 10:06 | 200.832 | 200.832 | -0.04 | 0.96 | -0.58 | 0.42 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:06 | 200.9297 | 200.9297 | -0.04 | 0.96 | -0.56 | 0.44 | -0.45 | 0.55 | 76.17 | 26.37
2019-10-01 | 10:06 | 201.0508 | 201.0508 | -0.03 | 0.97 | -0.57 | 0.43 | -0.43 | 0.57 | 75.2 | 24.41
2019-10-01 | 10:06 | 201.1602 | 201.1602 | -0.03 | 0.97 | -0.58 | 0.42 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:06 | 201.25 | 201.25 | -0.03 | 0.97 | -0.56 | 0.44 | -0.44 | 0.56 | 76.17 | 24.41
2019-10-01 | 10:06 | 201.3711 | 201.3711 | -0.03 | 0.97 | -0.56 | 0.44 | -0.42 | 0.58 | 75.2 | 28.32
2019-10-01 | 10:06 | 201.4609 | 201.4609 | -0.03 | 0.97 | -0.55 | 0.45 | -0.42 | 0.58 | 75.2 | 28.32
2019-10-01 | 10:06 | 201.5625 | 201.5625 | -0.07 | 0.93 | -0.52 | 0.48 | -0.45 | 0.55 | 76.17 | 26.37
2019-10-01 | 10:06 | 201.6406 | 201.6406 | -0.13 | 0.87 | -0.49 | 0.51 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:06 | 201.7695 | 201.7695 | -0.14 | 0.86 | -0.5 | 0.5 | -0.4 | 0.6 | 75.2 | 25.39
2019-10-01 | 10:06 | 201.8906 | 201.8906 | -0.15 | 0.85 | -0.51 | 0.49 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:06 | 201.9922 | 201.9922 | -0.15 | 0.85 | -0.53 | 0.47 | -0.39 | 0.61 | 75.2 | 26.37
2019-10-01 | 10:06 | 202.082 | 202.082 | -0.05 | 0.95 | -0.59 | 0.41 | -0.42 | 0.58 | 75.2 | 27.34
2019-10-01 | 10:06 | 202.1719 | 202.1719 | -0.04 | 0.96 | -0.57 | 0.43 | -0.42 | 0.58 | 76.17 | 29.3
2019-10-01 | 10:06 | 202.2695 | 202.2695 | -0.04 | 0.96 | -0.56 | 0.44 | -0.42 | 0.58 | 76.17 | 6.84
2019-10-01 | 10:06 | 202.3828 | 202.3828 | -0.03 | 0.97 | -0.57 | 0.43 | -0.44 | 0.56 | 76.17 | 26.37
2019-10-01 | 10:06 | 202.4922 | 202.4922 | -0.04 | 0.96 | -0.56 | 0.44 | -0.44 | 0.56 | 75.2 | 24.41
2019-10-01 | 10:06 | 202.5898 | 202.5898 | -0.01 | 0.99 | -0.56 | 0.44 | -0.43 | 0.57 | 75.2 | 24.41
2019-10-01 | 10:06 | 202.6914 | 202.6914 | -0.03 | 0.97 | -0.55 | 0.45 | -0.42 | 0.58 | 76.17 | 24.41
2019-10-01 | 10:06 | 202.793 | 202.793 | -0.03 | 0.97 | -0.55 | 0.45 | -0.41 | 0.59 | 75.2 | 26.37
2019-10-01 | 10:06 | 202.8828 | 202.8828 | -0.03 | 0.97 | -0.56 | 0.44 | -0.43 | 0.57 | 75.2 | 29.3
2019-10-01 | 10:06 | 202.9922 | 202.9922 | -0.03 | 0.97 | -0.55 | 0.45 | -0.43 | 0.57 | 76.17 | 42.97
2019-10-01 | 10:06 | 203.0898 | 203.0898 | -0.11 | 0.89 | -0.5 | 0.5 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:06 | 203.1914 | 203.1914 | -0.13 | 0.87 | -0.48 | 0.52 | -0.39 | 0.61 | 75.2 | 24.41
2019-10-01 | 10:06 | 203.3125 | 203.3125 | -0.14 | 0.86 | -0.49 | 0.51 | -0.42 | 0.58 | 75.2 | 27.34
2019-10-01 | 10:06 | 203.4102 | 203.4102 | -0.14 | 0.86 | -0.46 | 0.54 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:06 | 203.5117 | 203.5117 | -0.05 | 0.95 | -0.55 | 0.45 | -0.39 | 0.61 | 76.17 | 27.34
2019-10-01 | 10:06 | 203.6094 | 203.6094 | -0.05 | 0.95 | -0.53 | 0.47 | -0.43 | 0.57 | 76.17 | 28.32
2019-10-01 | 10:06 | 203.7109 | 203.7109 | -0.04 | 0.96 | -0.53 | 0.47 | -0.4 | 0.6 | 76.17 | 27.34
2019-10-01 | 10:06 | 203.832 | 203.832 | -0.04 | 0.96 | -0.54 | 0.46 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 203.9414 | 203.9414 | -0.03 | 0.97 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 25.39
2019-10-01 | 10:06 | 204.0508 | 204.0508 | -0.04 | 0.96 | -0.54 | 0.46 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:06 | 204.1406 | 204.1406 | -0.03 | 0.97 | -0.54 | 0.46 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:06 | 204.2422 | 204.2422 | -0.02 | 0.98 | -0.54 | 0.46 | -0.44 | 0.56 | 77.15 | 50.78
2019-10-01 | 10:06 | 204.3398 | 204.3398 | -0.01 | 0.99 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 29.3
2019-10-01 | 10:06 | 204.4297 | 204.4297 | -0.04 | 0.96 | -0.53 | 0.47 | -0.43 | 0.57 | 75.2 | 27.34
2019-10-01 | 10:06 | 204.543 | 204.543 | -0.04 | 0.96 | -0.52 | 0.48 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:06 | 204.6328 | 204.6328 | -0.11 | 0.89 | -0.45 | 0.55 | -0.43 | 0.57 | 75.2 | 26.37
2019-10-01 | 10:06 | 204.7305 | 204.7305 | -0.13 | 0.87 | -0.46 | 0.54 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:06 | 204.832 | 204.832 | -0.13 | 0.87 | -0.46 | 0.54 | -0.4 | 0.6 | 77.15 | 26.37
2019-10-01 | 10:06 | 204.9297 | 204.9297 | -0.15 | 0.85 | -0.46 | 0.54 | -0.39 | 0.61 | 76.17 | 24.41
2019-10-01 | 10:06 | 205.0703 | 205.0703 | -0.06 | 0.94 | -0.54 | 0.46 | -0.41 | 0.59 | 76.17 | 29.3
2019-10-01 | 10:06 | 205.1719 | 205.1719 | -0.05 | 0.95 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 28.32
2019-10-01 | 10:06 | 205.2695 | 205.2695 | -0.04 | 0.96 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 205.3594 | 205.3594 | -0.04 | 0.96 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 24.41
2019-10-01 | 10:06 | 205.4727 | 205.4727 | -0.02 | 0.98 | -0.55 | 0.45 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 205.5625 | 205.5625 | -0.03 | 0.97 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:06 | 205.6523 | 205.6523 | -0.03 | 0.97 | -0.54 | 0.46 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 205.7695 | 205.7695 | -0.03 | 0.97 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 28.32
2019-10-01 | 10:06 | 205.8906 | 205.8906 | -0.03 | 0.97 | -0.54 | 0.46 | -0.41 | 0.59 | 76.17 | 28.32
2019-10-01 | 10:06 | 205.9727 | 205.9727 | -0.01 | 0.99 | -0.52 | 0.48 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:06 | 206.082 | 206.082 | -0.1 | 0.9 | -0.48 | 0.52 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:06 | 206.1719 | 206.1719 | -0.11 | 0.89 | -0.44 | 0.56 | -0.39 | 0.61 | 76.17 | 27.34
2019-10-01 | 10:06 | 206.2813 | 206.2813 | -0.14 | 0.86 | -0.45 | 0.55 | -0.39 | 0.61 | 76.17 | 26.37
2019-10-01 | 10:06 | 206.3828 | 206.3828 | -0.13 | 0.87 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 206.4805 | 206.4805 | -0.06 | 0.94 | -0.52 | 0.48 | -0.4 | 0.6 | 76.17 | 29.3
2019-10-01 | 10:06 | 206.582 | 206.582 | -0.03 | 0.97 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 28.32
2019-10-01 | 10:06 | 206.6797 | 206.6797 | -0.04 | 0.96 | -0.53 | 0.47 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:06 | 206.793 | 206.793 | -0.02 | 0.98 | -0.54 | 0.46 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:06 | 206.8906 | 206.8906 | -0.02 | 0.98 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 24.41
2019-10-01 | 10:06 | 206.9805 | 206.9805 | -0.02 | 0.98 | -0.52 | 0.48 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:06 | 207.1016 | 207.1016 | -0.01 | 0.99 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 207.1992 | 207.1992 | -0.02 | 0.98 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 27.34
2019-10-01 | 10:06 | 207.3203 | 207.3203 | -0.02 | 0.98 | -0.52 | 0.48 | -0.42 | 0.58 | 75.2 | 29.3
2019-10-01 | 10:06 | 207.4414 | 207.4414 | -0.02 | 0.98 | -0.52 | 0.48 | -0.42 | 0.58 | 75.2 | 41.02
2019-10-01 | 10:06 | 207.543 | 207.543 | -0.03 | 0.97 | -0.52 | 0.48 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:06 | 207.6211 | 207.6211 | -0.1 | 0.9 | -0.45 | 0.55 | -0.41 | 0.59 | 75.2 | 24.41
2019-10-01 | 10:06 | 207.7109 | 207.7109 | -0.12 | 0.88 | -0.44 | 0.56 | -0.39 | 0.61 | 76.17 | 24.41
2019-10-01 | 10:06 | 207.8203 | 207.8203 | -0.14 | 0.86 | -0.44 | 0.56 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:06 | 207.9102 | 207.9102 | -0.12 | 0.88 | -0.44 | 0.56 | -0.38 | 0.62 | 75.2 | 27.34
2019-10-01 | 10:06 | 208.0313 | 208.0313 | -0.04 | 0.96 | -0.51 | 0.49 | -0.4 | 0.6 | 76.17 | 29.3
2019-10-01 | 10:06 | 208.1406 | 208.1406 | -0.03 | 0.97 | -0.5 | 0.5 | -0.41 | 0.59 | 77.15 | 28.32
2019-10-01 | 10:06 | 208.2227 | 208.2227 | -0.02 | 0.98 | -0.5 | 0.5 | -0.4 | 0.6 | 77.15 | 26.37
2019-10-01 | 10:06 | 208.332 | 208.332 | -0.02 | 0.98 | -0.51 | 0.49 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:06 | 208.4297 | 208.4297 | -0.02 | 0.98 | -0.51 | 0.49 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:06 | 208.543 | 208.543 | -0.01 | 0.99 | -0.51 | 0.49 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:06 | 208.6523 | 208.6523 | -0.02 | 0.98 | -0.51 | 0.49 | -0.42 | 0.58 | 77.15 | 40.04
2019-10-01 | 10:06 | 208.7617 | 208.7617 | -0.01 | 0.99 | -0.5 | 0.5 | -0.41 | 0.59 | 78.12 | 28.32
2019-10-01 | 10:06 | 208.8594 | 208.8594 | -0.01 | 0.99 | -0.51 | 0.49 | -0.42 | 0.58 | 76.17 | 27.34
2019-10-01 | 10:06 | 208.9492 | 208.9492 | -0.02 | 0.98 | -0.5 | 0.5 | -0.4 | 0.6 | 76.17 | 25.39
2019-10-01 | 10:06 | 209.0703 | 209.0703 | -0.07 | 0.93 | -0.46 | 0.54 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:06 | 209.1602 | 209.1602 | -0.11 | 0.89 | -0.44 | 0.56 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:06 | 209.25 | 209.25 | -0.12 | 0.88 | -0.42 | 0.58 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:06 | 209.3594 | 209.3594 | -0.13 | 0.87 | -0.42 | 0.58 | -0.38 | 0.62 | 76.17 | 24.41
2019-10-01 | 10:06 | 209.4805 | 209.4805 | -0.14 | 0.86 | -0.41 | 0.59 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:06 | 209.582 | 209.582 | -0.03 | 0.97 | -0.49 | 0.51 | -0.4 | 0.6 | 77.15 | 28.32
2019-10-01 | 10:06 | 209.6914 | 209.6914 | -0.03 | 0.97 | -0.49 | 0.51 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:06 | 209.793 | 209.793 | -0.03 | 0.97 | -0.48 | 0.52 | -0.38 | 0.62 | 76.17 | 26.37
2019-10-01 | 10:06 | 209.8828 | 209.8828 | -0.01 | 0.99 | -0.49 | 0.51 | -0.41 | 0.59 | 76.17 | 26.37
2019-10-01 | 10:06 | 209.9805 | 209.9805 | -0.02 | 0.98 | -0.48 | 0.52 | -0.4 | 0.6 | 76.17 | 26.37
2019-10-01 | 10:06 | 210.082 | 210.082 | -0.02 | 0.98 | -0.5 | 0.5 | -0.4 | 0.6 | 76.17 | 26.37
2019-10-01 | 10:06 | 210.1992 | 210.1992 | -0.01 | 0.99 | -0.5 | 0.5 | -0.41 | 0.59 | 76.17 | 29.3
2019-10-01 | 10:06 | 210.293 | 210.293 | -0.02 | 0.98 | -0.49 | 0.51 | -0.41 | 0.59 | 76.17 | 29.3
2019-10-01 | 10:06 | 210.3906 | 210.3906 | -0.01 | 0.99 | -0.5 | 0.5 | -0.39 | 0.61 | 76.17 | 26.37
2019-10-01 | 10:06 | 210.4805 | 210.4805 | -0.01 | 0.99 | -0.49 | 0.51 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:06 | 210.5898 | 210.5898 | -0.1 | 0.9 | -0.42 | 0.58 | -0.4 | 0.6 | 76.17 | 25.39
2019-10-01 | 10:06 | 210.6914 | 210.6914 | -0.11 | 0.89 | -0.42 | 0.58 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 210.793 | 210.793 | -0.13 | 0.87 | -0.42 | 0.58 | -0.38 | 0.62 | 75.2 | 25.39
2019-10-01 | 10:06 | 210.9102 | 210.9102 | -0.14 | 0.86 | -0.4 | 0.6 | -0.37 | 0.63 | 75.2 | 28.32
2019-10-01 | 10:06 | 211.0117 | 211.0117 | -0.05 | 0.95 | -0.48 | 0.52 | -0.39 | 0.61 | 75.2 | 28.32
2019-10-01 | 10:06 | 211.1328 | 211.1328 | -0.04 | 0.96 | -0.48 | 0.52 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:06 | 211.2109 | 211.2109 | -0.03 | 0.97 | -0.49 | 0.51 | -0.4 | 0.6 | 75.2 | 26.37
2019-10-01 | 10:06 | 211.3008 | 211.3008 | -0.03 | 0.97 | -0.48 | 0.52 | -0.38 | 0.62 | 75.2 | 24.41
2019-10-01 | 10:06 | 211.4102 | 211.4102 | -0.02 | 0.98 | -0.49 | 0.51 | -0.41 | 0.59 | 73.24 | 26.37
2019-10-01 | 10:06 | 211.5195 | 211.5195 | -0.02 | 0.98 | -0.49 | 0.51 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:06 | 211.6211 | 211.6211 | -0.02 | 0.98 | -0.49 | 0.51 | -0.39 | 0.61 | 75.2 | 27.34
2019-10-01 | 10:06 | 211.7227 | 211.7227 | -0.02 | 0.98 | -0.48 | 0.52 | -0.39 | 0.61 | 75.2 | 28.32
2019-10-01 | 10:06 | 211.8125 | 211.8125 | -0.03 | 0.97 | -0.49 | 0.51 | -0.4 | 0.6 | 75.2 | 30.27
2019-10-01 | 10:06 | 211.9414 | 211.9414 | -0.02 | 0.98 | -0.49 | 0.51 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:06 | 212.043 | 212.043 | -0.05 | 0.95 | -0.46 | 0.54 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:06 | 212.1602 | 212.1602 | -0.1 | 0.9 | -0.41 | 0.59 | -0.4 | 0.6 | 75.2 | 23.44
2019-10-01 | 10:06 | 212.2422 | 212.2422 | -0.13 | 0.87 | -0.4 | 0.6 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 212.3398 | 212.3398 | -0.12 | 0.88 | -0.41 | 0.59 | -0.37 | 0.63 | 76.17 | 32.23
2019-10-01 | 10:06 | 212.4414 | 212.4414 | -0.12 | 0.88 | -0.39 | 0.61 | -0.37 | 0.63 | 76.17 | 29.3
2019-10-01 | 10:06 | 212.5625 | 212.5625 | -0.05 | 0.95 | -0.47 | 0.53 | -0.38 | 0.62 | 76.17 | 28.32
2019-10-01 | 10:06 | 212.6406 | 212.6406 | -0.05 | 0.95 | -0.47 | 0.53 | -0.38 | 0.62 | 74.22 | 26.37
2019-10-01 | 10:06 | 212.7422 | 212.7422 | -0.05 | 0.95 | -0.46 | 0.54 | -0.39 | 0.61 | 74.22 | 25.39
2019-10-01 | 10:06 | 212.8516 | 212.8516 | -0.05 | 0.95 | -0.48 | 0.52 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:06 | 212.9492 | 212.9492 | -0.04 | 0.96 | -0.47 | 0.53 | -0.38 | 0.62 | 75.2 | 25.39
2019-10-01 | 10:06 | 213.0508 | 213.0508 | -0.04 | 0.96 | -0.47 | 0.53 | -0.37 | 0.63 | 74.22 | 26.37
2019-10-01 | 10:06 | 213.1523 | 213.1523 | -0.04 | 0.96 | -0.48 | 0.52 | -0.41 | 0.59 | 75.2 | 28.32
2019-10-01 | 10:06 | 213.2617 | 213.2617 | -0.04 | 0.96 | -0.48 | 0.52 | -0.4 | 0.6 | 75.2 | 28.32
2019-10-01 | 10:06 | 213.3711 | 213.3711 | -0.04 | 0.96 | -0.48 | 0.52 | -0.38 | 0.62 | 74.22 | 25.39
2019-10-01 | 10:06 | 213.4805 | 213.4805 | -0.03 | 0.97 | -0.48 | 0.52 | -0.4 | 0.6 | 75.2 | 24.41
2019-10-01 | 10:06 | 213.6016 | 213.6016 | -0.09 | 0.91 | -0.42 | 0.58 | -0.4 | 0.6 | 74.22 | 26.37
2019-10-01 | 10:06 | 213.6914 | 213.6914 | -0.11 | 0.89 | -0.41 | 0.59 | -0.37 | 0.63 | 74.22 | 25.39
2019-10-01 | 10:06 | 213.8203 | 213.8203 | -0.12 | 0.88 | -0.4 | 0.6 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:06 | 213.9102 | 213.9102 | -0.13 | 0.87 | -0.39 | 0.61 | -0.37 | 0.63 | 77.15 | 29.3
2019-10-01 | 10:06 | 214.0117 | 214.0117 | -0.06 | 0.94 | -0.44 | 0.56 | -0.36 | 0.64 | 76.17 | 29.3
2019-10-01 | 10:06 | 214.0898 | 214.0898 | -0.07 | 0.93 | -0.46 | 0.54 | -0.39 | 0.61 | 75.2 | 24.41
2019-10-01 | 10:06 | 214.1992 | 214.1992 | -0.04 | 0.96 | -0.46 | 0.54 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:06 | 214.3125 | 214.3125 | -0.03 | 0.97 | -0.46 | 0.54 | -0.38 | 0.62 | 77.15 | 25.39
2019-10-01 | 10:06 | 214.4023 | 214.4023 | -0.04 | 0.96 | -0.48 | 0.52 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 214.4922 | 214.4922 | -0.04 | 0.96 | -0.47 | 0.53 | -0.38 | 0.62 | 75.2 | 26.37
2019-10-01 | 10:06 | 214.6016 | 214.6016 | -0.03 | 0.97 | -0.46 | 0.54 | -0.38 | 0.62 | 76.17 | 26.37
2019-10-01 | 10:06 | 214.6992 | 214.6992 | -0.04 | 0.96 | -0.46 | 0.54 | -0.39 | 0.61 | 76.17 | 29.3
2019-10-01 | 10:06 | 214.8008 | 214.8008 | -0.03 | 0.97 | -0.47 | 0.53 | -0.37 | 0.63 | 75.2 | 49.8
2019-10-01 | 10:06 | 214.9219 | 214.9219 | -0.01 | 0.99 | -0.47 | 0.53 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:06 | 215.0117 | 215.0117 | -0.04 | 0.96 | -0.46 | 0.54 | -0.39 | 0.61 | 75.2 | 24.41
2019-10-01 | 10:06 | 215.1094 | 215.1094 | -0.09 | 0.91 | -0.41 | 0.59 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:06 | 215.2305 | 215.2305 | -0.12 | 0.88 | -0.4 | 0.6 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:06 | 215.332 | 215.332 | -0.12 | 0.88 | -0.39 | 0.61 | -0.37 | 0.63 | 77.15 | 28.32
2019-10-01 | 10:06 | 215.4297 | 215.4297 | -0.13 | 0.87 | -0.38 | 0.62 | -0.37 | 0.63 | 78.12 | 29.3
2019-10-01 | 10:06 | 215.5508 | 215.5508 | -0.05 | 0.95 | -0.46 | 0.54 | -0.37 | 0.63 | 77.15 | 27.34
2019-10-01 | 10:06 | 215.6406 | 215.6406 | -0.04 | 0.96 | -0.45 | 0.55 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:06 | 215.7305 | 215.7305 | -0.04 | 0.96 | -0.46 | 0.54 | -0.37 | 0.63 | 77.15 | 26.37
2019-10-01 | 10:06 | 215.832 | 215.832 | -0.04 | 0.96 | -0.45 | 0.55 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:06 | 215.9414 | 215.9414 | -0.03 | 0.97 | -0.44 | 0.56 | -0.38 | 0.62 | 75.2 | 25.39
2019-10-01 | 10:06 | 216.0625 | 216.0625 | -0.03 | 0.97 | -0.46 | 0.54 | -0.37 | 0.63 | 77.15 | 24.41
2019-10-01 | 10:06 | 216.1523 | 216.1523 | -0.04 | 0.96 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:06 | 216.25 | 216.25 | -0.02 | 0.98 | -0.46 | 0.54 | -0.38 | 0.62 | 77.15 | 28.32
2019-10-01 | 10:06 | 216.3398 | 216.3398 | -0.01 | 0.99 | -0.47 | 0.53 | -0.38 | 0.62 | 77.15 | 27.34
2019-10-01 | 10:06 | 216.4414 | 216.4414 | -0.03 | 0.97 | -0.46 | 0.54 | -0.38 | 0.62 | 77.15 | 25.39
2019-10-01 | 10:06 | 216.5508 | 216.5508 | -0.06 | 0.94 | -0.41 | 0.59 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:06 | 216.6523 | 216.6523 | -0.11 | 0.89 | -0.4 | 0.6 | -0.36 | 0.64 | 77.15 | 26.37
2019-10-01 | 10:06 | 216.75 | 216.75 | -0.13 | 0.87 | -0.38 | 0.62 | -0.35 | 0.65 | 78.12 | 25.39
2019-10-01 | 10:06 | 216.8516 | 216.8516 | -0.13 | 0.87 | -0.38 | 0.62 | -0.35 | 0.65 | 76.17 | 29.3
2019-10-01 | 10:06 | 216.9922 | 216.9922 | -0.12 | 0.88 | -0.37 | 0.63 | -0.35 | 0.65 | 75.2 | 28.32
2019-10-01 | 10:06 | 217.0898 | 217.0898 | -0.05 | 0.95 | -0.45 | 0.55 | -0.38 | 0.62 | 78.12 | 25.39
2019-10-01 | 10:06 | 217.1914 | 217.1914 | -0.04 | 0.96 | -0.43 | 0.57 | -0.38 | 0.62 | 77.15 | 26.37
2019-10-01 | 10:06 | 217.293 | 217.293 | -0.04 | 0.96 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 217.3906 | 217.3906 | -0.04 | 0.96 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 217.4727 | 217.4727 | -0.04 | 0.96 | -0.44 | 0.56 | -0.37 | 0.63 | 77.15 | 25.39
2019-10-01 | 10:06 | 217.582 | 217.582 | -0.03 | 0.97 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:06 | 217.6914 | 217.6914 | -0.03 | 0.97 | -0.44 | 0.56 | -0.38 | 0.62 | 76.17 | 29.3
2019-10-01 | 10:06 | 217.793 | 217.793 | -0.01 | 0.99 | -0.45 | 0.55 | -0.37 | 0.63 | 77.15 | 52.73
2019-10-01 | 10:06 | 217.9023 | 217.9023 | -0.02 | 0.98 | -0.45 | 0.55 | -0.37 | 0.63 | 75.2 | 27.34
2019-10-01 | 10:06 | 217.9922 | 217.9922 | -0.04 | 0.96 | -0.45 | 0.55 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:06 | 218.0898 | 218.0898 | -0.09 | 0.91 | -0.39 | 0.61 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:06 | 218.1797 | 218.1797 | -0.11 | 0.89 | -0.38 | 0.62 | -0.36 | 0.64 | 76.17 | 26.37
2019-10-01 | 10:06 | 218.3008 | 218.3008 | -0.11 | 0.89 | -0.39 | 0.61 | -0.35 | 0.65 | 77.15 | 26.37
2019-10-01 | 10:06 | 218.4023 | 218.4023 | -0.11 | 0.89 | -0.38 | 0.62 | -0.35 | 0.65 | 76.17 | 29.3
2019-10-01 | 10:06 | 218.5 | 218.5 | -0.05 | 0.95 | -0.44 | 0.56 | -0.34 | 0.66 | 77.15 | 27.34
2019-10-01 | 10:06 | 218.6094 | 218.6094 | -0.02 | 0.98 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:06 | 218.7227 | 218.7227 | 0 | 1 | -0.44 | 0.56 | -0.37 | 0.63 | 77.15 | 26.37
2019-10-01 | 10:06 | 218.8125 | 218.8125 | -0.01 | 0.99 | -0.44 | 0.56 | -0.37 | 0.63 | 78.12 | 26.37
2019-10-01 | 10:06 | 218.9219 | 218.9219 | -0.02 | 0.98 | -0.43 | 0.57 | -0.37 | 0.63 | 77.15 | 25.39
2019-10-01 | 10:06 | 219.0195 | 219.0195 | -0.01 | 0.99 | -0.44 | 0.56 | -0.38 | 0.62 | 76.17 | 26.37
2019-10-01 | 10:06 | 219.1406 | 219.1406 | -0.01 | 0.99 | -0.45 | 0.55 | -0.38 | 0.62 | 77.15 | 29.3
2019-10-01 | 10:06 | 219.2305 | 219.2305 | 0 | 1 | -0.45 | 0.55 | -0.37 | 0.63 | 75.2 | 28.32
2019-10-01 | 10:06 | 219.3203 | 219.3203 | -0.01 | 0.99 | -0.45 | 0.55 | -0.38 | 0.62 | 75.2 | 25.39
2019-10-01 | 10:06 | 219.4297 | 219.4297 | 0 | 1 | -0.44 | 0.56 | -0.38 | 0.62 | 76.17 | 24.41
2019-10-01 | 10:06 | 219.543 | 219.543 | -0.03 | 0.97 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 219.6523 | 219.6523 | -0.09 | 0.91 | -0.38 | 0.62 | -0.37 | 0.63 | 76.17 | 27.34
2019-10-01 | 10:06 | 219.75 | 219.75 | -0.12 | 0.88 | -0.36 | 0.64 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:06 | 219.8398 | 219.8398 | -0.12 | 0.88 | -0.37 | 0.63 | -0.36 | 0.64 | 75.2 | 28.32
2019-10-01 | 10:06 | 219.9492 | 219.9492 | -0.11 | 0.89 | -0.37 | 0.63 | -0.35 | 0.65 | 77.15 | 29.3
2019-10-01 | 10:06 | 220.0508 | 220.0508 | -0.03 | 0.97 | -0.44 | 0.56 | -0.35 | 0.65 | 75.2 | 26.37
2019-10-01 | 10:06 | 220.1523 | 220.1523 | -0.02 | 0.98 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:06 | 220.25 | 220.25 | -0.02 | 0.98 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 220.3594 | 220.3594 | -0.01 | 0.99 | -0.44 | 0.56 | -0.35 | 0.65 | 77.15 | 27.34
2019-10-01 | 10:06 | 220.4727 | 220.4727 | -0.02 | 0.98 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 220.582 | 220.582 | -0.02 | 0.98 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 27.34
2019-10-01 | 10:06 | 220.6797 | 220.6797 | -0.01 | 0.99 | -0.44 | 0.56 | -0.36 | 0.64 | 75.2 | 28.32
2019-10-01 | 10:06 | 220.7813 | 220.7813 | -0.01 | 0.99 | -0.43 | 0.57 | -0.37 | 0.63 | 77.15 | 26.37
2019-10-01 | 10:06 | 220.8594 | 220.8594 | -0.01 | 0.99 | -0.44 | 0.56 | -0.37 | 0.63 | 75.2 | 26.37
2019-10-01 | 10:06 | 220.9805 | 220.9805 | 0 | 1 | -0.44 | 0.56 | -0.37 | 0.63 | 78.12 | 25.39
2019-10-01 | 10:06 | 221.082 | 221.082 | -0.06 | 0.94 | -0.39 | 0.61 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:06 | 221.1992 | 221.1992 | -0.09 | 0.91 | -0.38 | 0.62 | -0.34 | 0.66 | 76.17 | 26.37
2019-10-01 | 10:06 | 221.3008 | 221.3008 | -0.11 | 0.89 | -0.37 | 0.63 | -0.35 | 0.65 | 75.2 | 50.78
2019-10-01 | 10:06 | 221.4102 | 221.4102 | -0.12 | 0.88 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 28.32
2019-10-01 | 10:06 | 221.5117 | 221.5117 | -0.08 | 0.92 | -0.4 | 0.6 | -0.33 | 0.67 | 75.2 | 27.34
2019-10-01 | 10:06 | 221.6016 | 221.6016 | -0.02 | 0.98 | -0.43 | 0.57 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:06 | 221.6992 | 221.6992 | -0.01 | 0.99 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:06 | 221.832 | 221.832 | -0.03 | 0.97 | -0.43 | 0.57 | -0.36 | 0.64 | 77.15 | 26.37
2019-10-01 | 10:06 | 221.9219 | 221.9219 | -0.02 | 0.98 | -0.43 | 0.57 | -0.36 | 0.64 | 76.17 | 27.34
2019-10-01 | 10:06 | 222 | 222 | -0.01 | 0.99 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 26.37
2019-10-01 | 10:06 | 222.1211 | 222.1211 | 0 | 1 | -0.42 | 0.58 | -0.36 | 0.64 | 77.15 | 29.3
2019-10-01 | 10:06 | 222.2109 | 222.2109 | -0.03 | 0.97 | -0.43 | 0.57 | -0.36 | 0.64 | 76.17 | 28.32
2019-10-01 | 10:06 | 222.3125 | 222.3125 | -0.02 | 0.98 | -0.43 | 0.57 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:06 | 222.4102 | 222.4102 | -0.01 | 0.99 | -0.43 | 0.57 | -0.36 | 0.64 | 77.15 | 27.34
2019-10-01 | 10:06 | 222.5117 | 222.5117 | -0.02 | 0.98 | -0.42 | 0.58 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:06 | 222.6094 | 222.6094 | -0.1 | 0.9 | -0.37 | 0.63 | -0.36 | 0.64 | 78.12 | 26.37
2019-10-01 | 10:06 | 222.7227 | 222.7227 | -0.12 | 0.88 | -0.37 | 0.63 | -0.35 | 0.65 | 75.2 | 24.41
2019-10-01 | 10:06 | 222.832 | 222.832 | -0.12 | 0.88 | -0.37 | 0.63 | -0.34 | 0.66 | 77.15 | 27.34
2019-10-01 | 10:06 | 222.9414 | 222.9414 | -0.13 | 0.87 | -0.37 | 0.63 | -0.34 | 0.66 | 75.2 | 29.3
2019-10-01 | 10:06 | 223.043 | 223.043 | -0.05 | 0.95 | -0.43 | 0.57 | -0.33 | 0.67 | 75.2 | 36.13
2019-10-01 | 10:06 | 223.1328 | 223.1328 | -0.04 | 0.96 | -0.42 | 0.58 | -0.36 | 0.64 | 75.2 | 26.37
2019-10-01 | 10:06 | 223.2305 | 223.2305 | -0.03 | 0.97 | -0.41 | 0.59 | -0.36 | 0.64 | 77.15 | 26.37
2019-10-01 | 10:06 | 223.332 | 223.332 | -0.03 | 0.97 | -0.42 | 0.58 | -0.34 | 0.66 | 78.12 | 26.37
2019-10-01 | 10:06 | 223.4297 | 223.4297 | -0.02 | 0.98 | -0.43 | 0.57 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:06 | 223.5508 | 223.5508 | -0.01 | 0.99 | -0.42 | 0.58 | -0.35 | 0.65 | 76.17 | 26.37
2019-10-01 | 10:06 | 223.6406 | 223.6406 | 0 | 1 | -0.43 | 0.57 | -0.35 | 0.65 | 75.2 | 28.32
2019-10-01 | 10:06 | 223.75 | 223.75 | -0.04 | 0.96 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 28.32
2019-10-01 | 10:06 | 223.8711 | 223.8711 | -0.02 | 0.98 | -0.43 | 0.57 | -0.36 | 0.64 | 76.17 | 27.34
2019-10-01 | 10:06 | 223.9414 | 223.9414 | -0.02 | 0.98 | -0.43 | 0.57 | -0.36 | 0.64 | 77.15 | 26.37
2019-10-01 | 10:06 | 224.0625 | 224.0625 | -0.05 | 0.95 | -0.39 | 0.61 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:06 | 224.1602 | 224.1602 | -0.09 | 0.91 | -0.37 | 0.63 | -0.35 | 0.65 | 77.15 | 26.37
2019-10-01 | 10:06 | 224.2617 | 224.2617 | -0.09 | 0.91 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 27.34
2019-10-01 | 10:06 | 224.3711 | 224.3711 | -0.11 | 0.89 | -0.37 | 0.63 | -0.33 | 0.67 | 77.15 | 29.3
2019-10-01 | 10:06 | 224.4609 | 224.4609 | -0.11 | 0.89 | -0.35 | 0.65 | -0.32 | 0.68 | 78.12 | 29.3
2019-10-01 | 10:06 | 224.582 | 224.582 | -0.03 | 0.97 | -0.42 | 0.58 | -0.35 | 0.65 | 76.17 | 27.34
2019-10-01 | 10:06 | 224.6602 | 224.6602 | -0.04 | 0.96 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 26.37
2019-10-01 | 10:06 | 224.7695 | 224.7695 | -0.01 | 0.99 | -0.42 | 0.58 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:06 | 224.8711 | 224.8711 | -0.01 | 0.99 | -0.41 | 0.59 | -0.36 | 0.64 | 76.17 | 26.37
2019-10-01 | 10:06 | 224.9727 | 224.9727 | -0.01 | 0.99 | -0.41 | 0.59 | -0.36 | 0.64 | 77.15 | 25.39
2019-10-01 | 10:06 | 225.0703 | 225.0703 | -0.01 | 0.99 | -0.43 | 0.57 | -0.35 | 0.65 | 77.15 | 29.3
2019-10-01 | 10:06 | 225.1797 | 225.1797 | 0 | 1 | -0.42 | 0.58 | -0.36 | 0.64 | 77.15 | 28.32
2019-10-01 | 10:06 | 225.2813 | 225.2813 | -0.02 | 0.98 | -0.42 | 0.58 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:06 | 225.3906 | 225.3906 | -0.02 | 0.98 | -0.43 | 0.57 | -0.36 | 0.64 | 75.2 | 26.37
2019-10-01 | 10:06 | 225.5 | 225.5 | -0.02 | 0.98 | -0.42 | 0.58 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:06 | 225.5898 | 225.5898 | -0.08 | 0.92 | -0.37 | 0.63 | -0.33 | 0.67 | 76.17 | 26.37
2019-10-01 | 10:06 | 225.6992 | 225.6992 | -0.1 | 0.9 | -0.37 | 0.63 | -0.34 | 0.66 | 77.15 | 26.37
2019-10-01 | 10:06 | 225.793 | 225.793 | -0.11 | 0.89 | -0.36 | 0.64 | -0.33 | 0.67 | 77.15 | 27.34
2019-10-01 | 10:06 | 225.9219 | 225.9219 | -0.11 | 0.89 | -0.35 | 0.65 | -0.32 | 0.68 | 77.15 | 29.3
2019-10-01 | 10:06 | 226.0195 | 226.0195 | -0.05 | 0.95 | -0.41 | 0.59 | -0.32 | 0.68 | 77.15 | 27.34
2019-10-01 | 10:06 | 226.1211 | 226.1211 | -0.04 | 0.96 | -0.4 | 0.6 | -0.35 | 0.65 | 76.17 | 26.37
2019-10-01 | 10:06 | 226.2305 | 226.2305 | -0.03 | 0.97 | -0.4 | 0.6 | -0.35 | 0.65 | 77.15 | 25.39
2019-10-01 | 10:06 | 226.332 | 226.332 | -0.04 | 0.96 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 25.39
2019-10-01 | 10:06 | 226.4219 | 226.4219 | -0.03 | 0.97 | -0.41 | 0.59 | -0.35 | 0.65 | 77.15 | 26.37
2019-10-01 | 10:06 | 226.5195 | 226.5195 | -0.04 | 0.96 | -0.41 | 0.59 | -0.34 | 0.66 | 75.2 | 24.41
2019-10-01 | 10:06 | 226.6211 | 226.6211 | -0.02 | 0.98 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 28.32
2019-10-01 | 10:06 | 226.75 | 226.75 | -0.03 | 0.97 | -0.42 | 0.58 | -0.36 | 0.64 | 75.2 | 28.32
2019-10-01 | 10:06 | 226.8516 | 226.8516 | -0.04 | 0.96 | -0.42 | 0.58 | -0.36 | 0.64 | 75.2 | 25.39
2019-10-01 | 10:06 | 226.9492 | 226.9492 | -0.02 | 0.98 | -0.42 | 0.58 | -0.35 | 0.65 | 76.17 | 24.41
2019-10-01 | 10:06 | 227.0508 | 227.0508 | -0.04 | 0.96 | -0.38 | 0.62 | -0.36 | 0.64 | 75.2 | 25.39
2019-10-01 | 10:06 | 227.1523 | 227.1523 | -0.1 | 0.9 | -0.36 | 0.64 | -0.32 | 0.68 | 76.17 | 25.39
2019-10-01 | 10:06 | 227.25 | 227.25 | -0.11 | 0.89 | -0.36 | 0.64 | -0.32 | 0.68 | 76.17 | 26.37
2019-10-01 | 10:06 | 227.3398 | 227.3398 | -0.12 | 0.88 | -0.36 | 0.64 | -0.32 | 0.68 | 75.2 | 28.32
2019-10-01 | 10:06 | 227.4414 | 227.4414 | -0.12 | 0.88 | -0.35 | 0.65 | -0.31 | 0.69 | 78.12 | 29.3
2019-10-01 | 10:06 | 227.5508 | 227.5508 | -0.05 | 0.95 | -0.4 | 0.6 | -0.33 | 0.67 | 76.17 | 26.37
2019-10-01 | 10:06 | 227.6602 | 227.6602 | -0.03 | 0.97 | -0.4 | 0.6 | -0.36 | 0.64 | 76.17 | 27.34
2019-10-01 | 10:06 | 227.7813 | 227.7813 | -0.03 | 0.97 | -0.4 | 0.6 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:06 | 227.8828 | 227.8828 | -0.02 | 0.98 | -0.41 | 0.59 | -0.34 | 0.66 | 77.15 | 27.34
2019-10-01 | 10:06 | 227.9727 | 227.9727 | -0.04 | 0.96 | -0.4 | 0.6 | -0.35 | 0.65 | 75.2 | 25.39
2019-10-01 | 10:06 | 228.0625 | 228.0625 | -0.02 | 0.98 | -0.41 | 0.59 | -0.34 | 0.66 | 76.17 | 27.34
2019-10-01 | 10:06 | 228.1719 | 228.1719 | -0.01 | 0.99 | -0.41 | 0.59 | -0.34 | 0.66 | 76.17 | 28.32
2019-10-01 | 10:06 | 228.293 | 228.293 | -0.02 | 0.98 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 28.32
2019-10-01 | 10:06 | 228.4023 | 228.4023 | -0.02 | 0.98 | -0.4 | 0.6 | -0.35 | 0.65 | 75.2 | 25.39
2019-10-01 | 10:06 | 228.5117 | 228.5117 | -0.02 | 0.98 | -0.41 | 0.59 | -0.35 | 0.65 | 75.2 | 25.39
2019-10-01 | 10:06 | 228.6094 | 228.6094 | -0.07 | 0.93 | -0.36 | 0.64 | -0.34 | 0.66 | 76.17 | 26.37
2019-10-01 | 10:06 | 228.7109 | 228.7109 | -0.09 | 0.91 | -0.36 | 0.64 | -0.32 | 0.68 | 76.17 | 27.34
2019-10-01 | 10:06 | 228.8008 | 228.8008 | -0.1 | 0.9 | -0.35 | 0.65 | -0.31 | 0.69 | 76.17 | 26.37
2019-10-01 | 10:06 | 228.8828 | 228.8828 | -0.1 | 0.9 | -0.34 | 0.66 | -0.31 | 0.69 | 78.12 | 29.3
2019-10-01 | 10:06 | 228.9805 | 228.9805 | -0.08 | 0.92 | -0.36 | 0.64 | -0.31 | 0.69 | 76.17 | 29.3
2019-10-01 | 10:06 | 229.082 | 229.082 | -0.03 | 0.97 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 27.34
2019-10-01 | 10:06 | 229.1914 | 229.1914 | -0.04 | 0.96 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 25.39
2019-10-01 | 10:06 | 229.293 | 229.293 | -0.03 | 0.97 | -0.41 | 0.59 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:06 | 229.4023 | 229.4023 | -0.02 | 0.98 | -0.41 | 0.59 | -0.33 | 0.67 | 78.12 | 27.34
2019-10-01 | 10:06 | 229.5117 | 229.5117 | -0.02 | 0.98 | -0.4 | 0.6 | -0.33 | 0.67 | 76.17 | 25.39
2019-10-01 | 10:06 | 229.6094 | 229.6094 | -0.03 | 0.97 | -0.4 | 0.6 | -0.33 | 0.67 | 77.15 | 28.32
2019-10-01 | 10:06 | 229.7109 | 229.7109 | -0.02 | 0.98 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 28.32
2019-10-01 | 10:06 | 229.832 | 229.832 | -0.02 | 0.98 | -0.4 | 0.6 | -0.34 | 0.66 | 78.12 | 25.39
2019-10-01 | 10:06 | 229.9297 | 229.9297 | -0.01 | 0.99 | -0.41 | 0.59 | -0.36 | 0.64 | 77.15 | 26.37
2019-10-01 | 10:06 | 230.0313 | 230.0313 | -0.02 | 0.98 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 25.39
2019-10-01 | 10:06 | 230.1406 | 230.1406 | -0.08 | 0.92 | -0.35 | 0.65 | -0.32 | 0.68 | 76.17 | 26.37
2019-10-01 | 10:06 | 230.2422 | 230.2422 | -0.11 | 0.89 | -0.35 | 0.65 | -0.3 | 0.7 | 76.17 | 26.37
2019-10-01 | 10:06 | 230.3398 | 230.3398 | -0.09 | 0.91 | -0.35 | 0.65 | -0.32 | 0.68 | 77.15 | 26.37
2019-10-01 | 10:06 | 230.4414 | 230.4414 | -0.12 | 0.88 | -0.34 | 0.66 | -0.31 | 0.69 | 76.17 | 28.32
2019-10-01 | 10:06 | 230.5313 | 230.5313 | -0.04 | 0.96 | -0.4 | 0.6 | -0.3 | 0.7 | 77.15 | 27.34
2019-10-01 | 10:06 | 230.6406 | 230.6406 | -0.03 | 0.97 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 26.37
2019-10-01 | 10:06 | 230.75 | 230.75 | -0.01 | 0.99 | -0.4 | 0.6 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:06 | 230.832 | 230.832 | -0.02 | 0.98 | -0.39 | 0.61 | -0.33 | 0.67 | 75.2 | 24.41
2019-10-01 | 10:06 | 230.9414 | 230.9414 | -0.03 | 0.97 | -0.4 | 0.6 | -0.33 | 0.67 | 75.2 | 25.39
2019-10-01 | 10:06 | 231.043 | 231.043 | -0.01 | 0.99 | -0.4 | 0.6 | -0.34 | 0.66 | 75.2 | 25.39
2019-10-01 | 10:06 | 231.1406 | 231.1406 | -0.02 | 0.98 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 28.32
2019-10-01 | 10:06 | 231.2422 | 231.2422 | -0.01 | 0.99 | -0.41 | 0.59 | -0.33 | 0.67 | 76.17 | 28.32
2019-10-01 | 10:06 | 231.3594 | 231.3594 | -0.01 | 0.99 | -0.4 | 0.6 | -0.34 | 0.66 | 76.17 | 26.37
2019-10-01 | 10:06 | 231.4609 | 231.4609 | -0.01 | 0.99 | -0.4 | 0.6 | -0.33 | 0.67 | 76.17 | 27.34
2019-10-01 | 10:06 | 231.5625 | 231.5625 | -0.05 | 0.95 | -0.37 | 0.63 | -0.33 | 0.67 | 77.15 | 24.41
2019-10-01 | 10:06 | 231.6797 | 231.6797 | -0.08 | 0.92 | -0.36 | 0.64 | -0.31 | 0.69 | 76.17 | 26.37
2019-10-01 | 10:06 | 231.793 | 231.793 | -0.1 | 0.9 | -0.34 | 0.66 | -0.31 | 0.69 | 75.2 | 24.41
2019-10-01 | 10:06 | 231.8711 | 231.8711 | -0.1 | 0.9 | -0.35 | 0.65 | -0.31 | 0.69 | 76.17 | 27.34
2019-10-01 | 10:06 | 231.9727 | 231.9727 | -0.11 | 0.89 | -0.33 | 0.67 | -0.3 | 0.7 | 76.17 | 28.32
2019-10-01 | 10:06 | 232.0703 | 232.0703 | -0.02 | 0.98 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 47.85
2019-10-01 | 10:06 | 232.1719 | 232.1719 | -0.02 | 0.98 | -0.38 | 0.62 | -0.34 | 0.66 | 77.15 | 26.37
2019-10-01 | 10:06 | 232.2695 | 232.2695 | -0.02 | 0.98 | -0.39 | 0.61 | -0.31 | 0.69 | 76.17 | 25.39
2019-10-01 | 10:06 | 232.3906 | 232.3906 | -0.01 | 0.99 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 26.37
2019-10-01 | 10:06 | 232.4922 | 232.4922 | -0.02 | 0.98 | -0.39 | 0.61 | -0.33 | 0.67 | 75.2 | 26.37
2019-10-01 | 10:06 | 232.5898 | 232.5898 | 0 | 1 | -0.39 | 0.61 | -0.32 | 0.68 | 75.2 | 42.97
2019-10-01 | 10:06 | 232.6992 | 232.6992 | 0.01 | 1.01 | -0.38 | 0.62 | -0.33 | 0.67 | 76.17 | 28.32
2019-10-01 | 10:06 | 232.8125 | 232.8125 | 0 | 1 | -0.39 | 0.61 | -0.34 | 0.66 | 77.15 | 27.34
2019-10-01 | 10:06 | 232.9023 | 232.9023 | -0.01 | 0.99 | -0.4 | 0.6 | -0.31 | 0.69 | 75.2 | 25.39
2019-10-01 | 10:06 | 232.9922 | 232.9922 | 0 | 1 | -0.4 | 0.6 | -0.33 | 0.67 | 75.2 | 25.39
2019-10-01 | 10:06 | 233.1016 | 233.1016 | -0.08 | 0.92 | -0.35 | 0.65 | -0.32 | 0.68 | 75.2 | 25.39
2019-10-01 | 10:06 | 233.2227 | 233.2227 | -0.07 | 0.93 | -0.34 | 0.66 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:06 | 233.3203 | 233.3203 | -0.09 | 0.91 | -0.34 | 0.66 | -0.31 | 0.69 | 75.2 | 25.39
2019-10-01 | 10:06 | 233.4219 | 233.4219 | -0.1 | 0.9 | -0.34 | 0.66 | -0.31 | 0.69 | 75.2 | 29.3
2019-10-01 | 10:06 | 233.5195 | 233.5195 | -0.05 | 0.95 | -0.39 | 0.61 | -0.3 | 0.7 | 75.2 | 28.32
2019-10-01 | 10:06 | 233.6211 | 233.6211 | -0.02 | 0.98 | -0.39 | 0.61 | -0.33 | 0.67 | 75.2 | 26.37
2019-10-01 | 10:06 | 233.7227 | 233.7227 | -0.02 | 0.98 | -0.38 | 0.62 | -0.33 | 0.67 | 75.2 | 25.39
2019-10-01 | 10:06 | 233.8398 | 233.8398 | -0.02 | 0.98 | -0.39 | 0.61 | -0.33 | 0.67 | 76.17 | 23.44
2019-10-01 | 10:06 | 233.9219 | 233.9219 | 0 | 1 | -0.4 | 0.6 | -0.33 | 0.67 | 75.2 | 25.39
2019-10-01 | 10:06 | 234.0195 | 234.0195 | -0.01 | 0.99 | -0.39 | 0.61 | -0.33 | 0.67 | 77.15 | 26.37
2019-10-01 | 10:06 | 234.1211 | 234.1211 | -0.01 | 0.99 | -0.39 | 0.61 | -0.33 | 0.67 | 80.08 | 27.34
2019-10-01 | 10:06 | 234.2305 | 234.2305 | 0 | 1 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 29.3
2019-10-01 | 10:06 | 234.332 | 234.332 | -0.01 | 0.99 | -0.4 | 0.6 | -0.32 | 0.68 | 77.15 | 27.34
2019-10-01 | 10:06 | 234.4414 | 234.4414 | 0 | 1 | -0.39 | 0.61 | -0.32 | 0.68 | 77.15 | 26.37
2019-10-01 | 10:06 | 234.582 | 234.582 | -0.01 | 0.99 | -0.37 | 0.63 | -0.32 | 0.68 | 76.17 | 27.34
2019-10-01 | 10:06 | 234.6992 | 234.6992 | -0.07 | 0.93 | -0.34 | 0.66 | -0.31 | 0.69 | 76.17 | 25.39
2019-10-01 | 10:06 | 234.793 | 234.793 | -0.07 | 0.93 | -0.34 | 0.66 | -0.31 | 0.69 | 76.17 | 26.37
2019-10-01 | 10:06 | 234.8711 | 234.8711 | -0.1 | 0.9 | -0.34 | 0.66 | -0.3 | 0.7 | 76.17 | 26.37
2019-10-01 | 10:06 | 234.9492 | 234.9492 | -0.09 | 0.91 | -0.33 | 0.67 | -0.29 | 0.71 | 75.2 | 28.32
2019-10-01 | 10:06 | 235.0508 | 235.0508 | -0.03 | 0.97 | -0.37 | 0.63 | -0.31 | 0.69 | 75.2 | 28.32
2019-10-01 | 10:06 | 235.1602 | 235.1602 | -0.01 | 0.99 | -0.38 | 0.62 | -0.33 | 0.67 | 76.17 | 26.37
2019-10-01 | 10:06 | 235.2695 | 235.2695 | 0 | 1 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 26.37
2019-10-01 | 10:06 | 235.3711 | 235.3711 | -0.01 | 0.99 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 26.37
2019-10-01 | 10:06 | 235.4492 | 235.4492 | 0 | 1 | -0.39 | 0.61 | -0.32 | 0.68 | 75.2 | 25.39
2019-10-01 | 10:06 | 235.5625 | 235.5625 | 0.01 | 1.01 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 26.37
2019-10-01 | 10:06 | 235.6602 | 235.6602 | -0.01 | 0.99 | -0.39 | 0.61 | -0.33 | 0.67 | 75.2 | 26.37
2019-10-01 | 10:06 | 235.7617 | 235.7617 | 0 | 1 | -0.39 | 0.61 | -0.32 | 0.68 | 76.17 | 28.32
2019-10-01 | 10:06 | 235.8594 | 235.8594 | -0.01 | 0.99 | -0.39 | 0.61 | -0.33 | 0.67 | 75.2 | 40.04
2019-10-01 | 10:06 | 235.9805 | 235.9805 | -0.01 | 0.99 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 27.34
2019-10-01 | 10:06 | 236.082 | 236.082 | -0.07 | 0.93 | -0.35 | 0.65 | -0.33 | 0.67 | 75.2 | 26.37
2019-10-01 | 10:06 | 236.2109 | 236.2109 | -0.09 | 0.91 | -0.34 | 0.66 | -0.3 | 0.7 | 77.15 | 27.34
2019-10-01 | 10:06 | 236.2813 | 236.2813 | -0.08 | 0.92 | -0.34 | 0.66 | -0.32 | 0.68 | 76.17 | 25.39
2019-10-01 | 10:06 | 236.4102 | 236.4102 | -0.09 | 0.91 | -0.32 | 0.68 | -0.3 | 0.7 | 77.15 | 37.11 | BREAK 1
2019-10-01 | 10:07 | 0.10156 | 236.5118 | -0.06 | 0.94 | -0.37 | 0.63 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 0.19922 | 236.6094 | -0.07 | 0.93 | -0.37 | 0.63 | -0.35 | 0.65 | 77.15 | 27.34
2019-10-01 | 10:07 | 0.30078 | 236.711 | -0.1 | 0.9 | -0.37 | 0.63 | -0.34 | 0.66 | 75.2 | 25.39
2019-10-01 | 10:07 | 0.41016 | 236.8204 | -0.1 | 0.9 | -0.37 | 0.63 | -0.34 | 0.66 | 75.2 | 28.32
2019-10-01 | 10:07 | 0.51172 | 236.9219 | 0.01 | 1.01 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 29.3
2019-10-01 | 10:07 | 0.60938 | 237.0196 | 0.01 | 1.01 | -0.43 | 0.57 | -0.37 | 0.63 | 75.2 | 34.18
2019-10-01 | 10:07 | 0.71094 | 237.1211 | 0.01 | 1.01 | -0.44 | 0.56 | -0.37 | 0.63 | 75.2 | 26.37
2019-10-01 | 10:07 | 0.82031 | 237.2305 | 0.01 | 1.01 | -0.43 | 0.57 | -0.37 | 0.63 | 74.22 | 24.41
2019-10-01 | 10:07 | 0.92188 | 237.3321 | 0.01 | 1.01 | -0.45 | 0.55 | -0.37 | 0.63 | 75.2 | 24.41
2019-10-01 | 10:07 | 1.0195 | 237.4297 | 0.01 | 1.01 | -0.44 | 0.56 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 1.1211 | 237.5313 | 0.03 | 1.03 | -0.45 | 0.55 | -0.38 | 0.62 | 74.22 | 50.78
2019-10-01 | 10:07 | 1.2305 | 237.6407 | 0.02 | 1.02 | -0.45 | 0.55 | -0.37 | 0.63 | 75.2 | 28.32
2019-10-01 | 10:07 | 1.3281 | 237.7383 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 75.2 | 27.34
2019-10-01 | 10:07 | 1.4297 | 237.8399 | 0.02 | 1.02 | -0.44 | 0.56 | -0.38 | 0.62 | 75.2 | 26.37
2019-10-01 | 10:07 | 1.5391 | 237.9493 | -0.05 | 0.95 | -0.4 | 0.6 | -0.37 | 0.63 | 75.2 | 24.41
2019-10-01 | 10:07 | 1.6406 | 238.0508 | -0.09 | 0.91 | -0.38 | 0.62 | -0.37 | 0.63 | 75.2 | 24.41
2019-10-01 | 10:07 | 1.7383 | 238.1485 | -0.09 | 0.91 | -0.38 | 0.62 | -0.37 | 0.63 | 74.22 | 25.39
2019-10-01 | 10:07 | 1.8398 | 238.25 | -0.08 | 0.92 | -0.37 | 0.63 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:07 | 1.9492 | 238.3594 | -0.02 | 0.98 | -0.44 | 0.56 | -0.36 | 0.64 | 75.2 | 29.3
2019-10-01 | 10:07 | 2.0508 | 238.461 | 0 | 1 | -0.45 | 0.55 | -0.38 | 0.62 | 75.2 | 29.3
2019-10-01 | 10:07 | 2.1484 | 238.5586 | 0.01 | 1.01 | -0.44 | 0.56 | -0.38 | 0.62 | 75.2 | 24.41
2019-10-01 | 10:07 | 2.25 | 238.6602 | 0.01 | 1.01 | -0.45 | 0.55 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:07 | 2.3594 | 238.7696 | 0.01 | 1.01 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 23.44
2019-10-01 | 10:07 | 2.4609 | 238.8711 | 0.01 | 1.01 | -0.45 | 0.55 | -0.38 | 0.62 | 75.2 | 25.39
2019-10-01 | 10:07 | 2.5586 | 238.9688 | 0.02 | 1.02 | -0.45 | 0.55 | -0.39 | 0.61 | 75.2 | 26.37
2019-10-01 | 10:07 | 2.6719 | 239.0821 | 0.03 | 1.03 | -0.46 | 0.54 | -0.38 | 0.62 | 75.2 | 41.02
2019-10-01 | 10:07 | 2.7695 | 239.1797 | 0.01 | 1.01 | -0.46 | 0.54 | -0.39 | 0.61 | 75.2 | 28.32
2019-10-01 | 10:07 | 2.8711 | 239.2813 | 0.02 | 1.02 | -0.46 | 0.54 | -0.4 | 0.6 | 75.2 | 27.34
2019-10-01 | 10:07 | 2.9805 | 239.3907 | 0.01 | 1.01 | -0.46 | 0.54 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:07 | 3.0781 | 239.4883 | -0.04 | 0.96 | -0.4 | 0.6 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 3.1797 | 239.5899 | -0.09 | 0.91 | -0.4 | 0.6 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 3.2812 | 239.6915 | -0.09 | 0.91 | -0.39 | 0.61 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:07 | 3.3906 | 239.8008 | -0.09 | 0.91 | -0.38 | 0.62 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 3.4883 | 239.8985 | 0 | 1 | -0.46 | 0.54 | -0.38 | 0.62 | 75.2 | 28.32
2019-10-01 | 10:07 | 3.5898 | 240 | 0.01 | 1.01 | -0.46 | 0.54 | -0.39 | 0.61 | 75.2 | 28.32
2019-10-01 | 10:07 | 3.6914 | 240.1016 | 0.01 | 1.01 | -0.47 | 0.53 | -0.4 | 0.6 | 75.2 | 25.39
2019-10-01 | 10:07 | 3.8008 | 240.211 | 0.02 | 1.02 | -0.47 | 0.53 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:07 | 3.8984 | 240.3086 | 0.02 | 1.02 | -0.48 | 0.52 | -0.4 | 0.6 | 76.17 | 25.39
2019-10-01 | 10:07 | 4 | 240.4102 | 0.02 | 1.02 | -0.47 | 0.53 | -0.41 | 0.59 | 75.2 | 24.41
2019-10-01 | 10:07 | 4.1016 | 240.5118 | 0.02 | 1.02 | -0.48 | 0.52 | -0.41 | 0.59 | 75.2 | 26.37
2019-10-01 | 10:07 | 4.2109 | 240.6211 | 0.01 | 1.01 | -0.49 | 0.51 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 4.3086 | 240.7188 | 0.02 | 1.02 | -0.49 | 0.51 | -0.41 | 0.59 | 75.2 | 28.32
2019-10-01 | 10:07 | 4.4102 | 240.8204 | 0.01 | 1.01 | -0.48 | 0.52 | -0.4 | 0.6 | 75.2 | 28.32
2019-10-01 | 10:07 | 4.5195 | 240.9297 | -0.01 | 0.99 | -0.44 | 0.56 | -0.4 | 0.6 | 77.15 | 27.34
2019-10-01 | 10:07 | 4.6211 | 241.0313 | -0.06 | 0.94 | -0.4 | 0.6 | -0.39 | 0.61 | 75.2 | 24.41
2019-10-01 | 10:07 | 4.7188 | 241.129 | -0.07 | 0.93 | -0.4 | 0.6 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:07 | 4.8203 | 241.2305 | -0.08 | 0.92 | -0.39 | 0.61 | -0.38 | 0.62 | 76.17 | 26.37
2019-10-01 | 10:07 | 4.9297 | 241.3399 | -0.1 | 0.9 | -0.4 | 0.6 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:07 | 5.0312 | 241.4415 | 0.01 | 1.01 | -0.48 | 0.52 | -0.41 | 0.59 | 75.2 | 29.3
2019-10-01 | 10:07 | 5.1289 | 241.5391 | 0.02 | 1.02 | -0.47 | 0.53 | -0.4 | 0.6 | 77.15 | 29.3
2019-10-01 | 10:07 | 5.2305 | 241.6407 | 0.01 | 1.01 | -0.49 | 0.51 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 5.3398 | 241.75 | 0.02 | 1.02 | -0.48 | 0.52 | -0.4 | 0.6 | 76.17 | 26.37
2019-10-01 | 10:07 | 5.4414 | 241.8516 | 0.02 | 1.02 | -0.49 | 0.51 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:07 | 5.5508 | 241.961 | 0.03 | 1.03 | -0.49 | 0.51 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:07 | 5.6484 | 242.0586 | 0.01 | 1.01 | -0.48 | 0.52 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 5.75 | 242.1602 | 0.02 | 1.02 | -0.49 | 0.51 | -0.41 | 0.59 | 76.17 | 27.34
2019-10-01 | 10:07 | 5.8516 | 242.2618 | 0.02 | 1.02 | -0.49 | 0.51 | -0.42 | 0.58 | 75.2 | 28.32
2019-10-01 | 10:07 | 5.9609 | 242.3711 | 0.03 | 1.03 | -0.48 | 0.52 | -0.42 | 0.58 | 75.2 | 27.34
2019-10-01 | 10:07 | 6.0586 | 242.4688 | -0.04 | 0.96 | -0.44 | 0.56 | -0.4 | 0.6 | 74.22 | 25.39
2019-10-01 | 10:07 | 6.1602 | 242.5704 | -0.08 | 0.92 | -0.42 | 0.58 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:07 | 6.2617 | 242.6719 | -0.08 | 0.92 | -0.42 | 0.58 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:07 | 6.3594 | 242.7696 | -0.09 | 0.91 | -0.41 | 0.59 | -0.4 | 0.6 | 75.2 | 24.41
2019-10-01 | 10:07 | 6.4688 | 242.879 | 0 | 1 | -0.49 | 0.51 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:07 | 6.5703 | 242.9805 | 0 | 1 | -0.5 | 0.5 | -0.42 | 0.58 | 75.2 | 29.3
2019-10-01 | 10:07 | 6.6719 | 243.0821 | 0.02 | 1.02 | -0.51 | 0.49 | -0.43 | 0.57 | 75.2 | 28.32
2019-10-01 | 10:07 | 6.7812 | 243.1915 | 0.01 | 1.01 | -0.51 | 0.49 | -0.44 | 0.56 | 75.2 | 26.37
2019-10-01 | 10:07 | 6.8789 | 243.2891 | 0.03 | 1.03 | -0.53 | 0.47 | -0.45 | 0.55 | 75.2 | 26.37
2019-10-01 | 10:07 | 6.9805 | 243.3907 | 0.02 | 1.02 | -0.52 | 0.48 | -0.43 | 0.57 | 75.2 | 24.41
2019-10-01 | 10:07 | 7.0898 | 243.5 | 0.02 | 1.02 | -0.53 | 0.47 | -0.43 | 0.57 | 77.15 | 26.37
2019-10-01 | 10:07 | 7.1914 | 243.6016 | 0.03 | 1.03 | -0.51 | 0.49 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 7.2891 | 243.6993 | 0.03 | 1.03 | -0.52 | 0.48 | -0.44 | 0.56 | 77.15 | 27.34
2019-10-01 | 10:07 | 7.3906 | 243.8008 | 0.02 | 1.02 | -0.53 | 0.47 | -0.45 | 0.55 | 75.2 | 29.3
2019-10-01 | 10:07 | 7.5 | 243.9102 | 0.02 | 1.02 | -0.52 | 0.48 | -0.45 | 0.55 | 75.2 | 25.39
2019-10-01 | 10:07 | 7.6016 | 244.0118 | -0.07 | 0.93 | -0.46 | 0.54 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 7.6992 | 244.1094 | -0.08 | 0.92 | -0.44 | 0.56 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 7.8086 | 244.2188 | -0.1 | 0.9 | -0.43 | 0.57 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:07 | 7.9102 | 244.3204 | -0.1 | 0.9 | -0.43 | 0.57 | -0.41 | 0.59 | 74.22 | 25.39
2019-10-01 | 10:07 | 8.0117 | 244.4219 | 0 | 1 | -0.52 | 0.48 | -0.45 | 0.55 | 74.22 | 25.39
2019-10-01 | 10:07 | 8.1094 | 244.5196 | 0.02 | 1.02 | -0.53 | 0.47 | -0.44 | 0.56 | 75.2 | 28.32
2019-10-01 | 10:07 | 8.2188 | 244.629 | 0.02 | 1.02 | -0.53 | 0.47 | -0.45 | 0.55 | 75.2 | 29.3
2019-10-01 | 10:07 | 8.3203 | 244.7305 | 0.03 | 1.03 | -0.54 | 0.46 | -0.45 | 0.55 | 76.17 | 25.39
2019-10-01 | 10:07 | 8.4219 | 244.8321 | 0.02 | 1.02 | -0.55 | 0.45 | -0.46 | 0.54 | 74.22 | 26.37
2019-10-01 | 10:07 | 8.5195 | 244.9297 | 0.03 | 1.03 | -0.55 | 0.45 | -0.45 | 0.55 | 75.2 | 26.37
2019-10-01 | 10:07 | 8.6289 | 245.0391 | 0.03 | 1.03 | -0.54 | 0.46 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:07 | 8.7305 | 245.1407 | 0.02 | 1.02 | -0.54 | 0.46 | -0.45 | 0.55 | 76.17 | 26.37
2019-10-01 | 10:07 | 8.8281 | 245.2383 | 0.04 | 1.04 | -0.54 | 0.46 | -0.44 | 0.56 | 76.17 | 27.34
2019-10-01 | 10:07 | 8.9297 | 245.3399 | 0.04 | 1.04 | -0.53 | 0.47 | -0.45 | 0.55 | 77.15 | 29.3
2019-10-01 | 10:07 | 9.0391 | 245.4493 | -0.02 | 0.98 | -0.49 | 0.51 | -0.44 | 0.56 | 77.15 | 53.71
2019-10-01 | 10:07 | 9.1406 | 245.5508 | -0.08 | 0.92 | -0.45 | 0.55 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 9.2383 | 245.6485 | -0.08 | 0.92 | -0.45 | 0.55 | -0.41 | 0.59 | 76.17 | 26.37
2019-10-01 | 10:07 | 9.3516 | 245.7618 | -0.1 | 0.9 | -0.45 | 0.55 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:07 | 9.4492 | 245.8594 | -0.04 | 0.96 | -0.5 | 0.5 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:07 | 9.5508 | 245.961 | 0 | 1 | -0.54 | 0.46 | -0.44 | 0.56 | 76.17 | 50.78
2019-10-01 | 10:07 | 9.6484 | 246.0586 | 0.02 | 1.02 | -0.55 | 0.45 | -0.46 | 0.54 | 77.15 | 28.32
2019-10-01 | 10:07 | 9.7617 | 246.1719 | 0.02 | 1.02 | -0.55 | 0.45 | -0.45 | 0.55 | 75.2 | 27.34
2019-10-01 | 10:07 | 9.8594 | 246.2696 | 0.02 | 1.02 | -0.54 | 0.46 | -0.45 | 0.55 | 76.17 | 27.34
2019-10-01 | 10:07 | 9.9609 | 246.3711 | 0.03 | 1.03 | -0.55 | 0.45 | -0.46 | 0.54 | 77.15 | 25.39
2019-10-01 | 10:07 | 10.0586 | 246.4688 | 0.03 | 1.03 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 24.41
2019-10-01 | 10:07 | 10.1719 | 246.5821 | 0.04 | 1.04 | -0.54 | 0.46 | -0.46 | 0.54 | 76.17 | 26.37
2019-10-01 | 10:07 | 10.2695 | 246.6797 | 0.03 | 1.03 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 26.37
2019-10-01 | 10:07 | 10.3711 | 246.7813 | 0.04 | 1.04 | -0.55 | 0.45 | -0.46 | 0.54 | 74.22 | 28.32
2019-10-01 | 10:07 | 10.4805 | 246.8907 | 0.03 | 1.03 | -0.56 | 0.44 | -0.45 | 0.55 | 77.15 | 29.3
2019-10-01 | 10:07 | 10.5781 | 246.9883 | -0.05 | 0.95 | -0.47 | 0.53 | -0.43 | 0.57 | 77.15 | 27.34
2019-10-01 | 10:07 | 10.6797 | 247.0899 | -0.07 | 0.93 | -0.46 | 0.54 | -0.42 | 0.58 | 77.15 | 25.39
2019-10-01 | 10:07 | 10.7812 | 247.1915 | -0.1 | 0.9 | -0.46 | 0.54 | -0.42 | 0.58 | 76.17 | 25.39
2019-10-01 | 10:07 | 10.8906 | 247.3008 | -0.09 | 0.91 | -0.45 | 0.55 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:07 | 10.9883 | 247.3985 | 0 | 1 | -0.55 | 0.45 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:07 | 11.0898 | 247.5 | 0.01 | 1.01 | -0.55 | 0.45 | -0.45 | 0.55 | 75.2 | 27.34
2019-10-01 | 10:07 | 11.1914 | 247.6016 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 78.12 | 29.3
2019-10-01 | 10:07 | 11.3008 | 247.711 | 0.04 | 1.04 | -0.55 | 0.45 | -0.43 | 0.57 | 75.2 | 28.32
2019-10-01 | 10:07 | 11.3984 | 247.8086 | 0.02 | 1.02 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:07 | 11.5 | 247.9102 | 0.03 | 1.03 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 24.41
2019-10-01 | 10:07 | 11.6016 | 248.0118 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 74.22 | 24.41
2019-10-01 | 10:07 | 11.7109 | 248.1211 | 0.02 | 1.02 | -0.55 | 0.45 | -0.44 | 0.56 | 76.17 | 25.39
2019-10-01 | 10:07 | 11.8086 | 248.2188 | 0.02 | 1.02 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 24.41
2019-10-01 | 10:07 | 11.9102 | 248.3204 | 0.04 | 1.04 | -0.54 | 0.46 | -0.45 | 0.55 | 76.17 | 29.3
2019-10-01 | 10:07 | 12.0195 | 248.4297 | 0 | 1 | -0.5 | 0.5 | -0.45 | 0.55 | 75.2 | 29.3
2019-10-01 | 10:07 | 12.1211 | 248.5313 | -0.06 | 0.94 | -0.47 | 0.53 | -0.43 | 0.57 | 76.17 | 26.37
2019-10-01 | 10:07 | 12.2188 | 248.629 | -0.08 | 0.92 | -0.45 | 0.55 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:07 | 12.3281 | 248.7383 | -0.09 | 0.91 | -0.45 | 0.55 | -0.41 | 0.59 | 77.15 | 26.37
2019-10-01 | 10:07 | 12.4297 | 248.8399 | -0.09 | 0.91 | -0.46 | 0.54 | -0.39 | 0.61 | 75.2 | 26.37
2019-10-01 | 10:07 | 12.5312 | 248.9415 | 0 | 1 | -0.54 | 0.46 | -0.43 | 0.57 | 75.2 | 24.41
2019-10-01 | 10:07 | 12.6289 | 249.0391 | 0.02 | 1.02 | -0.55 | 0.45 | -0.44 | 0.56 | 77.15 | 27.34
2019-10-01 | 10:07 | 12.7305 | 249.1407 | 0.02 | 1.02 | -0.55 | 0.45 | -0.42 | 0.58 | 75.2 | 28.32
2019-10-01 | 10:07 | 12.8398 | 249.25 | 0.02 | 1.02 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 43.95
2019-10-01 | 10:07 | 12.9414 | 249.3516 | 0.03 | 1.03 | -0.55 | 0.45 | -0.43 | 0.57 | 76.17 | 25.39
2019-10-01 | 10:07 | 13.0508 | 249.461 | 0.04 | 1.04 | -0.55 | 0.45 | -0.43 | 0.57 | 77.15 | 26.37
2019-10-01 | 10:07 | 13.1484 | 249.5586 | 0.03 | 1.03 | -0.55 | 0.45 | -0.44 | 0.56 | 76.17 | 26.37
2019-10-01 | 10:07 | 13.25 | 249.6602 | 0.03 | 1.03 | -0.54 | 0.46 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:07 | 13.3516 | 249.7618 | 0.02 | 1.02 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 49.8
2019-10-01 | 10:07 | 13.4609 | 249.8711 | 0.04 | 1.04 | -0.54 | 0.46 | -0.45 | 0.55 | 78.12 | 29.3
2019-10-01 | 10:07 | 13.5586 | 249.9688 | -0.04 | 0.96 | -0.47 | 0.53 | -0.43 | 0.57 | 75.2 | 27.34
2019-10-01 | 10:07 | 13.6602 | 250.0704 | -0.07 | 0.93 | -0.47 | 0.53 | -0.42 | 0.58 | 75.2 | 26.37
2019-10-01 | 10:07 | 13.7617 | 250.1719 | -0.1 | 0.9 | -0.45 | 0.55 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:07 | 13.8711 | 250.2813 | -0.09 | 0.91 | -0.44 | 0.56 | -0.4 | 0.6 | 75.2 | 24.41
2019-10-01 | 10:07 | 13.9688 | 250.379 | 0 | 1 | -0.53 | 0.47 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 14.0703 | 250.4805 | 0.02 | 1.02 | -0.53 | 0.47 | -0.42 | 0.58 | 76.17 | 26.37
2019-10-01 | 10:07 | 14.1797 | 250.5899 | 0.01 | 1.01 | -0.54 | 0.46 | -0.43 | 0.57 | 75.2 | 28.32
2019-10-01 | 10:07 | 14.2812 | 250.6915 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 28.32
2019-10-01 | 10:07 | 14.3789 | 250.7891 | 0.01 | 1.01 | -0.54 | 0.46 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 14.4805 | 250.8907 | 0.03 | 1.03 | -0.53 | 0.47 | -0.44 | 0.56 | 75.2 | 25.39
2019-10-01 | 10:07 | 14.5898 | 251 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 77.15 | 25.39
2019-10-01 | 10:07 | 14.6914 | 251.1016 | 0.03 | 1.03 | -0.55 | 0.45 | -0.44 | 0.56 | 75.2 | 24.41
2019-10-01 | 10:07 | 14.7891 | 251.1993 | 0.03 | 1.03 | -0.53 | 0.47 | -0.44 | 0.56 | 78.12 | 26.37
2019-10-01 | 10:07 | 14.8906 | 251.3008 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 27.34
2019-10-01 | 10:07 | 14.9883 | 251.3985 | 0.01 | 1.01 | -0.53 | 0.47 | -0.43 | 0.57 | 75.2 | 29.3
2019-10-01 | 10:07 | 15.1016 | 251.5118 | -0.05 | 0.95 | -0.48 | 0.52 | -0.43 | 0.57 | 76.17 | 26.37
2019-10-01 | 10:07 | 15.1992 | 251.6094 | -0.09 | 0.91 | -0.46 | 0.54 | -0.41 | 0.59 | 76.17 | 26.37
2019-10-01 | 10:07 | 15.3086 | 251.7188 | -0.09 | 0.91 | -0.45 | 0.55 | -0.41 | 0.59 | 75.2 | 24.41
2019-10-01 | 10:07 | 15.4102 | 251.8204 | -0.1 | 0.9 | -0.45 | 0.55 | -0.41 | 0.59 | 75.2 | 24.41
2019-10-01 | 10:07 | 15.5117 | 251.9219 | 0.01 | 1.01 | -0.55 | 0.45 | -0.43 | 0.57 | 76.17 | 25.39
2019-10-01 | 10:07 | 15.6094 | 252.0196 | 0.01 | 1.01 | -0.54 | 0.46 | -0.43 | 0.57 | 75.2 | 31.25
2019-10-01 | 10:07 | 15.7188 | 252.129 | 0.02 | 1.02 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 29.3
2019-10-01 | 10:07 | 15.8203 | 252.2305 | 0.02 | 1.02 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 28.32
2019-10-01 | 10:07 | 15.9219 | 252.3321 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 26.37
2019-10-01 | 10:07 | 16.0195 | 252.4297 | 0.03 | 1.03 | -0.55 | 0.45 | -0.42 | 0.58 | 76.17 | 24.41
2019-10-01 | 10:07 | 16.1289 | 252.5391 | 0.03 | 1.03 | -0.54 | 0.46 | -0.41 | 0.59 | 75.2 | 24.41
2019-10-01 | 10:07 | 16.2305 | 252.6407 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 76.17 | 25.39
2019-10-01 | 10:07 | 16.3281 | 252.7383 | 0.03 | 1.03 | -0.55 | 0.45 | -0.45 | 0.55 | 77.15 | 26.37
2019-10-01 | 10:07 | 16.4297 | 252.8399 | 0.04 | 1.04 | -0.54 | 0.46 | -0.44 | 0.56 | 76.17 | 28.32
2019-10-01 | 10:07 | 16.5391 | 252.9493 | -0.02 | 0.98 | -0.5 | 0.5 | -0.41 | 0.59 | 76.17 | 28.32
2019-10-01 | 10:07 | 16.6406 | 253.0508 | -0.08 | 0.92 | -0.46 | 0.54 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:07 | 16.7383 | 253.1485 | -0.07 | 0.93 | -0.46 | 0.54 | -0.42 | 0.58 | 76.17 | 25.39
2019-10-01 | 10:07 | 16.8516 | 253.2618 | -0.08 | 0.92 | -0.45 | 0.55 | -0.4 | 0.6 | 75.2 | 24.41
2019-10-01 | 10:07 | 16.9492 | 253.3594 | -0.04 | 0.96 | -0.49 | 0.51 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 17.0508 | 253.461 | 0.01 | 1.01 | -0.54 | 0.46 | -0.43 | 0.57 | 75.2 | 24.41
2019-10-01 | 10:07 | 17.1484 | 253.5586 | 0.02 | 1.02 | -0.55 | 0.45 | -0.43 | 0.57 | 76.17 | 28.32
2019-10-01 | 10:07 | 17.2617 | 253.6719 | 0.02 | 1.02 | -0.54 | 0.46 | -0.43 | 0.57 | 77.15 | 29.3
2019-10-01 | 10:07 | 17.3594 | 253.7696 | 0.03 | 1.03 | -0.54 | 0.46 | -0.42 | 0.58 | 74.22 | 26.37
2019-10-01 | 10:07 | 17.4609 | 253.8711 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 17.5586 | 253.9688 | 0.04 | 1.04 | -0.53 | 0.47 | -0.43 | 0.57 | 76.17 | 25.39
2019-10-01 | 10:07 | 17.6719 | 254.0821 | 0.03 | 1.03 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:07 | 17.7695 | 254.1797 | 0.03 | 1.03 | -0.55 | 0.45 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 17.8711 | 254.2813 | 0.03 | 1.03 | -0.55 | 0.45 | -0.44 | 0.56 | 77.15 | 50.78
2019-10-01 | 10:07 | 17.9805 | 254.3907 | 0.03 | 1.03 | -0.53 | 0.47 | -0.43 | 0.57 | 75.2 | 28.32
2019-10-01 | 10:07 | 18.0781 | 254.4883 | -0.05 | 0.95 | -0.46 | 0.54 | -0.41 | 0.59 | 76.17 | 29.3
2019-10-01 | 10:07 | 18.1797 | 254.5899 | -0.08 | 0.92 | -0.45 | 0.55 | -0.39 | 0.61 | 76.17 | 26.37
2019-10-01 | 10:07 | 18.2812 | 254.6915 | -0.08 | 0.92 | -0.45 | 0.55 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:07 | 18.3906 | 254.8008 | -0.09 | 0.91 | -0.43 | 0.57 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:07 | 18.4883 | 254.8985 | 0.01 | 1.01 | -0.54 | 0.46 | -0.39 | 0.61 | 77.15 | 25.39
2019-10-01 | 10:07 | 18.5898 | 255 | 0.02 | 1.02 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 26.37
2019-10-01 | 10:07 | 18.6914 | 255.1016 | 0.02 | 1.02 | -0.54 | 0.46 | -0.41 | 0.59 | 76.17 | 28.32
2019-10-01 | 10:07 | 18.8008 | 255.211 | 0.03 | 1.03 | -0.53 | 0.47 | -0.42 | 0.58 | 76.17 | 28.32
2019-10-01 | 10:07 | 18.8984 | 255.3086 | 0.02 | 1.02 | -0.53 | 0.47 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 19.0117 | 255.4219 | 0.02 | 1.02 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:07 | 19.1094 | 255.5196 | 0.03 | 1.03 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:07 | 19.2109 | 255.6211 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 77.15 | 26.37
2019-10-01 | 10:07 | 19.3086 | 255.7188 | 0.03 | 1.03 | -0.54 | 0.46 | -0.43 | 0.57 | 75.2 | 25.39
2019-10-01 | 10:07 | 19.4102 | 255.8204 | 0.03 | 1.03 | -0.54 | 0.46 | -0.42 | 0.58 | 75.2 | 27.34
2019-10-01 | 10:07 | 19.5195 | 255.9297 | 0.01 | 1.01 | -0.52 | 0.48 | -0.42 | 0.58 | 77.15 | 29.3
2019-10-01 | 10:07 | 19.6211 | 256.0313 | -0.06 | 0.94 | -0.47 | 0.53 | -0.41 | 0.59 | 75.2 | 27.34
2019-10-01 | 10:07 | 19.7188 | 256.129 | -0.08 | 0.92 | -0.44 | 0.56 | -0.4 | 0.6 | 75.2 | 27.34
2019-10-01 | 10:07 | 19.8203 | 256.2305 | -0.1 | 0.9 | -0.45 | 0.55 | -0.39 | 0.61 | 74.22 | 24.41
2019-10-01 | 10:07 | 19.9297 | 256.3399 | -0.09 | 0.91 | -0.45 | 0.55 | -0.39 | 0.61 | 74.22 | 25.39
2019-10-01 | 10:07 | 20.0312 | 256.4415 | 0.01 | 1.01 | -0.53 | 0.47 | -0.4 | 0.6 | 74.22 | 25.39
2019-10-01 | 10:07 | 20.1289 | 256.5391 | 0.03 | 1.03 | -0.53 | 0.47 | -0.41 | 0.59 | 74.22 | 41.99
2019-10-01 | 10:07 | 20.2383 | 256.6485 | 0.02 | 1.02 | -0.52 | 0.48 | -0.4 | 0.6 | 74.22 | 28.32
2019-10-01 | 10:07 | 20.3398 | 256.75 | 0.03 | 1.03 | -0.53 | 0.47 | -0.39 | 0.61 | 75.2 | 29.3
2019-10-01 | 10:07 | 20.4414 | 256.8516 | 0.04 | 1.04 | -0.53 | 0.47 | -0.41 | 0.59 | 74.22 | 25.39
2019-10-01 | 10:07 | 20.5508 | 256.961 | 0.03 | 1.03 | -0.52 | 0.48 | -0.39 | 0.61 | 74.22 | 25.39
2019-10-01 | 10:07 | 20.6484 | 257.0586 | 0.04 | 1.04 | -0.54 | 0.46 | -0.42 | 0.58 | 75.2 | 25.39
2019-10-01 | 10:07 | 20.75 | 257.1602 | 0.02 | 1.02 | -0.53 | 0.47 | -0.43 | 0.57 | 75.2 | 24.41
2019-10-01 | 10:07 | 20.8516 | 257.2618 | 0.04 | 1.04 | -0.52 | 0.48 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:07 | 20.9609 | 257.3711 | 0.03 | 1.03 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 28.32
2019-10-01 | 10:07 | 21.0586 | 257.4688 | -0.03 | 0.97 | -0.47 | 0.53 | -0.41 | 0.59 | 78.12 | 29.3
2019-10-01 | 10:07 | 21.1602 | 257.5704 | -0.07 | 0.93 | -0.45 | 0.55 | -0.41 | 0.59 | 76.17 | 26.37
2019-10-01 | 10:07 | 21.2695 | 257.6797 | -0.09 | 0.91 | -0.44 | 0.56 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:07 | 21.3711 | 257.7813 | -0.08 | 0.92 | -0.45 | 0.55 | -0.38 | 0.62 | 77.15 | 25.39
2019-10-01 | 10:07 | 21.4688 | 257.879 | 0 | 1 | -0.51 | 0.49 | -0.41 | 0.59 | 75.2 | 24.41
2019-10-01 | 10:07 | 21.5703 | 257.9805 | 0.02 | 1.02 | -0.52 | 0.48 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 21.6797 | 258.0899 | 0.03 | 1.03 | -0.52 | 0.48 | -0.41 | 0.59 | 77.15 | 29.3
2019-10-01 | 10:07 | 21.7812 | 258.1915 | 0.03 | 1.03 | -0.53 | 0.47 | -0.4 | 0.6 | 77.15 | 29.3
2019-10-01 | 10:07 | 21.8789 | 258.2891 | 0.04 | 1.04 | -0.53 | 0.47 | -0.4 | 0.6 | 76.17 | 45.9
2019-10-01 | 10:07 | 21.9805 | 258.3907 | 0.02 | 1.02 | -0.52 | 0.48 | -0.41 | 0.59 | 75.2 | 25.39
2019-10-01 | 10:07 | 22.0898 | 258.5 | 0.03 | 1.03 | -0.53 | 0.47 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:07 | 22.1914 | 258.6016 | 0.03 | 1.03 | -0.52 | 0.48 | -0.4 | 0.6 | 76.17 | 25.39
2019-10-01 | 10:07 | 22.2891 | 258.6993 | 0.03 | 1.03 | -0.53 | 0.47 | -0.4 | 0.6 | 76.17 | 25.39
2019-10-01 | 10:07 | 22.3906 | 258.8008 | 0.03 | 1.03 | -0.53 | 0.47 | -0.42 | 0.58 | 77.15 | 26.37
2019-10-01 | 10:07 | 22.5 | 258.9102 | 0.02 | 1.02 | -0.5 | 0.5 | -0.41 | 0.59 | 76.17 | 29.3
2019-10-01 | 10:07 | 22.6016 | 259.0118 | -0.05 | 0.95 | -0.45 | 0.55 | -0.4 | 0.6 | 78.12 | 27.34
2019-10-01 | 10:07 | 22.6992 | 259.1094 | -0.08 | 0.92 | -0.45 | 0.55 | -0.4 | 0.6 | 76.17 | 25.39
2019-10-01 | 10:07 | 22.8086 | 259.2188 | -0.08 | 0.92 | -0.44 | 0.56 | -0.4 | 0.6 | 75.2 | 26.37
2019-10-01 | 10:07 | 22.9102 | 259.3204 | -0.09 | 0.91 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 23.0117 | 259.4219 | 0.02 | 1.02 | -0.53 | 0.47 | -0.39 | 0.61 | 75.2 | 24.41
2019-10-01 | 10:07 | 23.1094 | 259.5196 | 0.01 | 1.01 | -0.52 | 0.48 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:07 | 23.2188 | 259.629 | 0.02 | 1.02 | -0.52 | 0.48 | -0.41 | 0.59 | 75.2 | 28.32
2019-10-01 | 10:07 | 23.3203 | 259.7305 | 0.04 | 1.04 | -0.52 | 0.48 | -0.4 | 0.6 | 76.17 | 29.3
2019-10-01 | 10:07 | 23.4219 | 259.8321 | 0.02 | 1.02 | -0.53 | 0.47 | -0.41 | 0.59 | 76.17 | 25.39
2019-10-01 | 10:07 | 23.5195 | 259.9297 | 0.04 | 1.04 | -0.52 | 0.48 | -0.41 | 0.59 | 78.12 | 26.37
2019-10-01 | 10:07 | 23.6289 | 260.0391 | 0.03 | 1.03 | -0.52 | 0.48 | -0.41 | 0.59 | 78.12 | 26.37
2019-10-01 | 10:07 | 23.7305 | 260.1407 | 0.04 | 1.04 | -0.53 | 0.47 | -0.41 | 0.59 | 77.15 | 24.41
2019-10-01 | 10:07 | 23.8281 | 260.2383 | 0.03 | 1.03 | -0.52 | 0.48 | -0.41 | 0.59 | 77.15 | 26.37
2019-10-01 | 10:07 | 23.9414 | 260.3516 | 0.04 | 1.04 | -0.52 | 0.48 | -0.41 | 0.59 | 75.2 | 28.32
2019-10-01 | 10:07 | 24.0391 | 260.4493 | -0.02 | 0.98 | -0.49 | 0.51 | -0.41 | 0.59 | 77.15 | 30.27
2019-10-01 | 10:07 | 24.1406 | 260.5508 | -0.06 | 0.94 | -0.45 | 0.55 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:07 | 24.2383 | 260.6485 | -0.08 | 0.92 | -0.45 | 0.55 | -0.39 | 0.61 | 77.15 | 27.34
2019-10-01 | 10:07 | 24.3516 | 260.7618 | -0.09 | 0.91 | -0.42 | 0.58 | -0.38 | 0.62 | 77.15 | 26.37
2019-10-01 | 10:07 | 24.4492 | 260.8594 | -0.08 | 0.92 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 24.5508 | 260.961 | 0.02 | 1.02 | -0.52 | 0.48 | -0.41 | 0.59 | 78.12 | 25.39
2019-10-01 | 10:07 | 24.6484 | 261.0586 | 0.02 | 1.02 | -0.51 | 0.49 | -0.41 | 0.59 | 76.17 | 27.34
2019-10-01 | 10:07 | 24.7617 | 261.1719 | 0.03 | 1.03 | -0.52 | 0.48 | -0.39 | 0.61 | 78.12 | 28.32
2019-10-01 | 10:07 | 24.8594 | 261.2696 | 0.02 | 1.02 | -0.53 | 0.47 | -0.4 | 0.6 | 75.2 | 25.39
2019-10-01 | 10:07 | 24.9609 | 261.3711 | 0.03 | 1.03 | -0.53 | 0.47 | -0.39 | 0.61 | 78.12 | 26.37
2019-10-01 | 10:07 | 25.0586 | 261.4688 | 0.02 | 1.02 | -0.51 | 0.49 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:07 | 25.1719 | 261.5821 | 0.03 | 1.03 | -0.53 | 0.47 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:07 | 25.2695 | 261.6797 | 0.03 | 1.03 | -0.52 | 0.48 | -0.39 | 0.61 | 76.17 | 26.37
2019-10-01 | 10:07 | 25.3711 | 261.7813 | 0.04 | 1.04 | -0.52 | 0.48 | -0.38 | 0.62 | 75.2 | 26.37
2019-10-01 | 10:07 | 25.4805 | 261.8907 | 0.04 | 1.04 | -0.51 | 0.49 | -0.4 | 0.6 | 78.12 | 29.3
2019-10-01 | 10:07 | 25.5781 | 261.9883 | -0.04 | 0.96 | -0.46 | 0.54 | -0.39 | 0.61 | 77.15 | 28.32
2019-10-01 | 10:07 | 25.6797 | 262.0899 | -0.06 | 0.94 | -0.44 | 0.56 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:07 | 25.7812 | 262.1915 | -0.07 | 0.93 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 25.8906 | 262.3008 | -0.08 | 0.92 | -0.43 | 0.57 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 25.9883 | 262.3985 | 0 | 1 | -0.51 | 0.49 | -0.37 | 0.63 | 75.2 | 26.37
2019-10-01 | 10:07 | 26.0898 | 262.5 | 0.03 | 1.03 | -0.5 | 0.5 | -0.38 | 0.62 | 75.2 | 24.41
2019-10-01 | 10:07 | 26.1914 | 262.6016 | 0.03 | 1.03 | -0.51 | 0.49 | -0.38 | 0.62 | 77.15 | 28.32
2019-10-01 | 10:07 | 26.3008 | 262.711 | 0.02 | 1.02 | -0.5 | 0.5 | -0.39 | 0.61 | 75.2 | 28.32
2019-10-01 | 10:07 | 26.3984 | 262.8086 | 0.03 | 1.03 | -0.51 | 0.49 | -0.39 | 0.61 | 75.2 | 26.37
2019-10-01 | 10:07 | 26.5117 | 262.9219 | 0.04 | 1.04 | -0.51 | 0.49 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 26.6094 | 263.0196 | 0.03 | 1.03 | -0.53 | 0.47 | -0.39 | 0.61 | 75.2 | 23.44
2019-10-01 | 10:07 | 26.7109 | 263.1211 | 0.02 | 1.02 | -0.52 | 0.48 | -0.38 | 0.62 | 76.17 | 24.41
2019-10-01 | 10:07 | 26.8086 | 263.2188 | 0.03 | 1.03 | -0.52 | 0.48 | -0.39 | 0.61 | 77.15 | 24.41
2019-10-01 | 10:07 | 26.9102 | 263.3204 | 0.03 | 1.03 | -0.52 | 0.48 | -0.39 | 0.61 | 77.15 | 29.3
2019-10-01 | 10:07 | 27.0195 | 263.4297 | 0 | 1 | -0.48 | 0.52 | -0.39 | 0.61 | 76.17 | 29.3
2019-10-01 | 10:07 | 27.1211 | 263.5313 | -0.06 | 0.94 | -0.48 | 0.52 | -0.38 | 0.62 | 76.17 | 20.51
2019-10-01 | 10:07 | 27.2305 | 263.6407 | -0.08 | 0.92 | -0.45 | 0.55 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 27.3281 | 263.7383 | -0.08 | 0.92 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 27.4297 | 263.8399 | -0.1 | 0.9 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 27.5312 | 263.9415 | 0 | 1 | -0.52 | 0.48 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 27.6406 | 264.0508 | 0.01 | 1.01 | -0.5 | 0.5 | -0.39 | 0.61 | 76.17 | 28.32
2019-10-01 | 10:07 | 27.7383 | 264.1485 | 0.02 | 1.02 | -0.5 | 0.5 | -0.38 | 0.62 | 77.15 | 29.3
2019-10-01 | 10:07 | 27.8398 | 264.25 | 0.03 | 1.03 | -0.51 | 0.49 | -0.38 | 0.62 | 76.17 | 27.34
2019-10-01 | 10:07 | 27.9414 | 264.3516 | 0.02 | 1.02 | -0.51 | 0.49 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:07 | 28.0508 | 264.461 | 0.03 | 1.03 | -0.51 | 0.49 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:07 | 28.1484 | 264.5586 | 0.03 | 1.03 | -0.51 | 0.49 | -0.39 | 0.61 | 77.15 | 25.39
2019-10-01 | 10:07 | 28.25 | 264.6602 | 0.02 | 1.02 | -0.5 | 0.5 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:07 | 28.3516 | 264.7618 | 0.04 | 1.04 | -0.5 | 0.5 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:07 | 28.4609 | 264.8711 | 0.03 | 1.03 | -0.5 | 0.5 | -0.39 | 0.61 | 77.15 | 28.32
2019-10-01 | 10:07 | 28.5586 | 264.9688 | -0.04 | 0.96 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:07 | 28.6602 | 265.0704 | -0.06 | 0.94 | -0.43 | 0.57 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 28.7695 | 265.1797 | -0.09 | 0.91 | -0.42 | 0.58 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 28.8711 | 265.2813 | -0.09 | 0.91 | -0.41 | 0.59 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 28.9688 | 265.379 | -0.01 | 0.99 | -0.49 | 0.51 | -0.38 | 0.62 | 78.12 | 25.39
2019-10-01 | 10:07 | 29.0703 | 265.4805 | 0 | 1 | -0.49 | 0.51 | -0.38 | 0.62 | 76.17 | 24.41
2019-10-01 | 10:07 | 29.1797 | 265.5899 | 0.02 | 1.02 | -0.5 | 0.5 | -0.38 | 0.62 | 76.17 | 28.32
2019-10-01 | 10:07 | 29.2812 | 265.6915 | 0.02 | 1.02 | -0.48 | 0.52 | -0.38 | 0.62 | 76.17 | 28.32
2019-10-01 | 10:07 | 29.3789 | 265.7891 | 0.02 | 1.02 | -0.49 | 0.51 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 29.4883 | 265.8985 | 0.02 | 1.02 | -0.5 | 0.5 | -0.36 | 0.64 | 77.15 | 24.41
2019-10-01 | 10:07 | 29.5898 | 266 | 0.03 | 1.03 | -0.5 | 0.5 | -0.38 | 0.62 | 76.17 | 25.39
2019-10-01 | 10:07 | 29.6992 | 266.1094 | 0.01 | 1.01 | -0.49 | 0.51 | -0.39 | 0.61 | 77.15 | 26.37
2019-10-01 | 10:07 | 29.7891 | 266.1993 | 0.03 | 1.03 | -0.49 | 0.51 | -0.4 | 0.6 | 78.12 | 26.37
2019-10-01 | 10:07 | 29.8906 | 266.3008 | 0.02 | 1.02 | -0.49 | 0.51 | -0.39 | 0.61 | 74.22 | 27.34
2019-10-01 | 10:07 | 30 | 266.4102 | 0.02 | 1.02 | -0.47 | 0.53 | -0.39 | 0.61 | 76.17 | 28.32
2019-10-01 | 10:07 | 30.1016 | 266.5118 | -0.06 | 0.94 | -0.42 | 0.58 | -0.37 | 0.63 | 78.12 | 33.2
2019-10-01 | 10:07 | 30.1992 | 266.6094 | -0.08 | 0.92 | -0.42 | 0.58 | -0.36 | 0.64 | 75.2 | 26.37
2019-10-01 | 10:07 | 30.3086 | 266.7188 | -0.09 | 0.91 | -0.41 | 0.59 | -0.36 | 0.64 | 75.2 | 26.37
2019-10-01 | 10:07 | 30.4102 | 266.8204 | -0.1 | 0.9 | -0.41 | 0.59 | -0.35 | 0.65 | 78.12 | 25.39
2019-10-01 | 10:07 | 30.5117 | 266.9219 | -0.01 | 0.99 | -0.5 | 0.5 | -0.37 | 0.63 | 77.15 | 25.39
2019-10-01 | 10:07 | 30.6094 | 267.0196 | 0.01 | 1.01 | -0.47 | 0.53 | -0.37 | 0.63 | 74.22 | 25.39
2019-10-01 | 10:07 | 30.7188 | 267.129 | 0.01 | 1.01 | -0.49 | 0.51 | -0.37 | 0.63 | 77.15 | 28.32
2019-10-01 | 10:07 | 30.8203 | 267.2305 | 0.01 | 1.01 | -0.48 | 0.52 | -0.37 | 0.63 | 74.22 | 27.34
2019-10-01 | 10:07 | 30.9219 | 267.3321 | 0.03 | 1.03 | -0.48 | 0.52 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:07 | 31.0195 | 267.4297 | 0.02 | 1.02 | -0.48 | 0.52 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 31.1289 | 267.5391 | 0.02 | 1.02 | -0.48 | 0.52 | -0.38 | 0.62 | 76.17 | 24.41
2019-10-01 | 10:07 | 31.2305 | 267.6407 | 0.01 | 1.01 | -0.49 | 0.51 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 31.3398 | 267.75 | 0.01 | 1.01 | -0.49 | 0.51 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 31.4414 | 267.8516 | 0.03 | 1.03 | -0.48 | 0.52 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:07 | 31.5391 | 267.9493 | -0.03 | 0.97 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 29.3
2019-10-01 | 10:07 | 31.6406 | 268.0508 | -0.07 | 0.93 | -0.41 | 0.59 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:07 | 31.7383 | 268.1485 | -0.08 | 0.92 | -0.41 | 0.59 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:07 | 31.8516 | 268.2618 | -0.09 | 0.91 | -0.4 | 0.6 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 31.9492 | 268.3594 | -0.09 | 0.91 | -0.39 | 0.61 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 32.0508 | 268.461 | 0 | 1 | -0.48 | 0.52 | -0.37 | 0.63 | 77.15 | 25.39
2019-10-01 | 10:07 | 32.1484 | 268.5586 | 0.02 | 1.02 | -0.47 | 0.53 | -0.37 | 0.63 | 77.15 | 28.32
2019-10-01 | 10:07 | 32.2617 | 268.6719 | 0.01 | 1.01 | -0.46 | 0.54 | -0.37 | 0.63 | 75.2 | 28.32
2019-10-01 | 10:07 | 32.3594 | 268.7696 | 0.01 | 1.01 | -0.47 | 0.53 | -0.37 | 0.63 | 76.17 | 47.85
2019-10-01 | 10:07 | 32.4609 | 268.8711 | 0.03 | 1.03 | -0.47 | 0.53 | -0.37 | 0.63 | 75.2 | 27.34
2019-10-01 | 10:07 | 32.5703 | 268.9805 | 0.02 | 1.02 | -0.48 | 0.52 | -0.37 | 0.63 | 77.15 | 26.37
2019-10-01 | 10:07 | 32.6719 | 269.0821 | 0.03 | 1.03 | -0.48 | 0.52 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:07 | 32.7695 | 269.1797 | 0.02 | 1.02 | -0.48 | 0.52 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 32.8711 | 269.2813 | 0.03 | 1.03 | -0.49 | 0.51 | -0.36 | 0.64 | 77.15 | 27.34
2019-10-01 | 10:07 | 32.9805 | 269.3907 | 0.02 | 1.02 | -0.48 | 0.52 | -0.38 | 0.62 | 76.17 | 28.32
2019-10-01 | 10:07 | 33.0781 | 269.4883 | -0.05 | 0.95 | -0.42 | 0.58 | -0.37 | 0.63 | 76.17 | 27.34
2019-10-01 | 10:07 | 33.1797 | 269.5899 | -0.07 | 0.93 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 26.37
2019-10-01 | 10:07 | 33.2812 | 269.6915 | -0.08 | 0.92 | -0.4 | 0.6 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:07 | 33.3906 | 269.8008 | -0.08 | 0.92 | -0.41 | 0.59 | -0.36 | 0.64 | 77.15 | 24.41
2019-10-01 | 10:07 | 33.5 | 269.9102 | -0.01 | 0.99 | -0.46 | 0.54 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 33.5898 | 270 | 0.01 | 1.01 | -0.47 | 0.53 | -0.36 | 0.64 | 77.15 | 25.39
2019-10-01 | 10:07 | 33.6992 | 270.1094 | 0.03 | 1.03 | -0.45 | 0.55 | -0.37 | 0.63 | 77.15 | 28.32
2019-10-01 | 10:07 | 33.8008 | 270.211 | 0.02 | 1.02 | -0.45 | 0.55 | -0.38 | 0.62 | 77.15 | 28.32
2019-10-01 | 10:07 | 33.8984 | 270.3086 | 0.02 | 1.02 | -0.47 | 0.53 | -0.36 | 0.64 | 78.12 | 27.34
2019-10-01 | 10:07 | 34.0117 | 270.4219 | 0.02 | 1.02 | -0.46 | 0.54 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:07 | 34.1094 | 270.5196 | 0.01 | 1.01 | -0.46 | 0.54 | -0.37 | 0.63 | 77.15 | 24.41
2019-10-01 | 10:07 | 34.2109 | 270.6211 | 0.03 | 1.03 | -0.46 | 0.54 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 34.3086 | 270.7188 | 0.03 | 1.03 | -0.47 | 0.53 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 34.4219 | 270.8321 | 0.04 | 1.04 | -0.46 | 0.54 | -0.38 | 0.62 | 76.17 | 27.34
2019-10-01 | 10:07 | 34.5195 | 270.9297 | 0.01 | 1.01 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 29.3
2019-10-01 | 10:07 | 34.6211 | 271.0313 | -0.05 | 0.95 | -0.4 | 0.6 | -0.37 | 0.63 | 76.17 | 51.76
2019-10-01 | 10:07 | 34.7305 | 271.1407 | -0.08 | 0.92 | -0.4 | 0.6 | -0.37 | 0.63 | 77.15 | 26.37
2019-10-01 | 10:07 | 34.8281 | 271.2383 | -0.07 | 0.93 | -0.39 | 0.61 | -0.34 | 0.66 | 77.15 | 25.39
2019-10-01 | 10:07 | 34.9297 | 271.3399 | -0.08 | 0.92 | -0.38 | 0.62 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:07 | 35.0312 | 271.4415 | 0 | 1 | -0.46 | 0.54 | -0.36 | 0.64 | 77.15 | 25.39
2019-10-01 | 10:07 | 35.1406 | 271.5508 | 0.03 | 1.03 | -0.44 | 0.56 | -0.38 | 0.62 | 77.15 | 26.37
2019-10-01 | 10:07 | 35.2383 | 271.6485 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 78.12 | 29.3
2019-10-01 | 10:07 | 35.3398 | 271.75 | 0.03 | 1.03 | -0.46 | 0.54 | -0.37 | 0.63 | 78.12 | 28.32
2019-10-01 | 10:07 | 35.4414 | 271.8516 | 0.02 | 1.02 | -0.44 | 0.56 | -0.36 | 0.64 | 76.17 | 26.37
2019-10-01 | 10:07 | 35.5508 | 271.961 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 35.6484 | 272.0586 | 0.02 | 1.02 | -0.46 | 0.54 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 35.75 | 272.1602 | 0.02 | 1.02 | -0.45 | 0.55 | -0.36 | 0.64 | 76.17 | 24.41
2019-10-01 | 10:07 | 35.8516 | 272.2618 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 35.9609 | 272.3711 | 0.03 | 1.03 | -0.45 | 0.55 | -0.37 | 0.63 | 79.1 | 29.3
2019-10-01 | 10:07 | 36.0586 | 272.4688 | -0.04 | 0.96 | -0.39 | 0.61 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:07 | 36.1602 | 272.5704 | -0.06 | 0.94 | -0.38 | 0.62 | -0.34 | 0.66 | 77.15 | 26.37
2019-10-01 | 10:07 | 36.2695 | 272.6797 | -0.08 | 0.92 | -0.38 | 0.62 | -0.34 | 0.66 | 78.12 | 27.34
2019-10-01 | 10:07 | 36.3711 | 272.7813 | -0.07 | 0.93 | -0.38 | 0.62 | -0.33 | 0.67 | 76.17 | 25.39
2019-10-01 | 10:07 | 36.4688 | 272.879 | -0.03 | 0.97 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 36.5703 | 272.9805 | 0.02 | 1.02 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:07 | 36.6797 | 273.0899 | 0.01 | 1.01 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:07 | 36.7812 | 273.1915 | 0.01 | 1.01 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:07 | 36.8789 | 273.2891 | 0.02 | 1.02 | -0.45 | 0.55 | -0.37 | 0.63 | 76.17 | 38.09
2019-10-01 | 10:07 | 36.9805 | 273.3907 | 0.03 | 1.03 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 26.37
2019-10-01 | 10:07 | 37.0898 | 273.5 | 0.03 | 1.03 | -0.43 | 0.57 | -0.37 | 0.63 | 77.15 | 24.41
2019-10-01 | 10:07 | 37.1914 | 273.6016 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:07 | 37.2891 | 273.6993 | 0.03 | 1.03 | -0.45 | 0.55 | -0.37 | 0.63 | 77.15 | 25.39
2019-10-01 | 10:07 | 37.3984 | 273.8086 | 0.03 | 1.03 | -0.45 | 0.55 | -0.36 | 0.64 | 76.17 | 36.13
2019-10-01 | 10:07 | 37.5 | 273.9102 | 0.02 | 1.02 | -0.43 | 0.57 | -0.37 | 0.63 | 77.15 | 28.32
2019-10-01 | 10:07 | 37.6016 | 274.0118 | -0.04 | 0.96 | -0.39 | 0.61 | -0.36 | 0.64 | 77.15 | 28.32
2019-10-01 | 10:07 | 37.6992 | 274.1094 | -0.06 | 0.94 | -0.37 | 0.63 | -0.35 | 0.65 | 77.15 | 26.37
2019-10-01 | 10:07 | 37.8086 | 274.2188 | -0.07 | 0.93 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 24.41
2019-10-01 | 10:07 | 37.9102 | 274.3204 | -0.08 | 0.92 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:07 | 38.0117 | 274.4219 | 0 | 1 | -0.45 | 0.55 | -0.35 | 0.65 | 78.12 | 25.39
2019-10-01 | 10:07 | 38.1094 | 274.5196 | 0.01 | 1.01 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:07 | 38.2188 | 274.629 | 0.02 | 1.02 | -0.43 | 0.57 | -0.36 | 0.64 | 77.15 | 28.32
2019-10-01 | 10:07 | 38.3203 | 274.7305 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 28.32
2019-10-01 | 10:07 | 38.4219 | 274.8321 | 0.03 | 1.03 | -0.42 | 0.58 | -0.35 | 0.65 | 77.15 | 25.39
2019-10-01 | 10:07 | 38.5312 | 274.9415 | 0.02 | 1.02 | -0.45 | 0.55 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:07 | 38.6289 | 275.0391 | 0.03 | 1.03 | -0.43 | 0.57 | -0.36 | 0.64 | 77.15 | 25.39
2019-10-01 | 10:07 | 38.7305 | 275.1407 | 0.04 | 1.04 | -0.43 | 0.57 | -0.36 | 0.64 | 78.12 | 27.34
2019-10-01 | 10:07 | 38.8281 | 275.2383 | 0.03 | 1.03 | -0.43 | 0.57 | -0.36 | 0.64 | 77.15 | 26.37
2019-10-01 | 10:07 | 38.9414 | 275.3516 | 0.03 | 1.03 | -0.44 | 0.56 | -0.36 | 0.64 | 76.17 | 27.34
2019-10-01 | 10:07 | 39.0391 | 275.4493 | -0.01 | 0.99 | -0.4 | 0.6 | -0.36 | 0.64 | 77.15 | 29.3
2019-10-01 | 10:07 | 39.1406 | 275.5508 | -0.06 | 0.94 | -0.38 | 0.62 | -0.34 | 0.66 | 77.15 | 26.37
2019-10-01 | 10:07 | 39.2383 | 275.6485 | -0.06 | 0.94 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 28.32
2019-10-01 | 10:07 | 39.3516 | 275.7618 | -0.08 | 0.92 | -0.37 | 0.63 | -0.35 | 0.65 | 75.2 | 24.41
2019-10-01 | 10:07 | 39.4609 | 275.8711 | -0.08 | 0.92 | -0.37 | 0.63 | -0.33 | 0.67 | 76.17 | 25.39
2019-10-01 | 10:07 | 39.5508 | 275.961 | 0.01 | 1.01 | -0.44 | 0.56 | -0.35 | 0.65 | 75.2 | 25.39
2019-10-01 | 10:07 | 39.6602 | 276.0704 | 0 | 1 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 49.8
2019-10-01 | 10:07 | 39.7617 | 276.1719 | 0.02 | 1.02 | -0.43 | 0.57 | -0.36 | 0.64 | 77.15 | 29.3
2019-10-01 | 10:07 | 39.8594 | 276.2696 | 0.02 | 1.02 | -0.43 | 0.57 | -0.36 | 0.64 | 76.17 | 28.32
2019-10-01 | 10:07 | 39.9609 | 276.3711 | 0.02 | 1.02 | -0.42 | 0.58 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 40.0703 | 276.4805 | 0.02 | 1.02 | -0.42 | 0.58 | -0.35 | 0.65 | 77.15 | 26.37
2019-10-01 | 10:07 | 40.1719 | 276.5821 | 0.02 | 1.02 | -0.43 | 0.57 | -0.36 | 0.64 | 76.17 | 24.41
2019-10-01 | 10:07 | 40.2695 | 276.6797 | 0.02 | 1.02 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:07 | 40.3711 | 276.7813 | 0.03 | 1.03 | -0.43 | 0.57 | -0.33 | 0.67 | 77.15 | 24.41
2019-10-01 | 10:07 | 40.4805 | 276.8907 | 0.04 | 1.04 | -0.42 | 0.58 | -0.35 | 0.65 | 77.15 | 28.32
2019-10-01 | 10:07 | 40.5781 | 276.9883 | -0.04 | 0.96 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 28.32
2019-10-01 | 10:07 | 40.6914 | 277.1016 | -0.06 | 0.94 | -0.37 | 0.63 | -0.33 | 0.67 | 77.15 | 25.39
2019-10-01 | 10:07 | 40.7891 | 277.1993 | -0.08 | 0.92 | -0.36 | 0.64 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:07 | 40.8906 | 277.3008 | -0.07 | 0.93 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 24.41
2019-10-01 | 10:07 | 40.9883 | 277.3985 | 0 | 1 | -0.42 | 0.58 | -0.33 | 0.67 | 76.17 | 26.37
2019-10-01 | 10:07 | 41.1016 | 277.5118 | 0.02 | 1.02 | -0.4 | 0.6 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 41.1992 | 277.6094 | 0.02 | 1.02 | -0.4 | 0.6 | -0.35 | 0.65 | 76.17 | 27.34
2019-10-01 | 10:07 | 41.3008 | 277.711 | 0.02 | 1.02 | -0.42 | 0.58 | -0.35 | 0.65 | 78.12 | 29.3
2019-10-01 | 10:07 | 41.3984 | 277.8086 | 0.03 | 1.03 | -0.41 | 0.59 | -0.34 | 0.66 | 75.2 | 27.34
2019-10-01 | 10:07 | 41.5117 | 277.9219 | 0.03 | 1.03 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 27.34
2019-10-01 | 10:07 | 41.6094 | 278.0196 | 0.03 | 1.03 | -0.42 | 0.58 | -0.34 | 0.66 | 77.15 | 26.37
2019-10-01 | 10:07 | 41.7109 | 278.1211 | 0.04 | 1.04 | -0.42 | 0.58 | -0.35 | 0.65 | 75.2 | 24.41
2019-10-01 | 10:07 | 41.8086 | 278.2188 | 0.03 | 1.03 | -0.42 | 0.58 | -0.36 | 0.64 | 77.15 | 25.39
2019-10-01 | 10:07 | 41.9219 | 278.3321 | 0.03 | 1.03 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:07 | 42.0195 | 278.4297 | 0.02 | 1.02 | -0.39 | 0.61 | -0.35 | 0.65 | 78.12 | 29.3
2019-10-01 | 10:07 | 42.1211 | 278.5313 | -0.04 | 0.96 | -0.37 | 0.63 | -0.33 | 0.67 | 77.15 | 28.32
2019-10-01 | 10:07 | 42.2305 | 278.6407 | -0.06 | 0.94 | -0.35 | 0.65 | -0.33 | 0.67 | 78.12 | 27.34
2019-10-01 | 10:07 | 42.3281 | 278.7383 | -0.07 | 0.93 | -0.36 | 0.64 | -0.32 | 0.68 | 77.15 | 26.37
2019-10-01 | 10:07 | 42.4297 | 278.8399 | -0.07 | 0.93 | -0.36 | 0.64 | -0.3 | 0.7 | 76.17 | 24.41
2019-10-01 | 10:07 | 42.5312 | 278.9415 | 0.02 | 1.02 | -0.42 | 0.58 | -0.34 | 0.66 | 78.12 | 26.37
2019-10-01 | 10:07 | 42.6406 | 279.0508 | 0.01 | 1.01 | -0.41 | 0.59 | -0.36 | 0.64 | 75.2 | 24.41
2019-10-01 | 10:07 | 42.7383 | 279.1485 | 0.03 | 1.03 | -0.4 | 0.6 | -0.34 | 0.66 | 76.17 | 28.32
2019-10-01 | 10:07 | 42.8398 | 279.25 | 0.02 | 1.02 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 28.32
2019-10-01 | 10:07 | 42.9414 | 279.3516 | 0.02 | 1.02 | -0.41 | 0.59 | -0.34 | 0.66 | 76.17 | 48.83
2019-10-01 | 10:07 | 43.0508 | 279.461 | 0.04 | 1.04 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 26.37
2019-10-01 | 10:07 | 43.1484 | 279.5586 | 0.03 | 1.03 | -0.41 | 0.59 | -0.36 | 0.64 | 76.17 | 26.37
2019-10-01 | 10:07 | 43.25 | 279.6602 | 0.03 | 1.03 | -0.42 | 0.58 | -0.35 | 0.65 | 77.15 | 26.37
2019-10-01 | 10:07 | 43.3594 | 279.7696 | 0.04 | 1.04 | -0.4 | 0.6 | -0.34 | 0.66 | 76.17 | 24.41
2019-10-01 | 10:07 | 43.4609 | 279.8711 | 0.03 | 1.03 | -0.41 | 0.59 | -0.35 | 0.65 | 76.17 | 26.37
2019-10-01 | 10:07 | 43.5586 | 279.9688 | -0.03 | 0.97 | -0.37 | 0.63 | -0.34 | 0.66 | 77.15 | 29.3
2019-10-01 | 10:07 | 43.6602 | 280.0704 | -0.06 | 0.94 | -0.35 | 0.65 | -0.32 | 0.68 | 76.17 | 27.34
2019-10-01 | 10:07 | 43.7695 | 280.1797 | -0.06 | 0.94 | -0.36 | 0.64 | -0.33 | 0.67 | 76.17 | 25.39
2019-10-01 | 10:07 | 43.8711 | 280.2813 | -0.08 | 0.92 | -0.34 | 0.66 | -0.32 | 0.68 | 75.2 | 24.41
2019-10-01 | 10:07 | 43.9688 | 280.379 | -0.04 | 0.96 | -0.37 | 0.63 | -0.33 | 0.67 | 76.17 | 25.39
2019-10-01 | 10:07 | 44.0703 | 280.4805 | 0.01 | 1.01 | -0.4 | 0.6 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:07 | 44.1797 | 280.5899 | 0.02 | 1.02 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 24.41
2019-10-01 | 10:07 | 44.2812 | 280.6915 | 0.03 | 1.03 | -0.41 | 0.59 | -0.33 | 0.67 | 78.12 | 29.3
2019-10-01 | 10:07 | 44.3789 | 280.7891 | 0.02 | 1.02 | -0.4 | 0.6 | -0.34 | 0.66 | 77.15 | 30.27
2019-10-01 | 10:07 | 44.4883 | 280.8985 | 0.03 | 1.03 | -0.4 | 0.6 | -0.32 | 0.68 | 77.15 | 26.37
2019-10-01 | 10:07 | 44.5898 | 281 | 0.02 | 1.02 | -0.4 | 0.6 | -0.34 | 0.66 | 76.17 | 26.37
2019-10-01 | 10:07 | 44.6914 | 281.1016 | 0.04 | 1.04 | -0.41 | 0.59 | -0.34 | 0.66 | 77.15 | 25.39
2019-10-01 | 10:07 | 44.7891 | 281.1993 | 0.03 | 1.03 | -0.41 | 0.59 | -0.34 | 0.66 | 75.2 | 24.41
2019-10-01 | 10:07 | 44.8984 | 281.3086 | 0.04 | 1.04 | -0.42 | 0.58 | -0.36 | 0.64 | 76.17 | 25.39
2019-10-01 | 10:07 | 45 | 281.4102 | 0.03 | 1.03 | -0.41 | 0.59 | -0.34 | 0.66 | 76.17 | 26.37
2019-10-01 | 10:07 | 45.1016 | 281.5118 | -0.03 | 0.97 | -0.36 | 0.64 | -0.34 | 0.66 | 75.2 | 29.3
2019-10-01 | 10:07 | 45.1992 | 281.6094 | -0.06 | 0.94 | -0.35 | 0.65 | -0.32 | 0.68 | 77.15 | 36.13
2019-10-01 | 10:07 | 45.3086 | 281.7188 | -0.07 | 0.93 | -0.35 | 0.65 | -0.3 | 0.7 | 76.17 | 26.37
2019-10-01 | 10:07 | 45.4102 | 281.8204 | -0.06 | 0.94 | -0.34 | 0.66 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:07 | 45.5117 | 281.9219 | 0.01 | 1.01 | -0.38 | 0.62 | -0.32 | 0.68 | 75.2 | 26.37
2019-10-01 | 10:07 | 45.6094 | 282.0196 | 0.02 | 1.02 | -0.39 | 0.61 | -0.34 | 0.66 | 77.15 | 25.39
2019-10-01 | 10:07 | 45.7188 | 282.129 | 0.02 | 1.02 | -0.39 | 0.61 | -0.33 | 0.67 | 77.15 | 37.11
2019-10-01 | 10:07 | 45.8203 | 282.2305 | 0.02 | 1.02 | -0.39 | 0.61 | -0.33 | 0.67 | 76.17 | 29.3
2019-10-01 | 10:07 | 45.9219 | 282.3321 | 0.03 | 1.03 | -0.38 | 0.62 | -0.34 | 0.66 | 75.2 | 27.34
2019-10-01 | 10:07 | 46.0312 | 282.4415 | 0.03 | 1.03 | -0.4 | 0.6 | -0.33 | 0.67 | 77.15 | 25.39
2019-10-01 | 10:07 | 46.1289 | 282.5391 | 0.02 | 1.02 | -0.39 | 0.61 | -0.33 | 0.67 | 76.17 | 24.41
2019-10-01 | 10:07 | 46.2305 | 282.6407 | 0.03 | 1.03 | -0.39 | 0.61 | -0.33 | 0.67 | 78.12 | 25.39
2019-10-01 | 10:07 | 46.3398 | 282.75 | 0.04 | 1.04 | -0.41 | 0.59 | -0.35 | 0.65 | 78.12 | 25.39
2019-10-01 | 10:07 | 46.4414 | 282.8516 | 0.04 | 1.04 | -0.41 | 0.59 | -0.33 | 0.67 | 76.17 | 26.37
2019-10-01 | 10:07 | 46.5391 | 282.9493 | -0.02 | 0.98 | -0.36 | 0.64 | -0.33 | 0.67 | 76.17 | 29.3
2019-10-01 | 10:07 | 46.6484 | 283.0586 | -0.05 | 0.95 | -0.35 | 0.65 | -0.31 | 0.69 | 76.17 | 28.32
2019-10-01 | 10:07 | 46.75 | 283.1602 | -0.06 | 0.94 | -0.34 | 0.66 | -0.3 | 0.7 | 76.17 | 24.41
2019-10-01 | 10:07 | 46.8516 | 283.2618 | -0.06 | 0.94 | -0.33 | 0.67 | -0.31 | 0.69 | 78.12 | 26.37
2019-10-01 | 10:07 | 46.9492 | 283.3594 | -0.07 | 0.93 | -0.33 | 0.67 | -0.3 | 0.7 | 75.2 | 24.41
2019-10-01 | 10:07 | 47.0586 | 283.4688 | 0.01 | 1.01 | -0.4 | 0.6 | -0.32 | 0.68 | 76.17 | 25.39
2019-10-01 | 10:07 | 47.1602 | 283.5704 | 0.02 | 1.02 | -0.39 | 0.61 | -0.34 | 0.66 | 75.2 | 25.39
2019-10-01 | 10:07 | 47.2617 | 283.6719 | 0.03 | 1.03 | -0.39 | 0.61 | -0.31 | 0.69 | 75.2 | 27.34
2019-10-01 | 10:07 | 47.3594 | 283.7696 | 0.03 | 1.03 | -0.4 | 0.6 | -0.34 | 0.66 | 74.22 | 28.32
2019-10-01 | 10:07 | 47.4688 | 283.879 | 0.04 | 1.04 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 26.37
2019-10-01 | 10:07 | 47.5703 | 283.9805 | 0.03 | 1.03 | -0.4 | 0.6 | -0.33 | 0.67 | 74.22 | 26.37
2019-10-01 | 10:07 | 47.6719 | 284.0821 | 0.04 | 1.04 | -0.39 | 0.61 | -0.34 | 0.66 | 74.22 | 23.44
2019-10-01 | 10:07 | 47.7695 | 284.1797 | 0.03 | 1.03 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:07 | 47.8789 | 284.2891 | 0.04 | 1.04 | -0.4 | 0.6 | -0.33 | 0.67 | 75.2 | 26.37
2019-10-01 | 10:07 | 47.9805 | 284.3907 | 0.03 | 1.03 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 51.76
2019-10-01 | 10:07 | 48.0781 | 284.4883 | -0.04 | 0.96 | -0.35 | 0.65 | -0.33 | 0.67 | 77.15 | 28.32
2019-10-01 | 10:07 | 48.1914 | 284.6016 | -0.05 | 0.95 | -0.34 | 0.66 | -0.31 | 0.69 | 75.2 | 29.3
2019-10-01 | 10:07 | 48.2891 | 284.6993 | -0.05 | 0.95 | -0.34 | 0.66 | -0.32 | 0.68 | 76.17 | 25.39
2019-10-01 | 10:07 | 48.3906 | 284.8008 | -0.07 | 0.93 | -0.32 | 0.68 | -0.29 | 0.71 | 76.17 | 24.41
2019-10-01 | 10:07 | 48.4883 | 284.8985 | 0 | 1 | -0.41 | 0.59 | -0.31 | 0.69 | 75.2 | 24.41
2019-10-01 | 10:07 | 48.6016 | 285.0118 | 0.03 | 1.03 | -0.38 | 0.62 | -0.33 | 0.67 | 77.15 | 27.34
2019-10-01 | 10:07 | 48.6992 | 285.1094 | 0.03 | 1.03 | -0.38 | 0.62 | -0.32 | 0.68 | 77.15 | 26.37
2019-10-01 | 10:07 | 48.8008 | 285.211 | 0.02 | 1.02 | -0.38 | 0.62 | -0.32 | 0.68 | 76.17 | 29.3
2019-10-01 | 10:07 | 48.8984 | 285.3086 | 0.03 | 1.03 | -0.38 | 0.62 | -0.32 | 0.68 | 76.17 | 28.32
2019-10-01 | 10:07 | 49.0117 | 285.4219 | 0.03 | 1.03 | -0.38 | 0.62 | -0.32 | 0.68 | 76.17 | 25.39
2019-10-01 | 10:07 | 49.1094 | 285.5196 | 0.04 | 1.04 | -0.39 | 0.61 | -0.33 | 0.67 | 76.17 | 24.41
2019-10-01 | 10:07 | 49.2109 | 285.6211 | 0.03 | 1.03 | -0.4 | 0.6 | -0.34 | 0.66 | 76.17 | 24.41
2019-10-01 | 10:07 | 49.3203 | 285.7305 | 0.04 | 1.04 | -0.38 | 0.62 | -0.32 | 0.68 | 75.2 | 24.41
2019-10-01 | 10:07 | 49.4219 | 285.8321 | 0.04 | 1.04 | -0.38 | 0.62 | -0.32 | 0.68 | 74.22 | 25.39
2019-10-01 | 10:07 | 49.5195 | 285.9297 | 0.02 | 1.02 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 27.34
2019-10-01 | 10:07 | 49.6211 | 286.0313 | -0.03 | 0.97 | -0.34 | 0.66 | -0.31 | 0.69 | 74.22 | 28.32
2019-10-01 | 10:07 | 49.7305 | 286.1407 | -0.05 | 0.95 | -0.34 | 0.66 | -0.3 | 0.7 | 76.17 | 28.32
2019-10-01 | 10:07 | 49.8281 | 286.2383 | -0.08 | 0.92 | -0.33 | 0.67 | -0.29 | 0.71 | 74.22 | 24.41
2019-10-01 | 10:07 | 49.9414 | 286.3516 | -0.06 | 0.94 | -0.33 | 0.67 | -0.3 | 0.7 | 76.17 | 24.41
2019-10-01 | 10:07 | 50.0312 | 286.4415 | 0.02 | 1.02 | -0.39 | 0.61 | -0.31 | 0.69 | 76.17 | 25.39
2019-10-01 | 10:07 | 50.1406 | 286.5508 | 0.02 | 1.02 | -0.38 | 0.62 | -0.32 | 0.68 | 75.2 | 25.39
2019-10-01 | 10:07 | 50.2383 | 286.6485 | 0.02 | 1.02 | -0.39 | 0.61 | -0.31 | 0.69 | 77.15 | 26.37
2019-10-01 | 10:07 | 50.3398 | 286.75 | 0.03 | 1.03 | -0.37 | 0.63 | -0.3 | 0.7 | 77.15 | 29.3
2019-10-01 | 10:07 | 50.4414 | 286.8516 | 0.03 | 1.03 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 28.32
2019-10-01 | 10:07 | 50.5508 | 286.961 | 0.04 | 1.04 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 25.39
2019-10-01 | 10:07 | 50.6484 | 287.0586 | 0.04 | 1.04 | -0.39 | 0.61 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:07 | 50.7617 | 287.1719 | 0.03 | 1.03 | -0.37 | 0.63 | -0.33 | 0.67 | 77.15 | 23.44
2019-10-01 | 10:07 | 50.8594 | 287.2696 | 0.04 | 1.04 | -0.38 | 0.62 | -0.33 | 0.67 | 76.17 | 24.41
2019-10-01 | 10:07 | 50.9609 | 287.3711 | 0.04 | 1.04 | -0.38 | 0.62 | -0.33 | 0.67 | 78.12 | 25.39
2019-10-01 | 10:07 | 51.0586 | 287.4688 | -0.02 | 0.98 | -0.34 | 0.66 | -0.32 | 0.68 | 77.15 | 27.34
2019-10-01 | 10:07 | 51.1602 | 287.5704 | -0.04 | 0.96 | -0.34 | 0.66 | -0.3 | 0.7 | 76.17 | 28.32
2019-10-01 | 10:07 | 51.2695 | 287.6797 | -0.06 | 0.94 | -0.33 | 0.67 | -0.29 | 0.71 | 76.17 | 41.02
2019-10-01 | 10:07 | 51.3711 | 287.7813 | -0.07 | 0.93 | -0.34 | 0.66 | -0.3 | 0.7 | 76.17 | 26.37
2019-10-01 | 10:07 | 51.4805 | 287.8907 | -0.03 | 0.97 | -0.36 | 0.64 | -0.29 | 0.71 | 75.2 | 26.37
2019-10-01 | 10:07 | 51.5703 | 287.9805 | 0.01 | 1.01 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 23.44
2019-10-01 | 10:07 | 51.6797 | 288.0899 | 0.03 | 1.03 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:07 | 51.7812 | 288.1915 | 0.02 | 1.02 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 45.9
2019-10-01 | 10:07 | 51.8906 | 288.3008 | 0.03 | 1.03 | -0.38 | 0.62 | -0.32 | 0.68 | 76.17 | 28.32
2019-10-01 | 10:07 | 51.9883 | 288.3985 | 0.04 | 1.04 | -0.38 | 0.62 | -0.31 | 0.69 | 78.12 | 29.3
2019-10-01 | 10:07 | 52.0898 | 288.5 | 0.04 | 1.04 | -0.37 | 0.63 | -0.32 | 0.68 | 76.17 | 25.39
2019-10-01 | 10:07 | 52.1914 | 288.6016 | 0.02 | 1.02 | -0.37 | 0.63 | -0.32 | 0.68 | 76.17 | 23.44
2019-10-01 | 10:07 | 52.2891 | 288.6993 | 0.03 | 1.03 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 22.46
2019-10-01 | 10:07 | 52.3984 | 288.8086 | 0.04 | 1.04 | -0.38 | 0.62 | -0.32 | 0.68 | 76.17 | 23.44
2019-10-01 | 10:07 | 52.5 | 288.9102 | 0.03 | 1.03 | -0.39 | 0.61 | -0.32 | 0.68 | 76.17 | 25.39
2019-10-01 | 10:07 | 52.6016 | 289.0118 | -0.04 | 0.96 | -0.34 | 0.66 | -0.32 | 0.68 | 76.17 | 28.32
2019-10-01 | 10:07 | 52.7109 | 289.1211 | -0.05 | 0.95 | -0.33 | 0.67 | -0.31 | 0.69 | 76.17 | 29.3
2019-10-01 | 10:07 | 52.8086 | 289.2188 | -0.06 | 0.94 | -0.33 | 0.67 | -0.29 | 0.71 | 76.17 | 23.44
2019-10-01 | 10:07 | 52.9102 | 289.3204 | -0.08 | 0.92 | -0.32 | 0.68 | -0.29 | 0.71 | 76.17 | 24.41
2019-10-01 | 10:07 | 53.0195 | 289.4297 | 0.01 | 1.01 | -0.39 | 0.61 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:07 | 53.1211 | 289.5313 | 0.02 | 1.02 | -0.37 | 0.63 | -0.32 | 0.68 | 77.15 | 25.39
2019-10-01 | 10:08 | 53.2188 | 289.629 | 0.02 | 1.02 | -0.37 | 0.63 | -0.33 | 0.67 | 76.17 | 26.37
2019-10-01 | 10:08 | 53.3281 | 289.7383 | 0.02 | 1.02 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 27.34
2019-10-01 | 10:08 | 53.4297 | 289.8399 | 0.03 | 1.03 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 28.32
2019-10-01 | 10:08 | 53.5312 | 289.9415 | 0.04 | 1.04 | -0.39 | 0.61 | -0.31 | 0.69 | 76.17 | 27.34
2019-10-01 | 10:08 | 53.6289 | 290.0391 | 0.03 | 1.03 | -0.38 | 0.62 | -0.31 | 0.69 | 77.15 | 25.39
2019-10-01 | 10:08 | 53.7305 | 290.1407 | 0.04 | 1.04 | -0.37 | 0.63 | -0.32 | 0.68 | 77.15 | 24.41
2019-10-01 | 10:08 | 53.8281 | 290.2383 | 0.04 | 1.04 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 23.44
2019-10-01 | 10:08 | 53.9414 | 290.3516 | 0.04 | 1.04 | -0.38 | 0.62 | -0.3 | 0.7 | 76.17 | 25.39
2019-10-01 | 10:08 | 54.0391 | 290.4493 | 0 | 1 | -0.35 | 0.65 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:08 | 54.1484 | 290.5586 | -0.04 | 0.96 | -0.33 | 0.67 | -0.29 | 0.71 | 77.15 | 28.32
2019-10-01 | 10:08 | 54.25 | 290.6602 | -0.04 | 0.96 | -0.32 | 0.68 | -0.29 | 0.71 | 77.15 | 29.3
2019-10-01 | 10:08 | 54.3516 | 290.7618 | -0.06 | 0.94 | -0.33 | 0.67 | -0.28 | 0.72 | 76.17 | 25.39
2019-10-01 | 10:08 | 54.4492 | 290.8594 | -0.05 | 0.95 | -0.32 | 0.68 | -0.29 | 0.71 | 77.15 | 24.41
2019-10-01 | 10:08 | 54.5586 | 290.9688 | 0.02 | 1.02 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 23.44
2019-10-01 | 10:08 | 54.6602 | 291.0704 | 0.02 | 1.02 | -0.37 | 0.63 | -0.31 | 0.69 | 75.2 | 24.41
2019-10-01 | 10:08 | 54.7617 | 291.1719 | 0.04 | 1.04 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:08 | 54.8594 | 291.2696 | 0.03 | 1.03 | -0.37 | 0.63 | -0.3 | 0.7 | 76.17 | 27.34
2019-10-01 | 10:08 | 54.9688 | 291.379 | 0.04 | 1.04 | -0.38 | 0.62 | -0.31 | 0.69 | 77.15 | 28.32
2019-10-01 | 10:08 | 55.0703 | 291.4805 | 0.03 | 1.03 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 27.34
2019-10-01 | 10:08 | 55.1719 | 291.5821 | 0.04 | 1.04 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:08 | 55.2695 | 291.6797 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 23.44
2019-10-01 | 10:08 | 55.3789 | 291.7891 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 25.39
2019-10-01 | 10:08 | 55.4805 | 291.8907 | 0.04 | 1.04 | -0.39 | 0.61 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:08 | 55.5781 | 291.9883 | -0.01 | 0.99 | -0.34 | 0.66 | -0.31 | 0.69 | 76.17 | 25.39
2019-10-01 | 10:08 | 55.6914 | 292.1016 | -0.05 | 0.95 | -0.33 | 0.67 | -0.29 | 0.71 | 76.17 | 29.3
2019-10-01 | 10:08 | 55.7891 | 292.1993 | -0.06 | 0.94 | -0.32 | 0.68 | -0.29 | 0.71 | 76.17 | 28.32
2019-10-01 | 10:08 | 55.8906 | 292.3008 | -0.06 | 0.94 | -0.32 | 0.68 | -0.27 | 0.73 | 76.17 | 24.41
2019-10-01 | 10:08 | 55.9883 | 292.3985 | 0.01 | 1.01 | -0.37 | 0.63 | -0.28 | 0.72 | 76.17 | 24.41
2019-10-01 | 10:08 | 56.1016 | 292.5118 | 0.02 | 1.02 | -0.37 | 0.63 | -0.33 | 0.67 | 76.17 | 24.41
2019-10-01 | 10:08 | 56.1992 | 292.6094 | 0.03 | 1.03 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:08 | 56.3008 | 292.711 | 0.03 | 1.03 | -0.37 | 0.63 | -0.29 | 0.71 | 76.17 | 26.37
2019-10-01 | 10:08 | 56.3984 | 292.8086 | 0.03 | 1.03 | -0.37 | 0.63 | -0.3 | 0.7 | 76.17 | 27.34
2019-10-01 | 10:08 | 56.5117 | 292.9219 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 28.32
2019-10-01 | 10:08 | 56.6094 | 293.0196 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 30.27
2019-10-01 | 10:08 | 56.7109 | 293.1211 | 0.04 | 1.04 | -0.37 | 0.63 | -0.3 | 0.7 | 77.15 | 24.41
2019-10-01 | 10:08 | 56.8203 | 293.2305 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 26.37
2019-10-01 | 10:08 | 56.9219 | 293.3321 | 0.04 | 1.04 | -0.37 | 0.63 | -0.3 | 0.7 | 75.2 | 22.46
2019-10-01 | 10:08 | 57.0195 | 293.4297 | 0.04 | 1.04 | -0.36 | 0.64 | -0.31 | 0.69 | 77.15 | 26.37
2019-10-01 | 10:08 | 57.1211 | 293.5313 | -0.03 | 0.97 | -0.32 | 0.68 | -0.3 | 0.7 | 77.15 | 51.76
2019-10-01 | 10:08 | 57.2305 | 293.6407 | -0.03 | 0.97 | -0.32 | 0.68 | -0.3 | 0.7 | 77.15 | 29.3
2019-10-01 | 10:08 | 57.3281 | 293.7383 | -0.04 | 0.96 | -0.31 | 0.69 | -0.27 | 0.73 | 76.17 | 28.32
2019-10-01 | 10:08 | 57.4414 | 293.8516 | -0.05 | 0.95 | -0.32 | 0.68 | -0.28 | 0.72 | 76.17 | 24.41
2019-10-01 | 10:08 | 57.5312 | 293.9415 | 0.01 | 1.01 | -0.37 | 0.63 | -0.28 | 0.72 | 77.15 | 23.44
2019-10-01 | 10:08 | 57.6406 | 294.0508 | 0.02 | 1.02 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 23.44
2019-10-01 | 10:08 | 57.7383 | 294.1485 | 0.03 | 1.03 | -0.36 | 0.64 | -0.31 | 0.69 | 77.15 | 25.39
2019-10-01 | 10:08 | 57.8398 | 294.25 | 0.03 | 1.03 | -0.37 | 0.63 | -0.31 | 0.69 | 75.2 | 24.41
2019-10-01 | 10:08 | 57.9492 | 294.3594 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 29.3
2019-10-01 | 10:08 | 58.0508 | 294.461 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 75.2 | 28.32
2019-10-01 | 10:08 | 58.1484 | 294.5586 | 0.04 | 1.04 | -0.36 | 0.64 | -0.31 | 0.69 | 76.17 | 35.16
2019-10-01 | 10:08 | 58.25 | 294.6602 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 75.2 | 24.41
2019-10-01 | 10:08 | 58.3594 | 294.7696 | 0.04 | 1.04 | -0.38 | 0.62 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:08 | 58.4609 | 294.8711 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 76.17 | 25.39
2019-10-01 | 10:08 | 58.5586 | 294.9688 | 0 | 1 | -0.34 | 0.66 | -0.32 | 0.68 | 76.17 | 23.44
2019-10-01 | 10:08 | 58.6719 | 295.0821 | -0.05 | 0.95 | -0.33 | 0.67 | -0.29 | 0.71 | 75.2 | 27.34
2019-10-01 | 10:08 | 58.7695 | 295.1797 | -0.04 | 0.96 | -0.31 | 0.69 | -0.28 | 0.72 | 76.17 | 28.32
2019-10-01 | 10:08 | 58.8711 | 295.2813 | -0.06 | 0.94 | -0.32 | 0.68 | -0.29 | 0.71 | 76.17 | 27.34
2019-10-01 | 10:08 | 58.9805 | 295.3907 | -0.05 | 0.95 | -0.31 | 0.69 | -0.28 | 0.72 | 75.2 | 25.39
2019-10-01 | 10:08 | 59.0781 | 295.4883 | 0.02 | 1.02 | -0.37 | 0.63 | -0.29 | 0.71 | 75.2 | 24.41
2019-10-01 | 10:08 | 59.1797 | 295.5899 | 0.03 | 1.03 | -0.36 | 0.64 | -0.31 | 0.69 | 76.17 | 24.41
2019-10-01 | 10:08 | 59.2812 | 295.6915 | 0.03 | 1.03 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 24.41
2019-10-01 | 10:08 | 59.3906 | 295.8008 | 0.04 | 1.04 | -0.37 | 0.63 | -0.3 | 0.7 | 76.17 | 25.39
2019-10-01 | 10:08 | 59.4883 | 295.8985 | 0.03 | 1.03 | -0.37 | 0.63 | -0.3 | 0.7 | 75.2 | 28.32
2019-10-01 | 10:08 | 59.5898 | 296 | 0.04 | 1.04 | -0.37 | 0.63 | -0.31 | 0.69 | 77.15 | 29.3
2019-10-01 | 10:08 | 59.6914 | 296.1016 | 0.03 | 1.03 | -0.37 | 0.63 | -0.3 | 0.7 | 76.17 | 25.39
2019-10-01 | 10:08 | 59.7891 | 296.1993 | 0.04 | 1.04 | -0.37 | 0.63 | -0.32 | 0.68 | 75.2 | 24.41
2019-10-01 | 10:08 | 59.8984 | 296.3086 | 0.04 | 1.04 | -0.38 | 0.62 | -0.3 | 0.7 | 76.17 | 24.41
2019-10-01 | 10:08 | 60 | 296.4102 | 0.04 | 1.04 | -0.37 | 0.63 | -0.32 | 0.68 | 75.2 | 24.41
2019-10-01 | 10:08 | 60.1094 | 296.5196 | -0.03 | 0.97 | -0.34 | 0.66 | -0.3 | 0.7 | 77.15 | 25.39
2019-10-01 | 10:08 | 60.2109 | 296.6211 | -0.05 | 0.95 | -0.34 | 0.66 | -0.3 | 0.7 | 76.17 | 28.32
2019-10-01 | 10:08 | 60.3086 | 296.7188 | -0.05 | 0.95 | -0.32 | 0.68 | -0.3 | 0.7 | 76.17 | 28.32
2019-10-01 | 10:08 | 60.4102 | 296.8204 | -0.06 | 0.94 | -0.34 | 0.66 | -0.3 | 0.7 | 76.17 | 27.34
2019-10-01 | 10:08 | 60.5195 | 296.9297 | 0.02 | 1.02 | -0.38 | 0.62 | -0.31 | 0.69 | 75.2 | 25.39
2019-10-01 | 10:08 | 60.6211 | 297.0313 | 0.02 | 1.02 | -0.38 | 0.62 | -0.33 | 0.67 | 76.17 | 24.41
2019-10-01 | 10:08 | 60.7188 | 297.129 | 0.02 | 1.02 | -0.38 | 0.62 | -0.33 | 0.67 | 75.2 | 24.41
2019-10-01 | 10:08 | 60.8203 | 297.2305 | 0.04 | 1.04 | -0.39 | 0.61 | -0.33 | 0.67 | 77.15 | 25.39
2019-10-01 | 10:08 | 60.9297 | 297.3399 | 0.04 | 1.04 | -0.38 | 0.62 | -0.33 | 0.67 | 76.17 | 26.37
2019-10-01 | 10:08 | 61.0312 | 297.4415 | 0.04 | 1.04 | -0.39 | 0.61 | -0.33 | 0.67 | 77.15 | 28.32
2019-10-01 | 10:08 | 61.1289 | 297.5391 | 0.04 | 1.04 | -0.39 | 0.61 | -0.34 | 0.66 | 77.15 | 29.3
2019-10-01 | 10:08 | 61.2305 | 297.6407 | 0.04 | 1.04 | -0.4 | 0.6 | -0.33 | 0.67 | 75.2 | 25.39
2019-10-01 | 10:08 | 61.3398 | 297.75 | 0.04 | 1.04 | -0.4 | 0.6 | -0.33 | 0.67 | 76.17 | 25.39
2019-10-01 | 10:08 | 61.4414 | 297.8516 | 0.03 | 1.03 | -0.4 | 0.6 | -0.34 | 0.66 | 75.2 | 24.41
2019-10-01 | 10:08 | 61.5391 | 297.9493 | 0 | 1 | -0.36 | 0.64 | -0.33 | 0.67 | 76.17 | 25.39
2019-10-01 | 10:08 | 61.6484 | 298.0586 | -0.05 | 0.95 | -0.34 | 0.66 | -0.32 | 0.68 | 75.2 | 26.37
2019-10-01 | 10:08 | 61.75 | 298.1602 | -0.06 | 0.94 | -0.33 | 0.67 | -0.31 | 0.69 | 75.2 | 40.04
2019-10-01 | 10:08 | 61.8516 | 298.2618 | -0.05 | 0.95 | -0.34 | 0.66 | -0.32 | 0.68 | 76.17 | 29.3
2019-10-01 | 10:08 | 61.9492 | 298.3594 | -0.06 | 0.94 | -0.34 | 0.66 | -0.29 | 0.71 | 75.2 | 27.34
2019-10-01 | 10:08 | 62.0586 | 298.4688 | 0.02 | 1.02 | -0.4 | 0.6 | -0.35 | 0.65 | 76.17 | 25.39
2019-10-01 | 10:08 | 62.1602 | 298.5704 | 0.03 | 1.03 | -0.4 | 0.6 | -0.33 | 0.67 | 76.17 | 24.41
2019-10-01 | 10:08 | 62.2617 | 298.6719 | 0.02 | 1.02 | -0.39 | 0.61 | -0.34 | 0.66 | 76.17 | 24.41
2019-10-01 | 10:08 | 62.3594 | 298.7696 | 0.03 | 1.03 | -0.41 | 0.59 | -0.34 | 0.66 | 75.2 | 25.39
2019-10-01 | 10:08 | 62.4688 | 298.879 | 0.03 | 1.03 | -0.41 | 0.59 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:08 | 62.5703 | 298.9805 | 0.02 | 1.02 | -0.4 | 0.6 | -0.35 | 0.65 | 75.2 | 28.32
2019-10-01 | 10:08 | 62.6719 | 299.0821 | 0.03 | 1.03 | -0.41 | 0.59 | -0.34 | 0.66 | 76.17 | 29.3
2019-10-01 | 10:08 | 62.7812 | 299.1915 | 0.03 | 1.03 | -0.41 | 0.59 | -0.35 | 0.65 | 75.2 | 26.37
2019-10-01 | 10:08 | 62.8789 | 299.2891 | 0.04 | 1.04 | -0.4 | 0.6 | -0.35 | 0.65 | 74.22 | 24.41
2019-10-01 | 10:08 | 62.9805 | 299.3907 | 0.03 | 1.03 | -0.41 | 0.59 | -0.36 | 0.64 | 77.15 | 25.39
2019-10-01 | 10:08 | 63.0781 | 299.4883 | -0.02 | 0.98 | -0.37 | 0.63 | -0.34 | 0.66 | 76.17 | 25.39
2019-10-01 | 10:08 | 63.1914 | 299.6016 | -0.06 | 0.94 | -0.35 | 0.65 | -0.32 | 0.68 | 77.15 | 26.37
2019-10-01 | 10:08 | 63.2891 | 299.6993 | -0.07 | 0.93 | -0.36 | 0.64 | -0.33 | 0.67 | 76.17 | 50.78
2019-10-01 | 10:08 | 63.3906 | 299.8008 | -0.07 | 0.93 | -0.36 | 0.64 | -0.33 | 0.67 | 76.17 | 28.32
2019-10-01 | 10:08 | 63.5 | 299.9102 | -0.01 | 0.99 | -0.4 | 0.6 | -0.33 | 0.67 | 76.17 | 27.34
2019-10-01 | 10:08 | 63.6016 | 300.0118 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 75.2 | 26.37
2019-10-01 | 10:08 | 63.6992 | 300.1094 | 0.02 | 1.02 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:08 | 63.8008 | 300.211 | 0.02 | 1.02 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:08 | 63.9102 | 300.3204 | 0.02 | 1.02 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:08 | 64.0117 | 300.4219 | 0.04 | 1.04 | -0.44 | 0.56 | -0.36 | 0.64 | 75.2 | 25.39
2019-10-01 | 10:08 | 64.1094 | 300.5196 | 0.03 | 1.03 | -0.43 | 0.57 | -0.37 | 0.63 | 75.2 | 27.34
2019-10-01 | 10:08 | 64.2109 | 300.6211 | 0.02 | 1.02 | -0.43 | 0.57 | -0.37 | 0.63 | 76.17 | 29.3
2019-10-01 | 10:08 | 64.3203 | 300.7305 | 0.03 | 1.03 | -0.44 | 0.56 | -0.38 | 0.62 | 76.17 | 48.83
2019-10-01 | 10:08 | 64.4219 | 300.8321 | 0.02 | 1.02 | -0.44 | 0.56 | -0.37 | 0.63 | 76.17 | 25.39
2019-10-01 | 10:08 | 64.5195 | 300.9297 | 0.03 | 1.03 | -0.45 | 0.55 | -0.38 | 0.62 | 76.17 | 24.41
2019-10-01 | 10:08 | 64.6211 | 301.0313 | -0.05 | 0.95 | -0.38 | 0.62 | -0.37 | 0.63 | 75.2 | 25.39
2019-10-01 | 10:08 | 64.7305 | 301.1407 | -0.06 | 0.94 | -0.39 | 0.61 | -0.37 | 0.63 | 75.2 | 26.37
2019-10-01 | 10:08 | 64.8281 | 301.2383 | -0.08 | 0.92 | -0.37 | 0.63 | -0.37 | 0.63 | 76.17 | 24.41
2019-10-01 | 10:08 | 64.9414 | 301.3516 | -0.07 | 0.93 | -0.37 | 0.63 | -0.37 | 0.63 | 76.17 | 29.3
2019-10-01 | 10:08 | 65.0391 | 301.4493 | 0.01 | 1.01 | -0.45 | 0.55 | -0.38 | 0.62 | 75.2 | 28.32
2019-10-01 | 10:08 | 65.1406 | 301.5508 | 0.02 | 1.02 | -0.45 | 0.55 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:08 | 65.2383 | 301.6485 | 0.03 | 1.03 | -0.45 | 0.55 | -0.39 | 0.61 | 75.2 | 25.39
2019-10-01 | 10:08 | 65.3516 | 301.7618 | 0.04 | 1.04 | -0.46 | 0.54 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:08 | 65.4492 | 301.8594 | 0.04 | 1.04 | -0.46 | 0.54 | -0.4 | 0.6 | 76.17 | 27.34
2019-10-01 | 10:08 | 65.5508 | 301.961 | 0.04 | 1.04 | -0.47 | 0.53 | -0.39 | 0.61 | 76.17 | 25.39
2019-10-01 | 10:08 | 65.6602 | 302.0704 | 0.04 | 1.04 | -0.47 | 0.53 | -0.4 | 0.6 | 76.17 | 27.34
2019-10-01 | 10:08 | 65.75 | 302.1602 | 0.04 | 1.04 | -0.48 | 0.52 | -0.41 | 0.59 | 76.17 | 28.32
2019-10-01 | 10:08 | 65.8594 | 302.2696 | 0.03 | 1.03 | -0.48 | 0.52 | -0.4 | 0.6 | 76.17 | 27.34
2019-10-01 | 10:08 | 65.9609 | 302.3711 | 0.04 | 1.04 | -0.48 | 0.52 | -0.41 | 0.59 | 77.15 | 25.39
2019-10-01 | 10:08 | 66.0703 | 302.4805 | 0 | 1 | -0.46 | 0.54 | -0.4 | 0.6 | 76.17 | 25.39
2019-10-01 | 10:08 | 66.1719 | 302.5821 | -0.05 | 0.95 | -0.41 | 0.59 | -0.4 | 0.6 | 76.17 | 24.41
2019-10-01 | 10:08 | 66.2695 | 302.6797 | -0.07 | 0.93 | -0.39 | 0.61 | -0.38 | 0.62 | 77.15 | 26.37
2019-10-01 | 10:08 | 66.3711 | 302.7813 | -0.07 | 0.93 | -0.4 | 0.6 | -0.39 | 0.61 | 75.2 | 26.37
2019-10-01 | 10:08 | 66.4805 | 302.8907 | -0.09 | 0.91 | -0.38 | 0.62 | -0.38 | 0.62 | 75.2 | 28.32
2019-10-01 | 10:08 | 66.5781 | 302.9883 | 0.01 | 1.01 | -0.48 | 0.52 | -0.42 | 0.58 | 76.17 | 29.3
2019-10-01 | 10:08 | 66.6797 | 303.0899 | 0.02 | 1.02 | -0.5 | 0.5 | -0.42 | 0.58 | 75.2 | 24.41
2019-10-01 | 10:08 | 66.7812 | 303.1915 | 0.04 | 1.04 | -0.5 | 0.5 | -0.42 | 0.58 | 76.17 | 25.39
2019-10-01 | 10:08 | 66.8906 | 303.3008 | 0.04 | 1.04 | -0.5 | 0.5 | -0.42 | 0.58 | 77.15 | 25.39
2019-10-01 | 10:08 | 66.9883 | 303.3985 | 0.03 | 1.03 | -0.51 | 0.49 | -0.43 | 0.57 | 77.15 | 24.41
2019-10-01 | 10:08 | 67.0898 | 303.5 | 0.03 | 1.03 | -0.51 | 0.49 | -0.44 | 0.56 | 77.15 | 26.37
2019-10-01 | 10:08 | 67.1914 | 303.6016 | 0.04 | 1.04 | -0.5 | 0.5 | -0.44 | 0.56 | 76.17 | 44.92
2019-10-01 | 10:08 | 67.2891 | 303.6993 | 0.04 | 1.04 | -0.5 | 0.5 | -0.44 | 0.56 | 76.17 | 29.3
2019-10-01 | 10:08 | 67.3984 | 303.8086 | 0.03 | 1.03 | -0.51 | 0.49 | -0.45 | 0.55 | 76.17 | 27.34
2019-10-01 | 10:08 | 67.5 | 303.9102 | 0.04 | 1.04 | -0.53 | 0.47 | -0.44 | 0.56 | 76.17 | 25.39
2019-10-01 | 10:08 | 67.6094 | 304.0196 | -0.03 | 0.97 | -0.44 | 0.56 | -0.43 | 0.57 | 76.17 | 25.39
2019-10-01 | 10:08 | 67.7109 | 304.1211 | -0.07 | 0.93 | -0.44 | 0.56 | -0.41 | 0.59 | 76.17 | 25.39
Open PLX DAQ UI

## Efficiency Analysis 50C Limit
CW Flow Rate (mL/s) | Max CWT2 [C] | Min CWT2 [C] | Average CWT2 [C] | Pb @ Start of Pulse | Density @ Pb start | Phe @ Start of Pulse | Density @ Phe start | K values | Average Density @ Start (kg/m3) | Pipe Diameter (m) | Pipe Cross Section Area (m2) | Steam Velocity at Start of Pulse (m/s) | Is flow choked? Set to 470 if above this | Steam Mass Flow @ Start (kg/s)
9.6 | 76.17 | 72.27 | 73.8371 | 1.04 | 0.59 | 0.17 | 0.112 | 10.7 | 0.351 | 0.011 | 9.5033e-05 | 205.8392 | 205.8392 | 0.0068661
7.2 | 81.05 | 77.15 | 78.6688 | 1.04 | 0.59 | 0.22 | 0.016 | 10.7 | 0.303 | 0.011 | 9.5033e-05 | 215.0838 | 215.0838 | 0.0061933
17.3 | 73.24 | 68.36 | 70.9211 | 1.08 | 0.646 | 0.2 | 0.015 | 10.7 | 0.3305 | 0.011 | 9.5033e-05 | 213.3426 | 213.3426 | 0.0067008
14.7 | 75.2 | 69.34 | 70.7671 | 1.07 | 0.646 | 0.12 | 0.00921 | 10.7 | 0.32761 | 0.011 | 9.5033e-05 | 222.6428 | 222.6428 | 0.0069316
13.1 | 75.2 | 71.29 | 72.8162 | 1.09 | 0.646 | 0.21 | 0.015 | 10.7 | 0.3305 | 0.011 | 9.5033e-05 | 213.3426 | 213.3426 | 0.0067008
10.5 | 76.17 | 68.36 | 73.5734 | 1 | 0.59 | 0.22 | 0.143 | 10.7 | 0.3665 | 0.011 | 9.5033e-05 | 190.7359 | 190.7359 | 0.0066433
CW Flow Rate (mL/s) | Pb @ End of Pulse | Density @ Pb end | Phe @ End of Pulse | Density @ Phe end | Average Density @ End (kg/m3) | Steam Velocity at End of Pulse (kg/s) | Is flow choked? Set to 470 if above this | Steam Mass Flow @ End (kg/s) | Average Steam Mass Flow Rate (kg/s) | Time Valve is Open (ms) | Time Valve is Closed (ms) | Experiment Average Mass Flow Rate (kg/s)
9.6 | 0.77 | 0.465 | 0.38 | 0.239 | 0.352 | 137.6205 | 137.6205 | 0.0046036 | 0.0057349 | 500 | 1000 | 0.0019116 |  | average mass flow rate: |  | 0.0019206
7.2 | 0.83 | 0.507 | 0.45 | 0.28 | 0.3935 | 128.4818 | 128.4818 | 0.0048046 | 0.005499 | 500 | 1000 | 0.001833
17.3 | 0.84 | 0.507 | 0.41 | 0.256 | 0.3815 | 138.8063 | 138.8063 | 0.0050324 | 0.0058666 | 500 | 1000 | 0.0019555
14.7 | 0.83 | 0.507 | 0.32 | 0.203 | 0.355 | 156.7087 | 156.7087 | 0.0052868 | 0.0061092 | 500 | 1000 | 0.0020364
13.1 | 0.85 | 0.507 | 0.42 | 0.262 | 0.3845 | 138.2637 | 138.2637 | 0.0050522 | 0.0058765 | 500 | 1000 | 0.0019588
10.5 | 0.76 | 0.451 | 0.42 | 0.262 | 0.3565 | 127.6826 | 127.6826 | 0.0043258 | 0.0054845 | 500 | 1000 | 0.0018282
CW Flow Rate (mL/s) | Average Boiler Pressure | Enthalpy of steam (hg) at average boiler pressure (kJ/kg) | Enthalpy of steam (hg) at 50C | Enthalpy of water (hf) at 50C | Average Steam Inlet Pressure | Density of Steam at Average Inlet Pressure (kg/m3) | Density of Steam at 50C (kg/m3) | Vapour fraction after condensation to limit (set by 50C cooling water) | Energy available in steam (kJ/kg) | Energy available from steam (kJ/s) | Density of water at CWT2 (kg/m3) | Cp (water) @CWT1 (kJ/kg.K) | Water Flow Rate (kg/s) | Energy Recovered in Water (kJ/s) | Percentage of Available Energy Recovered (%)
9.6 | 0.905 | 2671 | 2591.4 | 209.3 | 0.275 | 0.176 | 0.083 | 0.47159 | 1338.3233 | 2.5584 | 975 | 4.19 | 0.00936 | 0.93374 | 36.4974
7.2 | 0.935 | 2672 | 2591.4 | 209.3 | 0.335 | 0.212 | 0.083 | 0.39151 | 1530.0854 | 2.8046 | 972 | 4.2 | 0.0069984 | 0.84066 | 29.974
17.3 | 0.96 | 2673 | 2591.4 | 209.3 | 0.305 | 0.194 | 0.083 | 0.42784 | 1444.5541 | 2.8249 | 978 | 4.19 | 0.016919 | 1.4814 | 52.4403
14.7 | 0.95 | 2673 | 2591.4 | 209.3 | 0.22 | 0.143 | 0.083 | 0.58042 | 1081.0825 | 2.2015 | 976 | 4.19 | 0.014347 | 1.2469 | 56.6389
13.1 | 0.97 | 2674 | 2591.4 | 209.3 | 0.315 | 0.2 | 0.083 | 0.415 | 1476.1285 | 2.8915 | 976 | 4.19 | 0.012786 | 1.2208 | 42.222
10.5 | 0.88 | 2669 | 2591.4 | 209.3 | 0.32 | 0.203 | 0.083 | 0.40887 | 1485.7379 | 2.7162 | 976 | 4.19 | 0.010248 | 1.011 | 37.2217

## Uncertainty Analysis
PDF = Probability Density Function |  | SU = Standard Uncertainty
FLOW RATE UNCERTAINTY
9.6mL/s | Volume | Time |  | Uncertainty budget:
| 100 | 10 |  | Part of Measurement | Source of uncertainty | Value +/- | PDF | Divisor | SU | Combined SU | Relative SU | Comb. R SU | Total SU | Coverage Factor | Total Uncertainty
| 100 | 10 |  | Volume | Precision of beaker | 5 | Uniform | √3 | 2.8868 | 2.8868 | 0.028868 | 0.044181 | 0.42078 | 2 | 0.84155
| 100 | 10 |  |  | Repeatability of volume | 0 | Normal | 2.4495 | 0
| 100 | 11 |  | Time General | Precision of stopwatch | 0.5 | Uniform | √3 | 0.28868 | 0.35119 | 0.033447
| 100 | 11 |  |  | Human error | 0.1 | Normal * | 1 | 0.2
| 100 | 11 |  | Time Start | Repeatability of time | 0 | Normal | 1.7321 | 0
|  |  |  | Time End |  | 0 |  |  | 0
* This is according to: https://aapt.scitation.org/doi/10.1119/1.5085437
* This is actually the STDEV from the mean found by the author, but taken here as an estimate of uncertainty for human error for a single measurement.
7.2mL/s
| Volume | Time |  | Uncertainty budget:
| 100 | 13 |  | Part of Measurement | Source of uncertainty | Value +/- | PDF | Divisor | SU | Combined SU | Relative SU | Comb. R SU | Total SU | Coverage Factor | Total Uncertainty
| 100 | 13 |  | Volume | Precision of beaker | 5 | Uniform | √3 | 2.8868 | 2.8868 | 0.028868 | 0.038244 | 0.27317 | 2 | 0.54634
| 100 | 13 |  |  | Repeatability of volume | 0 | Normal | 2.4495 | 0
| 100 | 15 |  | Time General | Precision of stopwatch | 0.5 | Uniform | √3 | 0.28868 | 0.35119 | 0.025085
| 100 | 15 |  |  | Human error | 0.1 | Normal * | 1 | 0.2
| 100 | 15 |  | Time Start | Repeatability of time | 0 | Normal | 1.7321 | 0
|  |  |  | Time End |  | 0 |  |  | 0
17.3mL/s
| Volume | Time |  | Uncertainty budget:
| 100 | 5 |  | Part of Measurement | Source of uncertainty | Value +/- | PDF | Divisor | SU | Combined SU | Relative SU | Comb. R SU | Total SU | Coverage Factor | Total Uncertainty
| 100 | 5 |  | Volume | Precision of beaker | 5 | Uniform | √3 | 2.8868 | 2.8868 | 0.028868 | 0.090191 | 1.5916 | 2 | 3.1832
| 100 | 6 |  |  | Repeatability of volume | 0 | Normal | 2.4495 | 0
| 100 | 6 |  | Time General | Precision of stopwatch | 0.5 | Uniform | √3 | 0.28868 | 0.48419 | 0.085446
| 100 | 6 |  |  | Human error | 0.1 | Normal * | 1 | 0.2
| 100 | 6 |  | Time Start | Repeatability of time | 0.57735 | Normal | 1.7321 | 0.33333
|  |  |  | Time End |  | 0 |  |  | 0
14.7mL/s
| Volume | Time |  | Uncertainty budget:
| 100 | 7 |  | Part of Measurement | Source of uncertainty | Value +/- | PDF | Divisor | SU | Combined SU | Relative SU | Comb. R SU | Total SU | Coverage Factor | Total Uncertainty
| 100 | 6 |  | Volume | Precision of beaker | 5 | Uniform | √3 | 2.8868 | 2.8868 | 0.028868 | 0.076512 | 1.1197 | 2 | 2.2394
| 100 | 7 |  |  | Repeatability of volume | 0 | Normal | 2.4495 | 0
| 100 | 7 |  | Time General | Precision of stopwatch | 0.5 | Uniform | √3 | 0.28868 | 0.48419 | 0.070858
| 100 | 7 |  |  | Human error | 0.1 | Normal * | 1 | 0.2
| 100 | 7 |  | Time Start | Repeatability of time | 0.57735 | Normal | 1.7321 | 0.33333
|  |  |  | Time End |  | 0 |  |  | 0
13.1mL/s
| Volume | Time |  | Uncertainty budget:
| 100 | 8 |  | Part of Measurement | Source of uncertainty | Value +/- | PDF | Divisor | SU | Combined SU | Relative SU | Comb. R SU | Total SU | Coverage Factor | Total Uncertainty
| 100 | 7 |  | Volume | Precision of beaker | 5 | Uniform | √3 | 2.8868 | 2.8868 | 0.028868 | 0.069441 | 0.90575 | 2 | 1.8115
| 100 | 7 |  |  | Repeatability of volume | 0 | Normal | 2.4495 | 0
| 100 | 8 |  | Time General | Precision of stopwatch | 0.5 | Uniform | √3 | 0.28868 | 0.48419 | 0.063156
| 100 | 8 |  |  | Human error | 0.1 | Normal * | 1 | 0.2
| 100 | 8 |  | Time Start | Repeatability of time | 0.57735 | Normal | 1.7321 | 0.33333
|  |  |  | Time End |  | 0 |  |  | 0
10.5mL/s
| Volume | Time |  | Uncertainty budget:
| 100 | 9 |  | Part of Measurement | Source of uncertainty | Value +/- | PDF | Divisor | SU | Combined SU | Relative SU | Comb. R SU | Total SU | Coverage Factor | Total Uncertainty
| 100 | 9 |  | Volume | Precision of beaker | 5 | Uniform | √3 | 2.8868 | 2.8868 | 0.028868 | 0.046903 | 0.49372 | 2 | 0.98744
| 100 | 9 |  |  | Repeatability of volume | 0 | Normal | 2.4495 | 0
| 100 | 10 |  | Time General | Precision of stopwatch | 0.5 | Uniform | √3 | 0.28868 | 0.35119 | 0.036967
| 100 | 10 |  |  | Human error | 0.1 | Normal * | 1 | 0.2
| 100 | 10 |  | Time Start | Repeatability of time | 0 | Normal | 1.7321 | 0
|  |  |  | Time End |  | 0 |  |  | 0
Water Flow Rate (mL/s) | Total Uncertainty (mL/s)
9.6 | 0.84155
7.2 | 0.54634
17.3 | 3.1832
14.7 | 2.2394
13.1 | 1.8115
10.5 | 0.98744
PRESSURE UNCERTAINTY
Uncertainty Budget
HE Min Pressure (bar) | Calibration Uncertainty * | Precision Uncertainty | Combined SU | Coverage Factor | Total Uncertainty (bar)
0.17 | 0.000425 | 0.0028868 | 0.0029179 | 2 | 0.0058357
0.22 | 0.00055 | 0.0028868 | 0.0029387 | 2 | 0.0058774
0.2 | 0.0005 | 0.0028868 | 0.0029297 | 2 | 0.0058595
0.12 | 0.0003 | 0.0028868 | 0.0029023 | 2 | 0.0058046
0.21 | 0.000525 | 0.0028868 | 0.0029341 | 2 | 0.0058682
0.22 | 0.00055 | 0.0028868 | 0.0029387 | 2 | 0.0058774
* The RS Pro 797--4970 pressure sensor data sheet suggests an accuracy of +/- 0.25%.
* https://docs.rs-online.com/2349/0900766b8162acfd.pdf
TEMPERATURE UNCERTAINTY
Outlet Water Temperature C | Thermocouple Calibration * | Conditioner Calibration ** | Precision | Standard Deviation | Count | Repeatability SU | Combined SU | Coverage Factor | Total Uncertainty (degC)
73.8371 | 0.75 | 1 | 0.028868 | 0.80951 | 1852 | 0.018811 | 1.2505 | 2 | 2.5009
78.6688 | 0.75 | 1 | 0.028868 | 0.73734 | 650 | 0.028921 | 1.2507 | 2 | 2.5013
70.9211 | 0.75 | 1 | 0.028868 | 0.91666 | 1711 | 0.022161 | 1.2505 | 2 | 2.5011
70.7671 | 0.75 | 1 | 0.028868 | 0.85568 | 1714 | 0.020668 | 1.2505 | 2 | 2.501
72.8162 | 0.75 | 1 | 0.028868 | 0.78608 | 1471 | 0.020495 | 1.2505 | 2 | 2.501
73.5734 | 0.75 | 1 | 0.028868 | 0.91322 | 1752 | 0.021818 | 1.2505 | 2 | 2.501
PERCENTAGE ENERGY RECOVERED UNCERTAINTY
Water Flow Rate (mL/s) | Outlet Water Temperature C | Inlet water temperature C | Change in water temperature C | SU in inlet water temp | SU in outlet water temp * | SU in change in water temp | Relative Uncertainty in change in water temperature
9.6 | 73.8371 | 50 | 23.8371 | 0.028868 | 1.2505 | 1.2508 | 0.052473
7.2 | 78.6688 | 50 | 28.6688 | 0.028868 | 1.2507 | 1.251 | 0.043636
17.3 | 70.9211 | 50 | 20.9211 | 0.028868 | 1.2505 | 1.2509 | 0.05979
14.7 | 70.7671 | 50 | 20.7671 | 0.028868 | 1.2505 | 1.2508 | 0.060232
13.1 | 72.8162 | 50 | 22.8162 | 0.028868 | 1.2505 | 1.2508 | 0.054822
10.5 | 73.5734 | 50 | 23.5734 | 0.028868 | 1.2505 | 1.2509 | 0.053062
* There is no manufacturer calibration uncertainty nor repeat measurements to use here. Can only use the uncertainty based on precision.
Water Flow Rate (mL/s) | SU in water flow rate | Relative Uncertainty in water flow rate
9.6 | 0.42078 | 0.043831
7.2 | 0.27317 | 0.03794
17.3 | 1.5916 | 0.092
14.7 | 1.1197 | 0.07617
13.1 | 0.90575 | 0.069141
10.5 | 0.49372 | 0.047021
Water Flow Rate (mL/s) | Pb start | Phe start | Pb end | Phe end | Pb avg | Phe avg | Delta Pavg | SU in pressure measurements | SU in Pb avg | SU in Phe avg | SU in delta P | Relative SU in sqrt of pressure difference
9.6 | 1.04 | 0.17 | 0.77 | 0.38 | 0.905 | 0.275 | 0.63 | 0.005 | 0.0070711 | 0.0070711 | 0.01 | 0.0079365
7.2 | 1.04 | 0.22 | 0.83 | 0.45 | 0.935 | 0.335 | 0.6 | 0.005 | 0.0070711 | 0.0070711 | 0.01 | 0.0083333
17.3 | 1.08 | 0.2 | 0.84 | 0.41 | 0.96 | 0.305 | 0.655 | 0.005 | 0.0070711 | 0.0070711 | 0.01 | 0.0076336
14.7 | 1.07 | 0.12 | 0.83 | 0.32 | 0.95 | 0.22 | 0.73 | 0.005 | 0.0070711 | 0.0070711 | 0.01 | 0.0068493
13.1 | 1.09 | 0.21 | 0.85 | 0.42 | 0.97 | 0.315 | 0.655 | 0.005 | 0.0070711 | 0.0070711 | 0.01 | 0.0076336
10.5 | 1 | 0.22 | 0.76 | 0.42 | 0.88 | 0.32 | 0.56 | 0.005 | 0.0070711 | 0.0070711 | 0.01 | 0.0089286
Water Flow Rate (mL/s) | Energy Recovered Percentage (%) | Relative uncertainty in efficiency | Combined SU in efficiency (%) | Coverage Factor | Total Uncertainty (%)
9.6 | 36.4974 | 0.06883 | 2.5121 | 2 | 5.0242
7.2 | 29.974 | 0.058421 | 1.7511 | 2 | 3.5022
17.3 | 52.4403 | 0.10999 | 5.7677 | 2 | 11.5355
14.7 | 56.6389 | 0.097348 | 5.5137 | 2 | 11.0273
13.1 | 42.222 | 0.088568 | 3.7395 | 2 | 7.479
10.5 | 37.2217 | 0.071458 | 2.6598 | 2 | 5.3196

## Analysis Method
Figure 1 | Diagram showing system pressure points used to calculate steam flow rate during a pulse. Blue shows boiler pressure and red shows FPHE pressure.
Calculate steam flow rates: Steam is only flowing whilst the valve is open. This is shown by the drop-in boiler pressure (blue) and rise in heat exchanger pressure (red) in Figure 1. At the start of the steam pulse the flow rate can be found using the maximum boiler pressure and minimum FPHE pressure. Similarly, steam flow rate can be found at the end of the pulse using the minimum boiler pressure and the maximum heat exchanger pressure.
This is done using the Bernoulli equation with minor head losses in combination with the pipe cross sectional area; see Equation (0.1). This can also be converted into the steam mass flow rate using Equation (0.2).
(0.1)
(0.2)
Finally, an average steam flow rate during the pulse is found by scaling for the length of time the valve is both open and closed for, using Equation (0.3).
(0.3)
Calculate Energy Available for Recovery from Steam Condensation in FPHE:
Firstly, the enthalpy of steam entering the FPHE is read from steam tables using the average pressure during the pulse. This term is defined as hin and has units of kJ/kg.
The enthalpy of the steam leaving the FPHE is dependent on the dryness fraction when maximum possible condensation is achieved. This can be crudely estimated using the densities of the steam entering and exiting the FPHE, found based on temperature. The temperature value of the steam exiting the FPHE corresponds to the inlet cooling water temperature, the minimum temperature the steam can be brought to. The dimensionless ratio of these densities gives a representation of the change in volume of the steam per kilogram, assumed to be caused by condensation. This ratio can be multiplied by the entering dryness fraction, here assumed to be one, to give the new dryness fraction at the exit; see Equation (0.4). This method was used in the theoretical modelling of the two-stage system, described later, alongside use of T-s charts to support it. With the exit dryness fraction known, the minimum enthalpy at the exit can be found in Equation (0.5), and the resulting energy available for recovery during condensation found by Equation (0.6)
(0.4)
(0.5)
(0.6)
Where:
x is the dimensionless dryness fraction;
Ea,FPHE is the energy available for recovery during condensation in the FPHE (kJ/s).
Calculate Energy Recovered in Water in FPHE:
The flow rate of the water was measured by timing how many seconds were required to fill 100mL from the outlet pipe and converting this into a mL/s value. This was performed three times at the start of the experiment and three times at the end, with a final average taken to account for head loss in the water supply tank. This is shown in Equation (0.7). This can be converted to the mass flow rate using the density of the water at the outlet temperature; see Equation (0.8).
(0.7)
(0.8)
Where:
Vcw is the water volume flow rate (mL/s)
ti,start is the time measurement taken at the start of the test, where i ranges between 1-3 (s);
ti,end is the time measurement taken at the end of the test, where i ranges between 1-3 (s);
mcw is the mass flow rate of water (kg/s).
With the mass flow rate of the cooling water known, this can be used with the recorded inlet and outlet temperatures to calculate the energy recovered in the stream; see Equation (0.9).
(0.9)
Where:
Er,FPHE is the thermal energy recovered in the water stream (kJ/s);
Cp,avg is the average specific heat capacity of the water, taken as the mean of the Cp and inlet and outlet temperatures;
T is the change in cooling water temperature (oC)
Calculate Heat Recovery Efficiency in the FPHE:
Finally, the heat recovery efficiency can be calculated. This is simply achieved through the division of the energy recovered by the maximum energy available; see Equation (0.10).
(0.10)
Calculate steam flow rates: Steam is only flowing whilst the valve is open. This is shown by the drop-in boiler pressure (blue) and rise in heat exchanger pressure (red) in Figure 1. At the start of the steam pulse the flow rate can be found using the maximum boiler pressure and minimum FPHE pressure. Similarly, steam flow rate can be found at the end of the pulse using the minimum boiler pressure and the maximum heat exchanger pressure.
This is done using the Bernoulli equation with minor head losses in combination with the pipe cross sectional area; see Equation (0.1). This can also be converted into the steam mass flow rate using Equation (0.2).
𝑉 ̇=〖𝐶𝐴〗_𝑝𝑖𝑝𝑒×√((2(𝑃_𝑏−𝑃_𝐹𝑃𝐻𝐸))/((1+𝐾_𝑣𝑎𝑙𝑣𝑒)𝜌_𝑎𝑣𝑔 ))=(𝜋∙〖𝑑_𝑝𝑖𝑝𝑒〗^2)/4×√((2(𝑃_𝑏−𝑃_𝐹𝑃𝐻𝐸))/((1+𝐾_𝑣𝑎𝑙𝑣𝑒)𝜌_𝑎𝑣𝑔 ))
(0.1)
𝑚 ̇=𝑉 ̇∙𝜌_𝑎𝑣𝑔
(0.2)
Finally, an average steam flow rate during the pulse is found by scaling for the length of time the valve is both open and closed for, using Equation (0.3).
𝑉 ̇_(𝑠𝑡𝑒𝑎𝑚,𝑒𝑓𝑓𝑒𝑐𝑡𝑖𝑣𝑒)=𝑉 ̇_(𝑠𝑡𝑒𝑎𝑚, 𝑝𝑢𝑙𝑠𝑒)×𝑡_(𝑣𝑎𝑙𝑣𝑒_𝑜𝑝𝑒𝑛)/(𝑡_(𝑣𝑎𝑙𝑣𝑒_𝑜𝑝𝑒𝑛)+𝑡_(𝑣𝑎𝑙𝑣𝑒_𝑐𝑙𝑜𝑠𝑒𝑑) )
(0.3)
Calculate Energy Available for Recovery from Steam Condensation in FPHE:
Firstly, the enthalpy of steam entering the FPHE is read from steam tables using the average pressure during the pulse. This term is defined as hin and has units of kJ/kg.
The enthalpy of the steam leaving the FPHE is dependent on the dryness fraction when maximum possible condensation is achieved. This can be crudely estimated using the densities of the steam entering and exiting the FPHE, found based on temperature. The temperature value of the steam exiting the FPHE corresponds to the inlet cooling water temperature, the minimum temperature the steam can be brought to. The dimensionless ratio of these densities gives a representation of the change in volume of the steam per kilogram, assumed to be caused by condensation. This ratio can be multiplied by the entering dryness fraction, here assumed to be one, to give the new dryness fraction at the exit; see Equation (0.4). This method was used in the theoretical modelling of the two-stage system, described later, alongside use of T-s charts to support it. With the exit dryness fraction known, the minimum enthalpy at the exit can be found in Equation (0.5), and the resulting energy available for recovery during condensation found by Equation (0.6)
𝑥_𝑒𝑥𝑖𝑡=𝑥_𝑖𝑛𝑙𝑒𝑡×𝜌_𝑖𝑛/𝜌_𝑜𝑢𝑡
(0.4)
ℎ_𝑒𝑥𝑖𝑡=〖(ℎ〗_𝑔∙𝑥_𝑒𝑥𝑖𝑡)+ℎ_𝑓 (1−𝑥_𝑒𝑥𝑖𝑡)
(0.5)
𝐸_(𝑎,𝐹𝑃𝐻𝐸)=𝑚 ̇×(ℎ_𝑖𝑛−ℎ_𝑜𝑢𝑡)
(0.6)
Where:
x is the dimensionless dryness fraction;
Ea,FPHE is the energy available for recovery during condensation in the FPHE (kJ/s).
Calculate Energy Recovered in Water in FPHE:
The flow rate of the water was measured by timing how many seconds were required to fill 100mL from the outlet pipe and converting this into a mL/s value. This was performed three times at the start of the experiment and three times at the end, with a final average taken to account for head loss in the water supply tank. This is shown in Equation (0.7). This can be converted to the mass flow rate using the density of the water at the outlet temperature; see Equation (0.8).
(𝑉_𝑐𝑤 ) ̇=100/(((∑1▒〖𝑡_(𝑖,𝑠𝑡𝑎𝑟𝑡)+∑1▒𝑡_(𝑖,𝑒𝑛𝑑) 〗)/6) )
(0.7)
(𝑚_𝑐𝑤 ) ̇=(𝑉_𝑐𝑤 ) ̇/(1×10^(−6) )×𝜌_(𝑐𝑤,𝑜𝑢𝑡)
(0.8)
Where:
Vcw is the water volume flow rate (mL/s)
ti,start is the time measurement taken at the start of the test, where i ranges between 1-3 (s);
ti,end is the time measurement taken at the end of the test, where i ranges between 1-3 (s);
mcw is the mass flow rate of water (kg/s).
With the mass flow rate of the cooling water known, this can be used with the recorded inlet and outlet temperatures to calculate the energy recovered in the stream; see Equation (0.9).
𝐸_(𝑟,𝐹𝑃𝐻𝐸)=(𝑚_𝑐𝑤 ) ̇×𝐶_(𝑝,𝑎𝑣𝑔)×∆𝑇
(0.9)
Where:
Er,FPHE is the thermal energy recovered in the water stream (kJ/s);
Cp,avg is the average specific heat capacity of the water, taken as the mean of the Cp and inlet and outlet temperatures;
T is the change in cooling water temperature (oC)
Calculate Heat Recovery Efficiency in the FPHE:
Finally, the heat recovery efficiency can be calculated. This is simply achieved through the division of the energy recovered by the maximum energy available; see Equation (0.10).
𝜂_𝐹𝑃𝐻𝐸=𝐸_(𝑟,𝐹𝑃𝐻𝐸)/𝐸_(𝑎,𝐹𝑃𝐻𝐸) ×100
(0.10)

## PLXDAQ_new_Settings (hidden)
Previous Port: | 4 | DO NOT CHANGE THIS LAYOUT OR THE MACRO WONT WORK ANYMORE !!!!
Previous Baud: | 9600
Rst on Connect?: | FALSE
Custom Checkbox 1 | TRUE
Custom Checkbox 2 | TRUE
Custom Checkbox 3 | FALSE
Sheet name to use: | 9.6mL s
Log Incoming to DDW: | TRUE
Log Outgoing to DDW: | TRUE
Log System to DDW: | TRUE
Add Timestamp to DDW: | TRUE
Custom Form Width: | 536.25
#EXPERT-CONFIG# Serial Device Read buffer: | 1024
#EXPERT-CONFIG# Serial Device Write buffer: | 1024
#EXPERT-CONFIG# Excel Read buffer size: | 1024
#EXPERT-CONFIG# Excel interim buffer size: | 64