## Contents
Table of contents
Sheet 1 | Example cost details of 40kWp PV-battery system, a 50kW and 25kW diesel generator
Sheet2 | Economic cost analysis data for the energy generating systems for the cluster of 400 refugee households in Kutupalong camp, Bangladesh
Sheet 3 | Economic cost analysis data for the Bidi-bidi base camp energy generating systems, Uganda
Sheet 4 | Economic cost analysis data for the Imvepi trading centre energy generating systems, Uganda
Supplemental data for report "Data Collection for the Solar Photovoltaic (PV) based Electricity Access assessment to Replace Diesel generators in Refugee Camps in Southern Bangladesh and Northern Uganda"

## Sheet 1
Example cost details of 40kWp PV-battery system, a 50kW and 25kW diesel generator
40kWp PV-battery system details (for a cluster of 400 refugee households and other amenities) |  | Nominal discount rate 6%
Installed cost/ kWp= $800 |  | Expected inflation rate 2%
O&M cost=$2000+$95/year
Replacement $750 | Life time 20y
O&M $0.50/kWp/y
Lead acid battery 1.03kWh (513Ah) x 2V/ cell x 170 cells =~ 175kWh
Cost/cell $225 Peplacement $200 O&M $0.50/cell/y
Max depth of discharge 60%
Inverter 5kWp (85-90% effeciency) $4000 Life time 10 years
MPPT Charge controller 80A = $500/unit
25kW Diesel generator
Generator life 40,000hrs and Major overhaul at every 10,000 hours
Cost onf DG delivered and installed $22000
Fixed capital cost = $10000 (storage tank $3500+ housing & fuel supply chain $3500+ Admin $3000)
Replacement cost $18000
Operation and maintanance: Wages $960/year
Regular repair and maintanance $95x 12= $1140 (periodic and monthly)
Fuel loss $100/m
Optimised fuel consumption (HOMER) 61l/d (based on the estimated load)
On average generator runs 20h a day
50kW Diesel generator
Generator life 40,000hrs and Major overhaul at every 10,000 hours
Cost of DG delivered and installed $30000
Fixed capital cost= $12000 (Storage tank $5000+ housing & fuel supply facility $4000+ Admin $3000 )
Replacement cost: $25000
Operation and maintamance: Wages $1200/year
Regular repair and maintanance $130/m x 12 month = $1560 (overall periodic and monthly)
Fuel loss $158/month (estimated from interview)
Ovserved fuel consumption 100l/d (based on data kept by AIRD)
On average generator runs 20h a day

## Sheet 2
Energy generating systems for the Kutupalong refugee camp
Year on year accumulated costs (USD) of different electricity generating systems modelled for the study cluster of 400 refugee households along with 50 street lights, 30 toilet lights, 240 mobile phone charging and 150 radios in Kutupalong camp, Bangladesh.
Year | PV AC 20kWp | PV DC 16kWp | DG AC 10kW
USD
Y0 | 73000 | 55700 | 19000
Y1 | 76545 | 58570 | 33445
Y2 | 80090 | 61440 | 47890
Y3 | 83635 | 64310 | 62335
Y4 | 87180 | 67180 | 76780
Y5 | 90725 | 70050 | 91225
Y6 | 94270 | 72920 | 105670
Y7 | 97815 | 75790 | 120115
Y8 | 101360 | 78660 | 134560
Y9 | 104905 | 81530 | 149005
Y10 | 108450 | 84400 | 163450
Y11 | 111995 | 87270 | 177895
Y12 | 115540 | 90140 | 192340
Y13 | 119085 | 93010 | 206785
Y14 | 122630 | 95880 | 221230
Y15 | 126175 | 98750 | 235675
Y16 | 129720 | 101620 | 250120
Y17 | 133265 | 104490 | 264565
Y18 | 136810 | 107360 | 279010
Y19 | 140355 | 110230 | 293455
Y20 | 143900 | 113100 | 307900
NPC and LCOE (USD) of different electricity generating systems modelled for the study cluster of 400 refugee households along with 50 street lights, 30 toilet lights, 240 mobile phone charging and 150 radios in Kutupalong camp, Bangladesh.
Year | DG 10kW NPC | DG 10kW LCOE | PV 20kWp NPC | PV 20kWp LCOE | PV 16kWp NPC | PV 16kWp LCOE
USD
Y1 | 28224 | 1.9 | 40726 | 2.9 | 31995 | 2.28
Y2 | 41872 | 1.44 | 46982 | 1.7 | 36731 | 1.34
Y3 | 54966 | 1.28 | 52886 | 1.3 | 41250 | 1.02
Y4 | 67530 | 1.21 | 58457 | 1.1 | 45522 | 0.86
Y5 | 79653 | 1.16 | 63709 | 0.978 | 49560 | 0.764
Y6 | 91374 | 1.13 | 68661 | 0.895 | 53357 | 0.699
Y7 | 102619 | 1.11 | 73326 | 0.835 | 56977 | 0.651
Y8 | 113409 | 1.09 | 77720 | 0.788 | 60378 | 0.615
Y9 | 123761 | 1.08 | 81857 | 0.752 | 63588 | 0.586
Y10 | 133809 | 1.07 | 86183 | 0.725 | 66616 | 0.563
Y11 | 143467 | 1.06 | 90455 | 0.704 | 69879 | 0.547
Y12 | 152733 | 1.05 | 94483 | 0.687 | 72986 | 0.533
Y13 | 161623 | 1.05 | 94281 | 0.671 | 75921 | 0.521
Y14 | 170187 | 1.04 | 101859 | 0.657 | 78694 | 0.51
Y15 | 178481 | 1.04 | 105230 | 0.645 | 81313 | 0.5
Y16 | 186439 | 1.03 | 108403 | 0.634 | 83787 | 0.492
Y17 | 194074 | 1.03 | 111389 | 0.62 | 86116 | 0.484
Y18 | 201400 | 1.03 | 114197 | 0.61 | 88315 | 0.477
Y19 | 208498 | 1.02 | 117135 | 0.607 | 90388 | 0.47
Y20 | 215332 | 1.02 | 119920 | 0.6 | 92342 | 0.464

## Sheet 3
Energy generating systems for the Bidi-bidi base camp, Uganda
Year on year accumulated costs (USD) of different electricity generating systems modelled for the Bidi-bidi base camp, Uganda
Year | Diesel generator 25kW | PV-battery system 40kWp | Diesel generator 50kW
USD
Y0 | 32000 | 112400 | 42000
Y1 | 62410 | 116820 | 84150
Y2 | 92820 | 121240 | 126300
Y3 | 123230 | 125660 | 168450
Y4 | 153640 | 130080 | 210600
Y5 | 184050 | 134500 | 252750
Y6 | 214460 | 138920 | 294900
Y7 | 244870 | 143340 | 337050
Y8 | 275280 | 147760 | 379200
Y9 | 305690 | 152180 | 421350
Y10 | 336100 | 156600 | 463500
Y11 | 366510 | 161020 | 505650
Y12 | 396920 | 165440 | 547800
Y13 | 427330 | 169860 | 589950
Y14 | 457740 | 174280 | 632100
Y15 | 488150 | 178700 | 674250
Y16 | 518560 | 183120 | 716400
Y17 | 548970 | 187540 | 758550
Y18 | 579380 | 191960 | 800700
Y19 | 609790 | 196380 | 842850
Y20 | 640200 | 200800 | 885000
NPC and LCOE (USD) of different electricity generating systems modelled for the Bidi-bidi base camp, Uganda.
Year | PV-battery 40kWp NPC | PV-battery 40kWp LCOE | Diesel generator 25kW NPC | Diesel generator 25kW LOCE | Diesel generator 50kW NPC | Diesel generator 50kW LCOE
USD
Y1 | 55775 | 1.7 | 44430 | 1.32 | 63860 | 1.9
Y2 | 64425 | 1 | 73565 | 1.11 | 103980 | 1.57
Y3 | 72580 | 0.78 | 101465 | 1.04 | 142433 | 1.46
Y4 | 80625 | 0.65 | 128180 | 1.01 | 179288 | 1.41
Y5 | 87500 | 0.57 | 154000 | 0.97 | 214899 | 1.37
Y6 | 94315 | 0.53 | 179060 | 0.97 | 249365 | 1.35
Y7 | 100725 | 0.49 | 203045 | 0.96 | 282408 | 1.34
Y8 | 106750 | 0.47 | 226013 | 0.96 | 314080 | 1.33
Y9 | 112420 | 0.41 | 248006 | 0.95 | 344430 | 1.32
Y10 | 117740 | 0.42 | 269480 | 0.94 | 373987 | 1.31
Y11 | 123040 | 0.41 | 290100 | 0.94 | 402382 | 1.31
Y12 | 128615 | 0.4 | 309850 | 0.94 | 429600 | 1.3
Y13 | 133860 | 0.39 | 328760 | 0.94 | 455680 | 1.3
Y14 | 138800 | 0.38 | 346990 | 0.93 | 480820 | 1.29
Y15 | 143440 | 0.38 | 364720 | 0.93 | 505220 | 1.29
Y16 | 147810 | 0.37 | 381700 | 0.93 | 528604 | 1.29
Y17 | 151910 | 0.36 | 397960 | 0.93 | 551020 | 1.28
Y18 | 155760 | 0.36 | 413525 | 0.93 | 572500 | 1.28
Y19 | 159380 | 0.35 | 428680 | 0.93 | 593370 | 1.29
Y20 | 162780 | 0.35 | 443280 | 0.93 | 613465 | 1.28

## Sheet 4
Energy generating systems for the Imvepi trading centre , Uganda
Year on year acumulated cost (USD) of different electricity generating systems modelled for the Imvepi trading centre, Uganda
Year | PV-battery AC 28kWp | PV-battery DC 18kWp | Diesel generator 10kW
USD
Y0 | 82000 | 53000 | 19000
Y1 | 85145 | 54840 | 35455
Y2 | 88290 | 56680 | 51910
Y3 | 91435 | 58520 | 68365
Y4 | 94580 | 60360 | 84820
Y5 | 97725 | 62200 | 101275
Y6 | 100870 | 64040 | 117730
Y7 | 104015 | 65880 | 134185
Y8 | 107160 | 67720 | 150640
Y9 | 110305 | 69560 | 167095
Y10 | 113450 | 71400 | 183550
Y11 | 116595 | 73240 | 200005
Y12 | 119740 | 75080 | 216460
Y13 | 122885 | 76920 | 232915
Y14 | 126030 | 78760 | 249370
Y15 | 129175 | 80600 | 265825
Y16 | 132320 | 82440 | 282280
Y17 | 135465 | 84280 | 298735
Y18 | 138610 | 86120 | 315190
Y19 | 141755 | 87960 | 331645
Y20 | 144900 | 89800 | 348100
NPC and LCOE (USD) of different electricity generating systems modelled for the Imvepi trading centre, Uganda
Year | DG 10kW NPC | DG 10kW LCOE | PV 28kWp NPC | PV 28kWp LCOE | PV 18kWp NPC | PV 18kWp LCOE
USD
Y1 | 30145 | 1.39 | 41356 | 1.8 | 31874 | 1.74
Y2 | 45662 | 1.01 | 47692 | 1.1 | 36353 | 1.01
Y3 | 60544 | 0.91 | 53688 | 0.824 | 40610 | 0.766
Y4 | 74829 | 0.86 | 59358 | 0.696 | 43653 | 0.644
Y5 | 88608 | 0.81 | 66800 | 0.64 | 46494 | 0.57
Y6 | 101922 | 0.81 | 69789 | 0.566 | 47480 | 0.545
Y7 | 114701 | 0.79 | 74578 | 0.528 | 52606 | 0.484
Y8 | 126966 | 0.79 | 79102 | 0.499 | 55895 | 0.457
Y9 | 138738 | 0.776 | 83375 | 0.476 | 60016 | 0.436
Y10 | 150152 | 0.769 | 87700 | 0.456 | 61432 | 0.413
Y11 | 161124 | 0.764 | 90903 | 0.438 | 64789 | 0.404
Y12 | 171655 | 0.759 | 94642 | 0.426 | 66456 | 0.392
Y13 | 181763 | 0.756 | 98171 | 0.415 | 68985 | 0.37
Y14 | 191498 | 0.752 | 101502 | 0.405 | 71183 | 0.35
Y15 | 200920 | 0.75 | 104923 | 0.398 | 72351 | 0.343
Y16 | 209662 | 0.747 | 109267 | 0.392 | 73811 | 0.338
Y17 | 218641 | 0.745 | 111427 | 0.386 | 75432 | 0.334
Y18 | 226971 | 0.743 | 114411 | 0.381 | 77654 | 0.325
Y19 | 235035 | 0.741 | 118229 | 0.376 | 79627 | 0.324
Y20 | 242799 | 0.74 | 119400 | 0.37 | 81549 | 0.314